## EU -001, -002 & -003
Table 1, Summary of Air Pollutant Standards and Terms
Tampa Electric Company | [7 empty] | Draft/Proposed Permit No. 0570039-061-AV
Big Bend Station | [7 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-001, -002 & -003 | Fossil Fuel Fired Steam Generator Unit Nos. 1 - 3
Unless otherwise indicated, the following apply to each individual emissions unit listed.
Pollutant Name |  |  | Allowable Emissions |  |  | Equivalent Emissions*
or Parameter | Fuel(s) | Hours/Year | Standard(s) | lbs./hour | TPY | lbs./hour | TPY | Regulatory Citation(s) | See permit condition(s)
VE | All | 8760 | 20% w/ 27% for 6 min/hr |  |  |  |  | Rule 62-296.405(1)(a), F.A.C. | III.A.11.
VE-SB | All |  | 60% 3 hrs/24 hrs |  |  |  |  | Rule 62-210.700(3), F.A.C. | III.A.12.
-001 PM | All |  | 0.03 lb/MMBtu |  |  | 121.1 | 530 | Permit No. 0570039-060-AC | III.A.13. & 14.
-002 PM | All |  | 0.03 lb/MMBtu |  |  | 119.9 | 525 | Permit No. 0570039-060-AC | III.A.13. & 14.
-003 PM | All |  | 0.03 lb/MMBtu |  |  | 123.5 | 541 | Permit No. 0570039-060-AC | III.A.13. & 14.
-001 - -004 PM combined | raw & coal residual |  |  |  | 2767 |  |  | Rule 62-212.400 (escape PSD), F.A.C. | III.A.15.
PM-SB | All |  | 0.3 lb/MMBtu |  |  |  |  | Rule 62-210.700(3), F.A.C. | III.A.16.
SO2 | #2 Fuel Oil |  | 2.75 lb/MMBtu |  |  |  |  | Rule 62-296.405(1)(c)1.j., F.A.C. | III.A.17.
SO2 | #2 Fuel Oil |  | 0.5% S by weight |  |  |  |  | Rule 62-296.405(1)(e)3., F.A.C. | III.A.18.
-001 SO2 | Solid Fuel |  | 6.5 lb/MMBtu 2-hr avg. |  |  | 26240.5 | Included in cap. | Rule 62-296.405(1)(c)2.b., F.A.C. | III.A.19.
-002 SO2 | Solid Fuel |  | 6.5 lb/MMBtu 2-hr avg. |  |  | 25974 | Included in cap. | Rule 62-296.405(1)(c)2.b., F.A.C. | III.A.19.
-003 SO2 | Solid Fuel |  | 6.5 lb/MMBtu 2-hr avg. |  |  | 26747.5 | Included in cap. | Rule 62-296.405(1)(c)2.b., F.A.C. | III.A.19.
-001 - -003 SO2 combined |  |  | 31.5 tons/hour 3-hr avg. |  | NA | 63,000 3-hr avg. |  | Rule 62-296.405(1)(c)2.b., F.A.C. | III.A.19.
-001 - -003 SO2 combined |  |  | 25 tons/hour 24-hr avg. |  | NA | 50,000 24-hr avg. |  | Rule 62-296.405(1)(c)2.b., F.A.C. | III.A.19.
-001 - -004 SO2 combined | raw & coal residual |  |  |  | 71810 | 33,000 24-hr avg. |  | Rule 62-212.400 (escape PSD), F.A.C. | III.A.20.
-001 SO2 | Solid Fuel |  | 95% SO2 reduction or 0.25 lb/MMBtu 30-day rolling avg. on and after 01/01/2013 |  |  | 1009.3 | 4420 | Permit No. 0570039-060-AC | III.A.21. & 26.
-002 SO2 | Solid Fuel |  | 95% SO2 reduction or 0.25 lb/MMBtu 30-day rolling avg. on and after 01/01/2013 |  |  | 999 | 4376 | Permit No. 0570039-060-AC | III.A.21. & 26.
-003 SO2 | Solid Fuel |  | 95% SO2 reduction or 0.25 lb/MMBtu 30-day rolling avg. |  |  | 1028.8 | 4506 | Permit No. 0570039-060-AC | III.A.21. & 26.
-001 NOx | Solid Fuel |  | 0.12 lb/MMBtu 30-day rolling avg. on and after 06/01/2010 |  |  | 484.4 | 2121.9 | Permit No. 0570039-060-AC | III.A.23. & 26.
-002 NOx | Solid Fuel |  | 0.12 lb/MMBtu 30-day rolling avg. |  |  | 479.5 | 2100.3 | Permit No. 0570039-060-AC | III.A.23. & 26.
-003 NOx | Solid Fuel |  | 0.12 lb/MMBtu 30-day rolling avg. |  |  | 494 | 2163.7 | Permit No. 0570039-060-AC | III.A.24. & 26.
-001 & -002 CS-001 stack ammonia slip |  |  | 10 ppmv |  |  | 58.44 | 255.97 | Permit Nos. 0570039-024-AC | III.A.25.
-001 & -002 CS-0w1 stack ammonia slip |  |  | 10 ppmv |  |  | 56.15 | 245.94 | Permit Nos. 0570039-024-AC | III.A.25.
-003 ammonia slip |  |  | 10 ppmv |  |  | 33.15 | 145.2 | Permit Nos. 0570039-022-AC (amended by 0570039-035-AC) | III.A.25.
Notes:
* The "Equivalent Emissions" listed are for informational purposes only.

## EU -004
Table 1, Summary of Air Pollutant Standards and Terms
Tampa Electric Company | [7 empty] | Draft/Proposed Permit No. 0570039-061-AV
Big Bend Station | [7 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-004 | Fossil Fuel Fired Steam Generator Unit No. 4
Pollutant Name |  |  | Allowable Emissions |  |  | Equivalent Emissions*
or Parameter | Fuel(s) | Hours/Year | Standard(s) | lbs./hour | TPY | lbs./hour | TPY | Regulatory Citation(s) | See permit condition(s)
VE | All | 8760 | 20% w/ 27% for 6 min/hr |  |  |  |  | Rule 62-296.405(2)(a), F.A.C. | III.B.14.
PM | Solid or Liquid Fuel |  | 0.01 lb/MMBtu |  |  | 43.3 | 189.7 | Permit No. 0570039-060-AC | III.B.15. & 16.
-001 - -004 PM combined | raw & coal residual |  |  |  | 2767 |  |  | Rule 62-212.400 (escape PSD), F.A.C. | III.B.17.
SO2 | Solid or Liquid Fuel |  | 0.82 lb/MMBtu 30-day rolling avg. or 90% SO2 reduction | 3551 |  |  | 1553.4 | PSD-FL-040 | III.B.18., 19. & 23.
-001 - -004 SO2 combined | raw & coal residual |  |  |  | 71810 | 33,000 24-hr avg. |  | Rule 62-212.400 (escape PSD), F.A.C. | III.B.20.
NOx | Solid Fuel |  | 0.10 lb/MMBtu 30-day rolling avg. |  |  | 433 | 1896.5 | Permit No. 0570039-060-AC | III.B.21. & 23.
ammonia slip |  |  | 10 ppmv |  |  | 38.51 | 168.67 | Permit No. 0570039-020-AC (amended by 0570039-026, -031 & -036-AC) | III.B.22.
CO | Solid Fuel |  | 0.20 lb/MMBtu 30-day rolling avg. |  |  | 866 | 3793.1 | PSD-FL-390, as amended | III.B.24.
Notes:
* The "Equivalent Emissions" listed are for informational purposes only.

## EU -007
Table 1, Summary of Air Pollutant Standards and Terms
Tampa Electric Company |  | Draft/Proposed Permit No. 0570039-061-AV
Big Bend Station |  | Facility ID No. 0570039
This Unit was removed from service on 10/26/2010. Refer to Subsection C (reserved to preserve numbering)
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
Brief Description
E.U. ID No. | Combustion Turbine No. 1
-007

## EU -008 ...
Table 1, Summary of Air Pollutant Standards and Terms
Tampa Electric Company | [7 empty] | Draft/Proposed Permit No. 0570039-061-AV
Big Bend Station | [7 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
008,-009,-018,-019,-026 | Flyash Handling and Storage - Silo Nos. 1 & 2
Pollutant Name |  |  | Allowable Emissions |  |  | Equivalent Emissions*
or Parameter | Fuel(s) | Hours/Year | Standard(s) | lbs./hour | TPY | lbs./hour | TPY | Regulatory Citation(s) | See permit condition(s)
-008 &-018 PM |  | 8760 | 0.03 gr/dscf | 5.16 | 22.62 |  |  | Rule 62-4.160(2), F.A.C. | III.D.3.
-008 &-018 VE |  |  | 5% |  |  |  |  | Rule 62-296.711 (2) (b) F.A.C. | III.D.3. & 4.
-009 &-019 PM |  | 8760 | 0.03 gr/dscf | 5.16 | 22.62 |  |  | Rule 62-4.160(2), F.A.C. | III.D.3.
-009 &-019 VE |  |  | 5% |  |  |  |  | Rule 62-296.711 (2) (b) F.A.C. | III.D.3. & 4.
-026 VE |  | 8760 | <20% |  |  |  |  | Rule 62-296.320(4)(b)1., F.A.C. | FW4.
Notes:
* The "Equivalent Emissions" listed are for informational purposes only.

## EU -010, -029 & -030
Table 1, Summary of Air Pollutant Standards and Terms
Tampa Electric Company | [7 empty] | Draft/Proposed Permit No. 0570039-061-AV
Big Bend Station | [7 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-010, -029 & -030 | Solid Fuel Yard
Pollutant Name |  |  | Allowable Emissions |  |  | Equivalent Emissions*
or Parameter | Fuel(s) | Hours/Year | Standard(s) | lbs./hour | TPY | lbs./hour | TPY | Regulatory Citation(s) | See permit condition(s)
-010 VE |  | 8760 | <20% |  |  |  |  | Rule 62-296.320(4)(b)1., F.A.C. | FW4., III.H.7
-029 VE |  | 8760 | 5% |  |  |  |  | Rule 62-296.711(2), F.A.C. | III.P.4
-029 Particulate Matter |  | 8760 | 5% | [5 empty] | III. P.4
-030 VE |  | 8760 | 5% |  |  |  |  | Rule 62-296.711(2), F.A.C. | III.P.4
-030 Particulate Matter |  | 8760 | 5% | [5 empty] | III. P.4
Notes:
* The "Equivalent Emissions" listed are for informational purposes only.

## EU -011 ...
Table 1, Summary of Air Pollutant Standards and Terms
Tampa Electric Company | [7 empty] | Draft/Proposed Permit No. 0570039-061-AV
Big Bend Station | [7 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-011, -012, -013, | Limestone Handling and Storage
-23 & -25
Pollutant Name |  |  | Allowable Emissions |  |  | Equivalent Emissions*
or Parameter | Fuel(s) | Hours/Year | Standard(s) | lbs./hour | TPY | lbs./hour | TPY | Regulatory Citation(s) | See permit condition(s)
-011 VE |  | 8760 | <20% |  |  |  |  | Rule 62-296.320(4)(b)1., F.A.C. | FW4.
-012 & -013 PM |  | 8760 |  | 0.05 | 0.22 |  |  | PSD-FL-040 | III.F.8.
-012 & -013 VE |  |  | 5% |  |  |  |  | PSD-FL-040 | III.F.8.
-023 PM |  | 8760 |  | 0.65 | 2.9 |  |  | PSD-FL-040 | III.F.7.
-023 VE |  |  | 5% |  |  |  |  | PSD-FL-040 | III.F.7.
-020 PM |  | 8760 | 0.03 gr/dscf |  |  | 2.1 | 9.2 | Rule 62-296.711(2)(b), F.A.C. | III.F.9.
-020 VE |  |  | 5% |  |  |  |  | Rule 62-297.620(4), F.A.C. | III.F.9.
-021 PM |  | 8760 | 0.03 gr/dscf |  |  | 2.1 | 9.2 | Rule 62-296.711(2)(b), F.A.C. | III.F.9.
-021 VE |  |  | 5% |  |  |  |  | Rule 62-297.620(4), F.A.C. | III.F.9.
-025 VE |  | 8760 | <20% |  |  |  |  | Rule 62-296.320(4)(b)1., F.A.C. | FW4.
Notes:
* The "Equivalent Emissions" listed are for informational purposes only.

## EU -014, -027 & -028
Table 1, Summary of Air Pollutant Standards and Terms
Tampa Electric Company | [7 empty] | Draft/Proposed Permit No. 0570039-061-AV
Big Bend Station | [7 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-014, -027 & -028 | Flyash Handling and Storage Silo No. 3
Pollutant Name |  |  | Allowable Emissions |  |  | Equivalent Emissions*
or Parameter | Fuel(s) | Hours/Year | Standard(s) | lbs./hour | TPY | lbs./hour | TPY | Regulatory Citation(s) | See permit condition(s)
-014 & -027 PM |  | 8760 |  | 0.2 |  |  | 0.9 | PA79-12 & PSD-FL-040 | III.E.4.
-014 & -027 VE |  |  | 5% |  |  |  |  | PA79-12 & PSD-FL-040 | III.E.5.
-028 VE |  | 8760 | <20% |  |  |  |  | Rule 62-296.320(4)(b)1., F.A.C. | FW4.
Notes:
* The "Equivalent Emissions" listed are for informational purposes only.

## EU -015 ...
Table 1, Summary of Air Pollutant Standards and Terms
Tampa Electric Company | [7 empty] | Draft/Proposed Permit No. 0570039-061-AV
Big Bend Station | [7 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
015,-016,-017,-039 | Coal Bunkers with Roto-Clones
Pollutant Name |  |  | Allowable Emissions |  |  | Equivalent Emissions*
or Parameter | Fuel(s) | Hours/Year | Standard(s) | lbs./hour | TPY | lbs./hour | TPY | Regulatory Citation(s) | See permit condition(s)
-015 PM |  | 4167 |  | 0.48 | 0.99 |  |  | Rule 62-296.700(2)(c), F.A.C. | III.G.1. & 2.
-015 VE |  |  | 5% |  |  |  |  | Rule 62-297.620(4), F.A.C. | III.G.3.
-016 PM |  | 4167 |  | 0.48 | 0.99 |  |  | Rule 62-296.700(2)(c), F.A.C. | III.G.1. & 2.
-016 VE |  |  | 5% |  |  |  |  | Rule 62-297.620(4), F.A.C. | III.G.3.
-017 PM |  | 4167 |  | 0.48 | 0.99 |  |  | Rule 62-296.700(2)(c), F.A.C. | III.G.1. & 2.
-017 VE |  |  | 5% |  |  |  |  | Rule 62-297.620(4), F.A.C. | III.G.3.
-039 PM |  | 4167 |  | 0.48 | 0.99 |  |  | Rule 62-296.700(2)(c), F.A.C. | III.G.1. & 2.
-039 VE |  |  | 5% |  |  |  |  | Rule 62-297.620(4), F.A.C. | III.G.3.
Notes:
* The "Equivalent Emissions" listed are for informational purposes only.

## EU -022
Table 1, Summary of Air Pollutant Standards and Terms
Tampa Electric Company | [7 empty] | Draft/Proposed Permit No. 0570039-061-AV
Big Bend Station | [7 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-022 | Lime Silo for Wastewater Treatment Plant with one Baghouse
Pollutant Name |  |  | Allowable Emissions |  |  | Equivalent Emissions*
or Parameter | Fuel(s) | Hours/Year | Standard(s) | lbs./hour | TPY | lbs./hour | TPY | Regulatory Citation(s) | See permit condition(s)
PM |  | 8760 | 0.03 gr/dscf |  |  | 2.1 | 0.99 | Rule 62-296.700(2)(c), F.A.C. | III.L. 3.
VE |  |  | 5% |  |  |  |  | Rule 62-296.700(2)(c), F.A.C. | III.L. 3.
Notes:
* The "Equivalent Emissions" listed are for informational purposes only.

## EU -032
Table 1, Summary of Air Pollutant Standards and Terms
Tampa Electric Company | [7 empty] | Draft/Proposed Permit No. 0570039-061-AV
Big Bend Station | [7 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-032 | Surface Coating of Miscellaneous Metal Parts
Pollutant Name |  |  | Allowable Emissions |  |  | Equivalent Emissions*
or Parameter | Fuel(s) | Hours/Year | Standard(s) | lbs./hour | TPY | lbs./hour | TPY | Regulatory Citation(s) | See permit condition(s)
VOC |  | 3500 | 3.0 - 4.3 lb/gallon max. |  |  |  | 15 | Rule 62-296.513(2), F.A.C. | III.I.3.
Notes:
* The "Equivalent Emissions" listed are for informational purposes only.

## EU -033 & -034
Table 1, Summary of Air Pollutant Standards and Terms
Tampa Electric Company | [7 empty] | Draft/Proposed Permit No. 0570039-061-AV
Big Bend Station | [7 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-033 & -034 | Abrasive Blasting
Pollutant Name |  |  | Allowable Emissions |  |  | Equivalent Emissions*
or Parameter | Fuel(s) | Hours/Year | Standard(s) | lbs./hour | TPY | lbs./hour | TPY | Regulatory Citation(s) | See permit condition(s)
-033 & -034 PM |  | 8760 | 0.03 gr/dscf |  | 15 | 3.4 |  | Rule 62-296.712(2), F.A.C. | III.J.3.
VE |  |  | 5% |  |  |  |  | Rule 62-296.712(2), F.A.C. | III.J.3.
Notes:
* The "Equivalent Emissions" listed are for informational purposes only.

## EU -035
Table 1, Summary of Air Pollutant Standards and Terms
Tampa Electric Company | [7 empty] | Draft/Proposed Permit No. 0570039-061-AV
Big Bend Station | [7 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-035 | Surface Coating of Ships
Pollutant Name |  |  | Allowable Emissions |  |  | Equivalent Emissions*
or Parameter | Fuel(s) | Hours/Year | Standard(s) | lbs./hour | TPY | lbs./hour | TPY | Regulatory Citation(s) | See permit condition(s)
VOC |  | 8760 | 4.3 lb/gallon max., Table 2 |  |  |  | 0.57 | 40 CFR 63.783 | III.K.4.
Notes:
* The "Equivalent Emissions" listed are for informational purposes only.

## EU -037 & -038
Table 1, Summary of Air Pollutant Standards and Terms
Tampa Electric Company | [7 empty] | Draft/Proposed Permit No. 0570039-061-AV
Big Bend Station | [7 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-037 & -038 | Coal Residual Storage and Transfer from the Polk Power Station
Pollutant Name |  |  | Allowable Emissions |  |  | Equivalent Emissions*
or Parameter | Fuel(s) | Hours/Year | Standard(s) | lbs./hour | TPY | lbs./hour | TPY | Regulatory Citation(s) | See permit condition(s)
-037 VE |  | 8760 | <20% |  |  |  |  | Rule 62-296.320(4)(b)1., F.A.C. | FW4.
-038 VE |  |  | 5% |  |  |  |  | Rule 62-297.620(4), F.A.C. | III.M.4.
Notes:
* The "Equivalent Emissions" listed are for informational purposes only.

## EU -041 & -042
Table 1, Summary of Air Pollutant Standards and Terms
Tampa Electric Company | [7 empty] | Draft/Proposed Permit No. 0570039-061-AV
Big Bend Station | [7 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-041 & -042 | Simple Cycle Combustion Turbines
Pollutant Name |  |  | Allowable Emissions |  |  | Equivalent Emissions*
or Parameter | Fuel(s) | Hours/Year | Standard(s) | lbs./hour | TPY | lbs./hour | TPY | Regulatory Citation(s) | See permit condition(s)
-041 & -042 VE |  | 8760 | <10% | [5 empty] | III.O.7
-041 & -042 Nox | NG | 3500 | 25 ppmvd | 32 |  |  | 56 |  | III.O.8.
-041 & -042 Nox | ULSD | 500 | 42 ppmvd | 51.3 |  |  | 12.825 |  | III.O.8.
-041 & -042 Nox | NG & ULSD | 3500 | [6 empty] | III.O.8.
-041 & -042 CO | NG | 3500 | 21 ppmvd | 9.1 |  |  | 15.925 |  | III.O.9.
-041 & -042 CO | ULSD | 500 | 5.1 ppmvd | 2.1 |  |  | 0.525 |  | III.O.9.
-041 & -042 SO2 | NG | 3500 | 2.0 gr of S/100 scf of NG | [5 empty] | III.O.11.
-041 & -042 SO2 | ULSD | 500 | 0.0015% S by weight | [5 empty] | III.O.11.
Notes:
* The "Equivalent Emissions" listed are for informational purposes only.

## EU -046
Table 1, Summary of Air Pollutant Standards and Terms
Tampa Electric Company | [7 empty] | Draft/Proposed Permit No. 0570039-061-AV
Big Bend Station | [7 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-046 | Transloading and off-site Transfer
Pollutant Name |  |  | Allowable Emissions |  |  | Equivalent Emissions*
or Parameter | Fuel(s) | Hours/Year | Standard(s) | lbs./hour | TPY | lbs./hour | TPY | Regulatory Citation(s) | See permit condition(s)
-046 VE |  | 8760 | <20% |  |  |  |  | Rule 62-296.320(4)(b)1., F.A.C. | FW4. & III.Q.6
Notes:
* The "Equivalent Emissions" listed are for informational purposes only.

## EU -047
Table 1, Summary of Air Pollutant Standards and Terms
Tampa Electric Company | [7 empty] | Draft/Proposed Permit No. 0570039-061-AV
Big Bend Station | [7 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-047 | Railroad Unloading and Conveying
Pollutant Name |  |  | Allowable Emissions |  |  | Equivalent Emissions*
or Parameter | Fuel(s) | Hours/Year | Standard(s) | lbs./hour | TPY | lbs./hour | TPY | Regulatory Citation(s) | See permit condition(s)
-047 VE |  | 8760 | <20% |  |  |  |  | Rule 62-296.320(4)(b)1., F.A.C. | FW4. & III R.7
Notes:
* The "Equivalent Emissions" listed are for informational purposes only.