1030035 001 62181

HUMAN CREMATORY

COMPLIANCE INSPECTION CHECKLIST

INSPECTION TYPE:	ANNUAL (INS1, INS2)		COMPLAINT/DISCOVERY (CI)

RE-INSPECTION (FUI)		ARMS COMPLAINT NO:

AIRS ID#: 1030035 001  DATE:     10/25/07		ARRIVE:     11:00 AM		DEPART:    3:00 PM

FACILITY NAME:  Director's Services, Inc.

FACILITY LOCATION:		3121 44th Avenue North

St. Petersburg, FL

RESPONSIBLE OFFICIAL:  Phillip R Rouzer?	PHONE:  727-527-5667

CONTACT NAME:   Phillip R Rouzer?	PHONE:  727-527-5667

REMITTANCE YEAR:  N/A	  ENTITLEMENT PERIOD:  12/20/02	/	12/20/07

(effective date)	(end date)

PART I:  INSPECTION COMPLIANCE STATUS (check  only one box)

 IN COMPLIANCE         MINOR Non-COMPLIANCE 	 SIGNIFICANT Non-COMPLIANCE

PART II: TESTING/RECORDKEEPING REQUIREMENTS – Rule 62-296.401, F.A.C.

(check  appropriate box(es))

1.  Were there any objectionable odor(s) detected?---------------------------------------------------------------------	Yes	  No

2.  Was a visible emissions test conducted during this site visit according to EPA Method 9 (Ref.: Chapter

62-297, F.A.C.)?---------------------------------------------------------------------------------------------------------	Yes	  No

3.  In order to demonstrate individual source compliance, was an annual visible emissions test conducted 60

days prior to the AGP Notification form submission, and within 60 days prior to each anniversary date?

(Rule 62-296.401(5)(i), F.A.C.)----------------------------------------------------------------------------------------	Yes	  No

4.  In order to demonstrate individual source compliance were the remaining applicable standards testing

completed  within 60 days prior to the AGP Notification form submission? (Rule 62-210.300(4), F.A.C.)	Yes	  No

a)  Carbon Monoxide (CO) emissions equal to or below the requirements of 100 parts per million by

volume, dry basis, 	corrected to 7% O2 on an hourly average basis and tested according to EPA Method

10 (Ref.: Chapter 62-297, F.A.C.)?------------------------------------------------------------------------------------	Yes	  No

b)  Oxygen test performed according to EPA Method 3 (Ref.: Chapter 62-297, F.A.C.)?---------------------	Yes	  No

c)  Particulate matter emissions test with results equal to or below the requirements of 0.080 grains per

dry standard cubic foot (ft3)of flue gas, corrected to 7% O2 and tested according to EPA Method 5

(Ref.: Chapter.62-297, F.A.C.)?----------------------------------------------------------------------------------------	Yes	  No

5.  Was all emissions testing conducted with the source operating at the manufacturers recommended

capacity?-------------------------------------------------------------------------------------------------------------------	Yes	  No

6.  Was CO & PM compliance demonstrated by submission of a test report for an identical crematory unit?	Yes	  No

7.  Was the Department notified at least 15 days prior to the date of the last formal compliance test?----------	Yes	  No

8.  Was the required test report filed with the Department as soon as practical, but no longer than 45 days after

the test was completed?-------------------------------------------------------------------------------------------------	Yes	  No

PART III:  OPERATING/RECORDKEEPING REQUIREMENTS – Rule 62-296.401, F.A.C.

(check  appropriate box(es))

1.  Is there Continuous Emissions Monitoring System (CEMS) equipment installed on each unit to record temperatures in the 	primary and secondary chambers where there is a 1.0 second gas residence time in the secondary chamber combustion zone in 	accordance with the manufacturer’s instructions?-----------------------------------------------------------------------	Yes	  No

a)  Do temperature probes seem to be properly placed?-----------------------------------------------------------	Yes	  No

b)  Are the following records kept on file, available for inspection for at least two years following the recording of such

measurements, maintenance, reports and records?

1)  All measurements (including CEMS)---------------------------------------------------------------------	Yes	  No

2)  Monitoring device-------------------------------------------------------------------------------------------	Yes	  No

3)  Performance Testing Measurements	------------------------------------------------------------------	Yes	  No

4)  CEMS Performance Evaluation---------------------------------------------------------------------------	Yes	  No

5)  All CEMS or monitoring device calibration checks----------------------------------------------------	Yes	  No

6)  Adjustments--------------------------------------------------------------------------------------------------	Yes	  No

7)  Preventive maintenance performed on systems/devices-----------------------------------------------	Yes	  No

8)  Corrective maintenance performed on systems/devices-----------------------------------------------	Yes	  No

2.  Was this crematory unit constructed: (check only one  box)

a)  BEFORE  August 30, 1989? (If this box checked, continue on to #3 and skip #4)

b)  ON or AFTER  August 30, 1989? (If this box checked, skip #3 and continue on to #4)

3.  If constructed BEFORE August 30, 1989 is the:

a)  secondary chamber combustion zone providing at least a 1.0 second gas residence time @ 1600oF?	Yes	  No

b)  actual operating temperature of the secondary chamber combustion zone no less than 1400oF

throughout the combustion process in the primary chamber?-----------------------------------------------	Yes	  No

c)  cremation in the primary chamber begun after the secondary chamber combustion zone temperature

is equal to or greater than 1400oF?------------------------------------------------------------------------------	Yes	  No

d)  required monitoring equipment installed and operational, and providing continuous monitoring to

record the temperature at the point or beyond where 1.0 second gas residence time is obtained in the

secondary chamber combustion zone according to the manufacturer’s instructions?--------------------	Yes	  No

4.  If constructed ON or AFTER August 30, 1989 is the:

a)  volume in the secondary combustion zone sufficient to provide at least a 1.0 second gas residence time

@ 1800o F?---------------------------------------------------------------------------------------------------------	Yes	  No

b)  the actual operating temperature of the secondary chamber combustion zone no less than 1600oF

throughout the combustion process in the primary chamber?-----------------------------------------------	Yes	  No

c)  secondary chamber combustion zone temperature equal to or greater than 1600oF before the cremation

process begins in the primary chamber?-----------------------------------------------------------------------	Yes	  No

5.  Are appropriate cremation containers containing no more than 0.5 % (percent) by weight chlorinated

plastics used during the cremation of dead human bodies?-----------------------------------------------------	Yes	  No

a)  If the answer to question 4 above is YES, is certifying documentation from the manufacturer that they

are composed of 0.5% or less by weight chlorinated plastics kept on file at the site for the duration of

their use and for at least two years after their use?-----------------------------------------------------------	Yes	  No

b)  Are there any other materials, including biomedical wastes (Rule 62-210.200, FAC) incinerated at

this location?------------------------------------------------------------------------------------------------------	Yes	  No

6.  Have all crematory operators been trained and certified by a Department-approved training program?	Yes	  No

a)	Are copies of the training certificates for all crematory operators kept on file at the facility for the duration

of the operator’s employment & for an additional two years after termination of employment?-----	Yes	  No

PART IV:  SPECIAL CONDITIONS AND PROCEDURES – Rule 62-296.401, F.A.C.

A.  New or Modified Process Equipment

1.  Since the last inspection has there been

a)  installation of any new process equipment?----------------------------------------------------	Yes	  No

b)  alterations to existing process equipment without replacement?----------------------------	Yes	  No

c)  replacement of existing equipment substantially different than that noted on the most

recent notification form?--------------------------------------------------------------------------	Yes	  No

d)  If you answered YES to any of the above, did the owner submit a new and complete

notification form and appropriate fee (Rule 62-4.050, F.A.C.) to the appropriate DEP or

local program office?------------------------------------------------------------------------------	Yes	  No

2.  If a crematory unit has been modified to the extent that a Department air construction permit

was required, have all operators been retrained to operate the modified unit?------------------	Yes	  No

3.  In the case of new or modified equipment, where a Department air construction permit was

required, has the owner submitted copies of all operator training certificates?-----------------	Yes	  No

a) submitted within the 15 day required window following the training?----------------------	Yes	  No

Mike Ojo  Thomas

_______________________________________________		_______10/25/07_____

Inspector’s Name (Please Print)				     Date of Inspection

_______________________________________________		___________________________________

Inspector’s Signature				     Approximate Date of Next Inspection

COMMENTS:  See the attached Pinellas County inspection report form for additional information

| FACILITY: Director's Services, Inc. | PERMIT ID: 43 |
| --- | --- |
|  | DISTRICT: Southwest |
| ADDRESS: 3121 44th Avenue North | CONTACT PHONE: |
| St. Petersburg, FL | 727-527-5667 |
| ARMS NO: 1030035 001 | PERMIT NO: | Expiration Date: 12/20/07 Renewal Date: 11/20/07 |
|  | 1030035-004-AG |  |
|  |  | Test Date: 11/20/07 |
| EMISSION UNIT DESCRIPTION: Unit B: Human Crematory, Industrial Equipment & Engineering Company, Model IE-43, Northernmost unit. Unit must operate at >1400 degrees F by rule |
| INSPECTION DATE: | ARMS INSPECTION TYPE: | COMPLIANCE STATUS: |
| 10/25/07 | INS2 or INS_____ | IN MNC SNC |
| Type of Inspection: Initial Re-inspection Complaint Drive-by Quarterly A. General Review: |
| 1. | Permit File Review Yes No |
| 2. | Introduction and Entry Yes No Comments: : This inspection was performed in order to determine if this facility has been operating within applicable regulations. Mr. Phillip Rouzer (manager) was present during the facility inspection of the emission unit. |
| 3. | Administrative Corrections. Within thirty (30) days of any minor changes requiring corrections to information contained in the registration form, the owner or operator shall notify the Department in writing. Such changes shall include: 1. Any change in the name, address, or phone number of the facility or authorized representative not associated with a change in ownership or with a physical relocation of the facility or any emissions units or operations comprising the facility; or 2. Any other similar minor administrative change at the facility. Is the Authorized Representative still: Phillip R Rouzer? Yes No Is the facility contact still: Phillip R Rouzer? Yes No [62-210.310(2)(d), F.A.C.] Comments: Facility contact and Authorized Representative is still Phillip R. Rouzer. |

| IN | MNC | SNC | B. Specific Conditions |
| --- | --- | --- | --- |
|  |  |  | Visible emissions - Visible emissions shall not exceed five percent (5%) opacity, six (6) minute average, except that visible emissions not exceeding fifteen percent (15%) opacity shall be allowed for up to six (6) minutes in any one (1) hour period. [Rule 62-296.401(5)(b)1, F.A.C.] Comments: The last annual visible emissions test, conducted on 11/17/06 demonstrated an opacity of 0%. An AQD VE test was performed during this site visit Yes or No. An opacity of 0 % was observed. |
|  |  |  | Operating Temperature - Human crematory units shall operate with a secondary chamber temperature of no less than : ( 1600 degrees Fahrenheit throughout the combustion process in the primary chamber, for construction applications received by the Department on or after August 30, 1989. Cremation in the primary chamber shall not begin unless the secondary chamber combustion zone temperature is equal to or greater than 1600 degrees Fahrenheit. [Rule 62-296.401(5)(c), F.A.C.], or ٱ 1400 degrees Fahrenheit throughout the combustion process in the primary, for construction applications received by the Department prior to August 30, 1989. Cremation in the primary chamber shall not begin unless the secondary chamber combustion zone temperature is equal to or greater than 1400 degrees Fahrenheit. [Rule 62-296.401(5)(c), F.A.C.] Comments: Facility is required to operate at a temperature of 1600 o F based on identical stack testing, source specific stack testing and visible emissions tests, or rule. Based on record reviews, the lowest operating temperature observed was 1510 o F |
|  |  |  | Allowed Materials - Human crematory units shall cremate only human or fetal remains with appropriate containers. The remains may be clothed. The containers shall contain no more than 0.5 percent by weight chlorinated plastics as demonstrated by the manufacturer’s data sheet. If containers are incinerated, documentation from the manufacturer certifying that they are composed of 0.5 percent or less by weight chlorinated plastics shall be kept on-file at the site for the duration of their use and for at least two (2) years after their use. No other material, including biomedical waste as defined in Rule 62-210.200, F.A.C., shall be incinerated. [Rule 62-296.401(5)(d), F.A.C.] Comments: Reviewed records for the months of 1/2/07 through 10/25/07 The highest reported chlorine content was _0_%. Supporting documentation was verified ( Yes or No) Note: The facility used only cardboard for cremation. |
|  |  |  | Equipment Maintenance -All human crematory units shall be maintained in proper working order in accordance with the manufacturer’s specifications to ensure the integrity and efficiency of the equipment. If a crematory unit contains a defect that affects the integrity or efficiency of the unit, the unit shall be taken out of service. No person shall use or permit the use of that unit until it has been repaired or adjusted. Repair records on all crematory units shall be maintained onsite for at least two years. A written plan with operating procedures for startup, shutdown and malfunction of each crematory unit shall be maintained and followed during those events. Each unit’s burners shall be operated with a proper air-to-fuel ratio. If the unit so allows, the burners’ flame characteristics shall be visually checked at least once during each operating shift and adjusted when warranted by the visual checks. [Rule 62-296.401(5)(e), F.A.C.] Comments: The facility ( does/ does not) have a written plan for operating procedures for startup, shutdown and malfunction. Repair records were reviewed for the months of 1/2/06 through 10/25/07. The records were available and maintained on site for a period of two years. The crematory unit ( does/ does not) allow, the burners’ flame characteristics shall be visually checked. The flame ( was/ was not/ NA) observed during each shift. |
|  |  |  | Frequency of Testing. 1. The owner or operator of any human crematory unit using an air general permit shall have a performance test conducted for visible emissions no later than thirty (30) days after the unit commences operation, and annually thereafter. 2. The owner or operator of any human crematory unit operating under the authority of an air construction permit or air operation permit shall have a performance test conducted for visible emissions prior to submitting the application for an initial air operation permit, and annually thereafter. 3. The owner or operator of any human crematory unit shall not be required to have performance tests conducted for carbon monoxide and particulate matter, except as provided at paragraph 62-297.310(7)(b), F.A.C. [Rule 62-296.401(5)(h), F.A.C.] Comments: The last test was conducted on11/17/06. This( is / is not) within the allowable 60 day window. |
|  |  |  | Test Notification - The owner or operator shall notify the Department, at least 15 days prior to the date on which each formal compliance test is to begin, of the date, time, and place of each such test, and the test contact person who will be responsible for coordinating and having such test conducted for the owner or operator. [62-297.310(7)(a)9. F.A.C.] Comments: The County was notified on _11/3/06, for the test that was conducted on 11/17/06. This( is / is not) within the allowable 15 day window. |
|  |  |  | Test Reports - The required test report shall be filed with the PCDEM as soon as practical but no later than 45 days after the test is completed. [62-297.310(8), F.A.C.] Comments: The last test was conducted on 11/17/06, and the test results were submitted on 2/7/07. This( is / is not) within the allowable 45 day window. |
|  |  |  | Continuous Monitoring Requirements- Each crematory unit shall be equipped and operated with a continuous monitor to record temperature at the point or beyond where 1.0 second gas residence time is obtained in the secondary chamber combustion zone in accordance with the manufacturer’s instructions. In addition, each crematory unit installed after February 1, 2007, shall be equipped and operated with a pollutant monitoring system to automatically control combustion based on continuous in-stack opacity measurement. Such system shall be calibrated to restrict combustion in the primary chamber whenever any opacity exceeding 15% opacity is occurring. A complete file of all temperature measurements; all continuous monitoring systems, monitoring devices, and performance testing measurements; all continuous monitoring system performance evaluations; all continuous monitoring system or monitoring device calibration checks; and all adjustments, preventive maintenance, and corrective maintenance performed on these systems or devices, shall be recorded in a permanent legible form available for inspection. Continuous temperature monitoring documentation shall include operator name, operator indication of when cremation in the primary chamber was begun, date, time, and temperature markings. Pollutant monitoring system documentation shall include indication of when the opacity measurement system was cleaned and checked for proper operation in accordance with the manufacturer’s recommended maintenance schedule. The file shall be retained for at least two (2) years following the recording of such measurements, maintenance, reports, and records. [Rule 62-296.401(5)(i), F.A.C.] Comments: Reviewed temperature charts for the months of 1/2/06 through 10/25/07. The last calibration on the temperature chart was on 6/17/03. The temperature probe appears properly placed ( Yes or No). Note: Probe is located at the front right west corner of the emission unit. This facility ( was/ was no)t installed after February 1, 2007, therefore ( must/ does no)t have to be equipped and operated with a pollutant monitoring system to automatically control combustion based on continuous in-stack opacity measurement. The system( is/ is not/ NA) calibrated to restrict combustion in the primary chamber whenever any opacity exceeding 15% opacity is occurring. |
|  |  |  | Process Rate Comments: The maximum load for this crematory unit is 300 pounds. The largest body cremated during this review period was 200 pounds. |

| IN | MNC | SNC | C. Selected General Conditions and Procedures |
| --- | --- | --- | --- |
|  |  |  | Periods of Noncompliance - If, for any reason, the owner or operator of any facility operating under an air general permit pursuant to Rule 62-210.300(4)(a), F.A.C., does not comply with or will be unable to comply with any condition or limitation of the permit, the permittee shall immediately provide the Department with the following information: 1. A description of and cause of noncompliance; and 2. The period of noncompliance, including dates and times; or, if not corrected, the anticipated time the noncompliance is expected to continue, and steps being taken to reduce, eliminate, and prevent recurrence of the noncompliance. The permittee shall be responsible for any and all damages which may result. [62-210.310(3)(i), F.A.C.] Comments: A review of this facilities records show no upset to this emission unit. |
|  |  |  | Valid Permit To avoid lapse of authority to operate, an owner or operator intending to use, or continue to use, an air general permit must submit the proper registration form and processing fee at least thirty (30) days prior to expiration of the facility’s existing air operation permit or air general permit. [62-210.310(2)(c)2., F.A.C.] Comments: The permit expires on 12/20/07. A new notification form is required to be submitted no later than 11/20/07. |
|  |  |  | Equipment Changes - The owner or operator shall maintain records of all equipment changes. In the case of installation of new process or air pollution control equipment, alteration of existing process or control equipment without replacement, or replacement of existing process or control equipment with equipment substantially different in terms of capacity, method of operation, material processed, or intended use than that noted on the most recent registration form, the owner or operator shall submit a new and complete air general permit registration form for the facility with the appropriate fee pursuant to Rule 62-4.050, F.A.C. to the Department, provided, however, that any change that would constitute a new major stationary source, major modification, or modification that would be a major modification but for the provisions of paragraph 62-212.400(2)(a), F.A.C., shall require authorization by air construction permit. [62-210.310(2)(e)., F.A.C.] Comments: There have been no changes at this time. |

D. Other:

Closing Conference Yes No Comments: I informed Mr. Rouzer, the facility appears to be in non-compliance at this time.

Other Comments: I asked Mr. Rouzer for a written plan with operating procedures for startup, shutdown and malfunction of crematory unit. He stated he was not aware that they have to have a written plan with operating procedures for startup, shutdown and malfunction of crematory unit. I told Mr. Rouzer there has some changes to the General Permit rules in January 10, 2007. I explained to Mr. Rouzer that they need to have a written plan with operating procedures for startup, shutdown and malfunction of crematory unit onsite. He stated he would have the written plan with operating procedures onsite within 30 days and copy AQ Division office. I told Mr. Rouzer, the facility appears to be in non-compliance at this time.

Inspector(s): Mike Ojo Thomas, Pinellas County, Air Quality Division

Signature(s) Date: 10/8/07

CONTACT LOG? __11/8/07,    ACCESS? 11/8/07,    ARMs? 11/8/07

H:\users\wpdocs\airqual\Air_Compliance\AQI\1030035 001 62181.doc