TECHNICAL EVALUATION

&

PRELIMINARY DETERMINATION

APPLICANT

Florida Power & Light Company

700 Universe Boulevard

Juno Beach, FL 33408

Lauderdale Plant

ARMS Facility ID No. 0110037

PROJECT

Project No. 0110037-018-AC (PSD-FL-145C & 423C)

Application for Minor Source Air Construction Permit

Miscellaneous Changes with Renewal

COUNTY

Broward County, Florida

PERMITTING AUTHORITY

Florida Department of Environmental Protection

Division of Air Resource Management

Office of Permitting and Compliance

2600 Blair Stone Road, MS#5505

Tallahassee, Florida  32399-2400

June 15, 2018

- General Project INFORMATION

  - Air Pollution Regulations

Projects at stationary sources with the potential to emit air pollution are subject to the applicable environmental laws specified in Section 403 of the Florida Statutes (F.S.).  The statutes authorize the Department of Environmental Protection (Department) to establish regulations regarding air quality as part of the Florida Administrative Code (F.A.C.), which includes the following applicable chapters:  62-4 (Permits); 62-204 (Air Pollution Control – General Provisions); 62-210 (Stationary Sources – General Requirements); 62-212 (Stationary Sources – Preconstruction Review); 62-213 (Operation Permits for Major Sources of Air Pollution); 62-296 (Stationary Sources - Emission Standards); and 62-297 (Stationary Sources – Emissions Monitoring).  Specifically, air construction permits are required pursuant to Chapters 62-4, 62-210 and 62-212, F.A.C.

In addition, the U. S. Environmental Protection Agency (EPA) establishes air quality regulations in Title 40 of the Code of Federal Regulations (CFR).  Part 60 specifies New Source Performance Standards (NSPS) for numerous industrial categories.  Part 61 specifies National Emission Standards for Hazardous Air Pollutants (NESHAP) based on specific pollutants.  Part 63 specifies NESHAP based on the Maximum Achievable Control Technology (MACT) for numerous industrial categories.  The Department adopts these federal regulations in Rule 62-204.800, F.A.C.

  - Glossary of Common Terms

Because of the technical nature of the project, the permit contains numerous acronyms and abbreviations, which are defined in Appendix A of this permit.

  - Facility Description and Location

The Florida Power & Light Company (FPL) operates the existing Lauderdale Plant, which is an electric power plant with a Standard Industrial Classification Code of SIC No. 4911.  The facility is located at Dania Beach in Broward County, two miles west of Ravenswood Road, and can be accessed from Southwest 42nd Street and Griffin Road.  Figure 1 below shows the location of Broward County, while Figure 2 shows a map of the site’s location.  The UTM coordinates are Zone 17, 580.2 kilometers (km) East, and 2883.3 km North.

Broward County

Figure 1.  Location of Broward County, Florida.	Figure 2.  Location of the Lauderdale Plant.

The Lauderdale Plant consists primarily of two combined-cycle generating units (Units 4 and 5), five new simple-cycle GE 7F.05 generating units (Unit 6), two simple-cycle gas turbine units, an auxiliary boiler, an emergency fire pump engine, circuit breakers and fuel oil storage tanks.  Table 1 list the regulated emission units (EU) at the facility.

Table 1 - regulated Emissions Unit IDentification Numbers and descriptions.

| EU No. | ## Brief Description |
| --- | --- |
| 035 | CCCT with HRSG (CT 4A) |
| 036 | CCCT with HRSG (CT 4B) |
| 037 | CCCT with HRSG (CT 5A) |
| 038 | CCCT with HRSG (CT 5B) |
| 003 | Two Combustion Turbines |
| 027 | Fuel Oil Storage Tank #2 (80,000 barrel (bbl)) |
| 028 | Fuel Oil Storage Tank #3 (150,000 bbl) |
| 029 | Fuel Oil Storage Tank #5 (75,000 bbl) |
| 030 | 2 Fuel Oil Dump Tanks (2,500 gallon and 110 gallon) |
| 039 | Site Solvent Usage |
| 042 | Auxiliary Boiler (15.5 MMBtu/hr) |
| 044 | Emergency Diesel Fire Pump Engine (376 HP) |
| 046 | SCCT Unit 6B |
| 047 | SCCT Unit 6C |
| 048 | SCCT Unit 6D |
| 049 | SCCT Unit 6E |
| 053 | SCCT Unit 6A |
| 054 | Circuit Breakers |

  - Facility Regulatory Categories

- The facility is a major source of hazardous air pollutants (HAP).

- The facility operates units subject to the acid rain provisions of the Clean Air Act.

- The facility is a Title V major source of air pollution in accordance with Chapter 62-213, F.A.C.

- The facility is a major stationary source in accordance with Rule 62-212.400, F.A.C. for the Prevention of Significant Deterioration (PSD) of Air Quality.

- The facility operates units subject to the New Source Performance Standards (NSPS) of 40 Code of Federal Regulations (CFR) 60.

- The facility operates units subject to the National Emissions Standards for Hazardous Air Pollutants (NESHAP) of 40 Code of Federal Regulations (CFR) 63.

  - Project Description

The applicant is requesting revisions to Air Construction Permit Nos. 0110037-013-AC (PSD-FL-423A), PSD-FL-145 and AC06-179848.  The miscellaneous revisions to the referenced permits include:

- The revision of the volatile organic compound (VOC) emissions cap for the facility to clarify the exclusion of newly permitted emissions units from the initial VOC RACT determination;

- The annual tests required will be changed from each federal fiscal year to each calendar year;

- The removal of Jet A fuel oil from the list of fuel storage tanks at the facility; and,

- Additional clarification to the testing requirements for Unit 6 (designated as EU Nos. 046-049 & 053).

  - Processing Schedule

- 03/29/2018	Department received the application for an air pollution construction permit.

- 06/15/2018	Draft permit package issued.

- PSD Applicability

This project will not cause an increase in emissions; therefore, the project is not subject to PSD preconstruction review.

- Department review

  - Applicant’s Requested Changes

FPL requested for a minor air construction permit in order to incorporate a few requested changes to the renewed Title V air operation permit.  Each request is identified below, along with the Department’s Response.

- Applicant’s Request:  The facility no longer stores or utilizes Jet A fuel oil.  As such, FPL requests that all references to Jet A fuel be removed from the permit (e.g. Specific Condition C.1 of Permit No. 0110037-016-AV).

Department’s Response:  Specific Condition C.1 of Permit No. 0110037-016-AV cited Permit Nos. AC06-179848 and AO06-230614.  However, neither permit contained mention of Jet A fuel oil.  On May 31, 2018, the applicant provided background information regarding the history of Jet A fuel at the Lauderdale Plant.  According to the applicant, the condition was established due to the non-attainment status for ozone in the early 1990s for Miami-Dade, Broward, and Palm Beach counties.  The repowering of Units 4 & 5 required that the entire Lauderdale site needed to be under 100 tons per year (TPY) of volatile organic compound (VOC) emissions to avoid the Lowest Achievable Emission Rate (LAER) analysis.  To limit VOC's to 99.9 TPY, this required the determination of VOC emissions from the storage tanks.  Since light distillate fuel oil was authorized by existing permits, and Jet A was considered "light distillate fuel oil" per existing permits, Jet A fuel was considered in determining the total VOC emissions.  Jet A fuel was specifically included as a condition directly in the initial Title V, Section C.  Thus, it was more of a clarification to the Title V permit in calling out the type of distillate since distillate fuel itself had already been authorized by previous existing permit(s).

Since Jet A fuel was not mentioned in any underlying air construction permits, the Department shall remove all references to Jet A fuel through the Title V air operation permit.  A similar explanation regarding the site’s discontinued use of Jet A fuel will be provided in the statement of basis of the renewed operation permit.

- Applicant’s Request:  FPL requests all testing frequencies within the Title V permit be updated from fiscal year to calendar year to be consistent with Chapter 62-297, F.A.C.

Department’s Response:  Due to an agreement made between the applicant and EPA on March 3rd, 1998, the Department could not revise the annual stack testing requirements for visible emissions (VE).  As part of this agreement, compliance demonstrations for VE were specified to occur each federal fiscal year.  Although annual testing was specified in this agreement for other pollutants such as particulate matter (PM) and carbon monoxide (CO), the annual basis was unspecified.  Therefore, PSD-FL-145 was revised to allow compliance demonstrations for PM and CO to occur each calendar year (January 1st to December 31st), pursuant to Rule 62-297.310(8), F.A.C.

- Applicant’s Request:  Historically, the VOC emissions cap, referenced in Specific Condition FW9. of Permit No. 0110037-016-AV, was included in the Title V air operation permit in relation to VOC RACT for the existing Lauderdale facility.  This condition excluded Units 4 & 5 VOC emissions from the facility VOC emissions cap.  Since Unit 6 has recently been added to the Title V permit, and therefore was not included in the initial VOC RACT determination or permitting, FPL requests that this condition FW9 be updated to identify that the exclusion also applies to Unit 6 and associated equipment.

Department’s Response:  The Department has modified the Specific Condition 26 of Permit No. AC06-179848 in order to incorporate the exclusion of the recently permitted Unit 6.

- Applicant’s Request:  As seen in Permit No. 0110037-016-AV, Table B.9 in Subsection B for Unit 6 (EU Nos. 046-049 & 053) currently contains footnote (a) regarding CO standards at low loads < 90% but above the Minimum Emissions Compliance Load (MECL).  FPL’s understanding during the initial permitting and testing of Unit 6 was that these lower load CO limits required initial stack testing only.  Specific Condition B.29 further clarifies that emissions testing is to be conducted at 90% or greater load.  FPL requests that Footnote (a) of Table B.9 be updated to clarify that the stated low load CO lb/hr limits only required initial stack testing only.

Department’s Response:  Unit 6 was authorized for installation and initial operation through Permit No. 0110037-013-AC (PSD-FL-423A).  The Department has reviewed the technical write-up of the project and validated the initial testing requirements with the primary processor of PSD-FL-423A.  Given the information provided, Specific Condition 11 of Section 3 in Permit No. 0110037-013-AC (PSD-FL-423A) has been revised to specify that only initial testing is required for low loads below 90%.

- Applicant’s Request:  FPL requests updating Specific Condition B.28 (as seen in Permit No. 0110037-016-AV) to clarify that the required annual testing for CO and VE are to be conducted at normal operating conditions.

Department’s Response:  The Department has modified Specific Condition 17 (Section III, Subsection A) of Permit No. 0110037-013-AC (PSD-FL-423A) in order to incorporate further clarification for the CO and VE annual testing requirements for Unit 6.

- Applicant’s Request:  On June 8, 2018, FPL requested to revise Specific Condition B.34.b (as seen in Permit No. 0110037-016-AV).  The condition is intended for quarterly excess emissions resulting from SIP-based emission standards, not NSPS requirements.  Please assist in clarifying this condition for Unit 6 by removing mention of the NSPS format and add language specifying the NSPS requirements for excess emissions.

Department’s Response:  The Department has granted this revision and has added language by modifying Permit No. 0110037-013-AC (PSD-FL-423A), Section III, Subsection A, Specific Condition 37.

- In addition to the requested changes, the Department has revised the following condition(s):

- Permit No. AC06-179848, Specific Condition 21:  The referenced condition was revised in order to remove mention of ‘each bank’, as intended through Permit No. 0110037-013-AC (PSD-FL-423A) for EU 003.  In addition, the record retention requirement has been revised from three years to five years, pursuant to Rule 62-213.440(1)(b)2, F.A.C.

- Permit No. 0110037-006-AC (PSD-FL-145B), Specific Condition 3:  PSD-FL-145, Specific Condition 12, was revised through Specific Condition 3 of PSD-FL-145B to remove continuous steam injection monitoring and impose NOX CEMS as the continuous compliance determination method.  The referenced specific condition was revised to further clarify the averaging period (4 hour rolling average) for continuous compliance of Units 4 and 5.

  - State Requirements

As specified, the affected units of this project are subject to the following state rules:

    - EU 003

Rule 62-296.570, F.A.C., Reasonably Available Control Technology (RACT)

- An emissions cap was established for the facility in the early 1990s due to Broward County’s non-attainment status for ozone in previous years, i.e. 1992-1994.

- This rule specifies emissions standards for major volatile organic compounds (VOC) and nitrogen oxide (NOX) emitting facilities.

    - EU 035-038, 046 - 049, 053 & 054

Rule 62-212.400, F.A.C., PSD

- This rule applies to the construction of any new major stationary source or the major modification of any existing major stationary source.

- Covers air quality modeling, air monitoring, source obligation, and control technology review.

    - EU 035 - 038, 046 – 049 & 053

Chapter 62-214, F.A.C., Acid Rain, Phase II

- This chapter outlines the additional permitting requirements for Title V sources that are subject to the Federal Acid Rain Program.

- Requires a complete Acid Rain compliance plan for each Acid Rain unit included in an Acid Rain Part application.

  - Federal NSPS Provisions

    - EU 035 - 038

40 CFR 60, Subpart GG, Standards of Performance for Stationary Gas Turbines

- The provisions of this subpart include emissions standards for NOX and SO2.

- Also requires the installation of a continuous monitoring system to monitor and record the fuel consumption and the ratio of water or steam to fuel being fired in the turbine.

    - EU 046 – 049 & 053

40 CFR 60, Subpart KKKK, Standards of Performance for Stationary Combustion Turbines

- This subpart contains emissions standards for NOX and SO2.

- Establishes compliance schedules for the control of emissions from stationary combustion turbines that commenced construction, modification or reconstruction after February 18, 2005.

40 CFR 60, Subpart TTTT, Standards of Performance for Greenhouse Gas for Electric Generating Units

- Under NSPS, Subpart TTTT, base load combustion turbines that combust more than 90% natural gas are subject to a standard of 1,000 lb CO2 per megawatt-hour (MWh), gross, on a 12-operating-month rolling average basis.

- For gas or oil-fired turbines under Subpart TTTT, and under the Acid Rain continuous monitoring provisions of 40 CFR 75, emissions of CO2 may be measured using a continuous emissions monitor, or through fuel use monitoring and emissions factors

  - Federal NESHAP Provisions

    - EU 046 – 049 & 053

40 CFR 63, Subpart YYYY, NESHAP for Stationary Combustion Turbines

- Establishes national emission limitations and operating limitations for HAP emissions from stationary combustion turbines located at major sources of HAP emissions

- Requires demonstrating continuous compliance with the emission and operating limitations.

    - EU 046

40 CFR 63, Subpart ZZZZ, NESHAP for Stationary Reciprocating Internal Combustion Engines

- Establishes emission limitations and operating limitations for HAP emitted from stationary reciprocating internal combustion engines (RICE) located at major and area sources of HAP emissions.

- Requires demonstrating continuous compliance with the emission and operating limitations.

    - EU 042

40 CFR 63, Subpart DDDDD, NESHAP for Industrial, Commercial, and Institutional Boilers and Process Heaters

- This auxiliary boiler qualifies as a “Unit designed to burn gas 1 subcategory” since it is designed to burn propane (i.e., gas 1 fuel) as its primary, and only, fuel.

- Requires annual tune-up and minimizing emissions from startup and shutdown.

- Preliminary Determination

The Department makes a preliminary determination that the proposed project will comply with all applicable state and federal air pollution regulations as conditioned by the draft permit.  This determination is based on a technical review of the complete application, reasonable assurances provided by the applicant, and the conditions specified in the draft permit.  No air quality modeling analysis is required because the project does not result in a significant increase in emissions.  Lara Rabbath is the project engineer responsible for reviewing the application and drafting the permit.  Additional details of this analysis may be obtained by contacting the project engineer at the Department’s Office of Permitting and Compliance at Mail Station #5505, 2600 Blair Stone Road, Tallahassee, Florida  32399-2400 at 850-717-9082 or by email Lara.Rabbath@dep.state.fl.us.