Permittee

| Waste Management Inc. of Florida 2700 Wiles Road Pompano Beach, Florida, 33073 Authorized Representative: Mr. Jeff Roccapriore, District Manager | Air Permit No. 0112094-014-AC Permit Expires: 12/31/2022 Minor Air Construction Permit Monarch Hill Landfill New Flare and Sulfur Treatment System |
| --- | --- |

Project

This is the final air construction permit, which authorizes the installation of 3,000 standard cubic feet per minute (scfm) open flare with flow limited to 12- month rolling total of 1,156.32 million standard cubic feet (MMscf), and a sulfur treatment system upstream of the flare to remove hydrogen sulfide (H2S) prior to combustion to minimize emissions of sulfur dioxide (SO2).  The proposed work will be conducted at the existing Monarch Hill Landfill, which is a municipal solid waste landfill categorized under Standard Industrial Classification No. 4953.  The existing facility is in Broward County at 2700 Wiles Road in Pompano Beach, Florida.  The UTM coordinates are Zone 17, 583.19 kilometers (km) East, and 2908.03 km North.

This final permit is organized into the following sections:  Section 1 (General Information); Section 2 (Administrative Requirements); Section 3 (Emissions Unit Specific Conditions); and Section 4 (Appendices).  Because of the technical nature of the project, the permit contains numerous acronyms and abbreviations, which are defined in Appendix A of Section 4 of this permit.

Statement of Basis

This air pollution construction permit is issued under the provisions of:  Chapter 403 of the Florida Statutes (F.S.) and Chapters 62-4, 62-204, 62-210, 62-212, 62-296 and 62-297 of the Florida Administrative Code (F.A.C.).  The permittee is authorized to conduct the proposed work in accordance with the conditions of this permit.  This project is subject to the general preconstruction review requirements in Rule 62-212.300, F.A.C. and is not subject to the preconstruction review requirements for major stationary sources in Rule 62-212.400, F.A.C. for the Prevention of Significant Deterioration (PSD) of Air Quality.

Upon issuance of this final permit, any party to this order has the right to seek judicial review of it under Section 120.68 of the Florida Statutes by filing a notice of appeal under Rule 9.110 of the Florida Rules of Appellate Procedure with the clerk of the Department of Environmental Protection in the Office of General Counsel (Mail Station #35, 3900 Commonwealth Boulevard, Tallahassee, Florida, 32399-3000) and by filing a copy of the notice of appeal accompanied by the applicable filing fees with the appropriate District Court of Appeal.  The notice must be filed within 30 days after this order is filed with the clerk of the Department.

Executed in Tallahassee, Florida

(DRAFT)

For:

Syed Arif, P.E., Program Administrator

Office of Permitting and Compliance

Division of Air Resource Management

CERTIFICATE OF SERVICE

The undersigned duly designated deputy agency clerk hereby certifies that this Final Air Construction Permit package was sent by electronic mail, or a link to these documents made available electronically on a publicly accessible server, with received receipt requested before the close of business on the date indicated below to the following persons.

Mr. Jeff Roccapriore, Waste Management:  jroccapr@wm.com

Mr. Craig Ash, Waste Management:  cash1@wm.com

Mr. Jim Christiansen, Carlson Environmental Consultants:  jchristi@cecenv.com

Ms. Lindsey E. Kennelly, P.E., Carlson Environmental Consultants:  lkennelly@cecenv.com

# Southeast District:  sed.air@dep.state.fl.us

# Mr. Robert Wong, Broward County:  rwong@broward.org

# Broward County:  airlicense@broward.org

# Ms. Lynn Scearce, DEP OPC:  lynn.scearce@dep.state.fl.us

# Clerk Stamp

# FILING AND ACKNOWLEDGMENT FILED, on this date, pursuant to Section 120.52(7), Florida Statutes, with the designated agency clerk, receipt of which is hereby acknowledged.

(DRAFT)

Facility Description

Monarch Hill Landfill, owned and operated by Waste Management Inc. of Florida (WMIF), is an active Class I Landfill which began receiving waste in 1965.  The overall design capacity of the landfill as of 2015 is 80 million cubic yards (approximately 61 million cubic meters).  There are 391.5 acres permitted to receive MSW and 44.5 acres for ash monofill.  Of the 44.5 acres for the ash monofill, 31 acres are dedicated to receiving construction and demolition debris (C&D).  Landfill gases (LFGs) generated from waste are collected by a gas collection system and routed to enclosed flares, an open flare, or to a gas treatment plant.  The LFGs from the gas treatment plant is directed to combustion turbines for subsequent use in an electrical power generation plant.  Although the open flare is currently used as an aid to start the turbines, the owner or operator has the option to use it as a primary control device if deemed necessary.

LFGs are primarily composed of methane (CH4) and carbon dioxide (CO2), but also contain non-methane organics (NMOC), volatile organic compounds (VOCs), hazardous air pollutants (HAPs), and H2S.  SO2 and nitrogen oxides (NOx) are generated from the combustion of LFGs in the combustion turbines, the enclosed flares and the open flare.  Particulate matter (PM) emissions result from fugitive dust from roads, earthmoving activities and waste placement and compaction activities.  The existing facility consists of the following emissions units.

| E.U. ID No. | ## Brief Description |
| --- | --- |
| Regulated Emissions Units |  |
| 010 | Landfill Gas (LFG)-Fired Turbines |
| 011 | MSW Class I Landfill with Gas Extraction |
| 012 | 166 Horse Power (HP) Emergency Diesel Generator - Mechanic Shop |
| 013 | 635 HP Emergency Diesel Generator - Desulfurization Plant |
| 014 | 165 HP Emergency Diesel Generator - Area Office |
| 015 | Enclosed Flare (Enclosed Combustor) - South, 4,000 scfm |
| 016 | Enclosed Flare (Enclosed Combustor) - North, 6,000 scfm |
| 017 | Open Flare - 5,100 scfm |
| 018 | 3,000 scfm Mobile Backup Open Flare |
| Unregulated Emissions Units |  |
| 007 | Fugitive NMOC & HAP Emissions from MSW Landfill |
| 009 | Fugitive PM Emissions from Vehicular Traffic |

PROPOSED PROJECT

The applicant submitted an application to the Department on June 21, 2018, (Link to application) requesting authorization to install a 3,000 scfm open flare with flow limited to 12- month rolling total of 1,156.32 MMscf.  The applicant also proposes to install a sulfur treatment system upstream of the flare to remove H2S prior to combustion to minimize emissions of SO2.

This project will add the following emissions units.

| EU No. | Emission Unit Description |
| --- | --- |
| 019 | 3,000 scfm Limited Flow Open Flare |

Facility Regulatory Classification

- The facility is not a major source of HAP.

- The facility does not operate units subject to the acid rain provisions of the Clean Air Act.

- The facility is a Title V major source of air pollution in accordance with Chapter 62-213, F.A.C.

- The facility is a major stationary source in accordance with Rule 62-212.400, F.A.C. for the Prevention of Significant Deterioration (PSD) of Air Quality.

- The facility operates units subject to the NSPS.

- The facility operates units subject to the NESHAP.

- Permitting Authority:  The permitting authority for this project is the Office of Permitting and Compliance in the Division of Air Resource Management of the Department of Environmental Protection (Department).  The Office of Permitting and Compliance mailing address is 2600 Blair Stone Road (MS #5505), Tallahassee, Florida  32399-2400.

- Compliance Authority:  All documents related to compliance activities such as reports, tests, and notifications shall be submitted to the Broward County Environmental Engineering and Permitting Division at:  One North University Drive, Suite 203, Plantation, Florida  33324-2038.

- Appendices:  The following Appendices are attached as a part of this permit:  Appendix A (Citation Formats and Glossary of Common Terms); Appendix B (General Conditions); Appendix C (Common Conditions); Appendix D (Common Testing Requirements); Appendix E (NSPS Subpart A); and Appendix F (NSPS Subpart WWW).

- Applicable Regulations, Forms and Application Procedures:  Unless otherwise specified in this permit, the construction and operation of the subject emissions units shall be in accordance with the capacities and specifications stated in the application.  The facility is subject to all applicable provisions of: Chapter 403, F.S.; and Chapters 62-4, 62-204, 62-210, 62-212, 62-213, 62-296 and 62-297, F.A.C.  Issuance of this permit does not relieve the permittee from compliance with any applicable federal, state, or local permitting or regulations.

- New or Additional Conditions:  For good cause shown and after notice and an administrative hearing, if requested, the Department may require the permittee to conform to new or additional conditions.  The Department shall allow the permittee a reasonable time to conform to the new or additional conditions, and on application of the permittee, the Department may grant additional time.  [Rule 62-4.080, F.A.C.]

- Modifications:  The permittee shall notify the Compliance Authority upon commencement of construction.  No new emissions unit shall be constructed and no existing emissions unit shall be modified without obtaining an air construction permit from the Department.  Such permit shall be obtained prior to beginning construction or modification.  [Rules 62-210.300(1) and 62-212.300(1)(a), F.A.C.]

- Construction and Expiration:  The expiration date shown on the first page of this permit provides time to complete the physical construction activities authorized by this permit, complete any necessary compliance testing, and obtain an operation permit.  Notwithstanding this expiration date, all specific emissions limitations and operating requirements established by this permit shall remain in effect until the facility or emissions unit is permanently shut down.  For good cause, the permittee may request that a permit be extended.  Pursuant to Rule 62-4.080(3), F.A.C., such a request shall be submitted to the Permitting Authority in writing before the permit expires.  [Rules 62-4.070(3) & (4), 62-4.080 & 62-210.300(1), F.A.C.]

- Application for Title V Permit:  This permit authorizes construction of the permitted emissions units and initial operation to determine compliance with Department rules.  A Title V air operation permit is required for regular operation of the permitted emissions unit.  The permittee shall apply for a Title V air operation permit at least 90 days prior to expiration of this permit, but no later than 180 days after commencing operation.  To apply for a Title V operation permit, the applicant shall submit the appropriate application form, compliance test results, and such additional information as the Department may by law require.  The application shall be submitted to the appropriate Permitting Authority with copies to the Compliance Authority.  [Rules 62-4.030, 62-4.050 and Chapter 62-213, F.A.C.]

This section of the permit addresses the following emissions unit.

| EU No. | Emission Unit Description |
| --- | --- |
| 019 | 3,000 scfm Limited Flow Open Flare |

This emissions unit is a 3,000 scfm open flare with flow limited to 12- month rolling total of 1,156.32 MMscf (equivalent to 2,200 scfm).  The landfill gas will be treated prior to flaring to minimize emissions of SO2.

{Permitting Note:  This emission unit is regulated under NSPS Subpart A (General Provisions) and NSPS Subpart WWW (Standards of Performance for Municipal Solid Waste Landfills) of 40 CFR 60, adopted and incorporated by reference in Rules 62-204.800(8)(d) and 62-204.800(b)76., F.A.C. respectively.}

Equipment

- Limited Flow Open Flare:  The permittee is authorized to install a 3,000 scfm open flare.  [Application No. 0112094-014-AC]

- Sulfur Treatment System:  The permittee shall install, operate, and maintain one or more sulfur removal systems, as needed, to comply with the SO2 emissions limit in Specific Condition 6.  [Rule 62-212.400 (PSD Avoidance), F.A.C.; and Application No. 0112094-014-AC]

{Permitting Note:  The sulfur treatment system may comprise of a system of vapor tanks filled with sulfur adsorbent media such as Sulfatreat (or similar media) to remove H2S from the landfill gas prior to flaring to minimize SO2 emissions.}

Performance Restrictions

- Permitted Capacity:  The flow of landfill gas to the flare shall be limited to 1,156.32 MMscf, based on a 12- month rolling total.  [Rules 62-210.200(PTE) and 62-212.400 (PSD Avoidance), F.A.C.]

{Permitting Note:  The 12-month rolling total flow of 1,156.32 MMscf, equates to (but not limited to) an average landfill gas flow of 2,200 scfm.}

- Authorized Fuel:  Only landfill gas shall be fired in the flare.  [Rule 62-210.200(PTE), F.A.C. and Application No. 0112094-014-AC]

- Hours of Operation:  The hours of operation are not limited (8,760 hours/year).  [Rule 62-210.200(PTE), F.A.C.]

##### Emissions Standards

- SO2 Emissions Limit:  Emissions of SO2 from the flare shall not exceed 36 tons/year.  [Rule 62-212.400 (PSD Avoidance), F.A.C.; and Application No. 0112094-014-AC]

- Visible Emissions (VE):  The flare shall be designed for, and operated with, no visible emissions as determined by the method specified in Specific Condition 16 of this subsection, except for periods not to exceed a total of 5 minutes during any 2 consecutive hours.  [Rule 62-204.800(8)(d), F.A.C., and 40 CFR 60.18(c)]

##### OPERATIONAL PROCEDURES

- Operational Standards:

- The flare shall be non-assisted.

- The flare shall be operated with a flame present at all times.

[Rule 62-204.800(8)(d), F.A.C., and 40 CFR 60.18(c)]

- Heat Content Specifications:

- Flares shall be used only with the net heating value of the gas being combusted is 7.45 mega joules per standard cubic meter (MJ/scm) and 200 British thermal units per standard cubic feet (Btu/scf) or greater if the flare is non-assisted.  The net heating value of the gas being combusted in a flare shall be calculated by the following equation:

where:

HT	=  	Net heating value of the sample, MJ/scm; where the net enthalpy per mole of off gas is based on combustion at 25°C and 760 millimeters (mm) mercury (Hg), but the standard temperature for determining the volume corresponding to one mole is 20°C;

where the standard temperature for  is 20°C

Ci  =  	Concentration of sample component i in ppm on a wet basis, as measured for organics by Reference Method 18 and measured for hydrogen and carbon  monoxide by American Society for Testing and Materials (ASTM) D1946–77 or 90 (Reapproved 1994) (Incorporated by reference as specified in 40 CFR 60.17); and

Hi  =  	Net heat of combustion of sample component i, kcal/g mole at 25°C and 760 mm Hg. The heats of combustion may be determined using ASTM D2382–76 or 88 or D4809–95 (incorporated by reference as specified in 40 CFR 60.17) if published values are not available or cannot be calculated.

- The actual exit velocity of a flare shall be determined by dividing the volumetric flow rate (in units of standard temperature and pressure), as determined by Reference Methods 2, 2A, 2C, or 2D as appropriate; by the unobstructed (free) cross sectional area of the flare tip.

- The maximum permitted velocity, Vmax, for flares complying with 40 CFR 60.18 (c)(4)(iii) shall be determined by the following equation:

where,

Vmax  = Maximum permitted velocity, m/sec

28.8  = Constant

31.7  = Constant

HT  = The net heating value as determined in 40 CFR 60.18 (f)(3).

[Rule 62-204.800(8)(d), F.A.C., and 40 CFR 60.18(c) & (f)]

- Maximum Tip Velocity Specifications:  Non-assisted flares shall be designed for and operated with an exit velocity, as determined by the methods specified in 40 CFR 60.18(f)(4), less than 18.3 m/sec (60 feet/sec), except as provided in Specific Conditions 10.a and 10.b below:

- Nonassisted flares designed for and operated with an exit velocity, as determined by the methods specified in paragraph 40 CFR 60.18(f)(4), equal to or greater than 18.3 m/sec (60 ft/sec) but less than 122 m/sec (400 ft/sec) are allowed if the net heating value of the gas being combusted is greater than 37.3 MJ/scm (1,000 Btu/scf).

- Nonassisted flares designed for and operated with an exit velocity, as determined by the methods specified in paragraph (f)(4), less than the velocity, Vmax, as determined by the method specified in paragraph 40 CFR 60.18 (f)(5), and less than 122 m/sec (400 ft/sec) are allowed.

[Rule 62-204.800(8)(d), F.A.C., and 40 CFR 60.18(c)]

- Design Specifications:

- The flare has the option to meet Specific Conditions 9. and 10, or shall meet the following design specifications:  have a diameter of 3 inches or greater; are non-assisted; have a hydrogen content of 8% (by volume), or greater; and are designed for and operated with an exit velocity less than 37.2 m/sec (122 feet/sec) and less than the velocity, Vmax, as determined by the following equation:

Vmax= XH2- K1* K2

where:

Vmax= Maximum permitted velocity, m/sec.

K1 = Constant, 6.0 volume-% hydrogen.

K2 = Constant, 3.9(m/sec)/volume-% hydrogen.

XH2 = The volume-% of hydrogen, on a wet basis, as calculated by using the ASTM Method D1946–77. (Incorporated by reference as specified in 40 CFR 60.17).

- The actual exit velocity of a flare shall be determined by the method specified in 40 CFR 60(f)(4).

[Rule 62-204.800(8)(d), F.A.C. and 40 CFR 60.18(c)]

##### Testing Requirements

- Initial Compliance Tests:  The emissions unit shall be tested to demonstrate initial compliance with the emissions standards for VE.  The initial tests shall be conducted within 60 days after achieving permitted capacity, but not later than 180 days after initial operation of the unit.  [Rules 62-4.070(3) and 62-297.310(8)(b)1, F.A.C.]

- Annual Compliance Tests:  During each calendar year (January 1st to December 31st), the emissions unit shall be tested to demonstrate compliance with the emissions standards for VE.  An annual test is not required if the flare did not operate at the site that year.  [Rule 62-297.310(8)(a)1, F.A.C.]

- Test Requirements:  The permittee shall notify the Compliance Authority in writing at least 15 days prior to any required tests.  Tests shall be conducted in accordance with the applicable requirements specified in Appendix D (Common Testing Requirements) of this permit.  [Rule 62-297.310(9), F.A.C.]

- Test Methods:  Required tests shall be performed in accordance with the following reference methods.

| Method | Description of Method and Comments |
| --- | --- |
| 15 | Determination of Hydrogen Sulfide, Carbonyl Sulfide, And Carbon Disulfide Emissions from Stationary Sources |
| 16 | Semicontinuous Determination of Sulfur Emissions From Stationary Sources |
| 22 | Visual Determination of Fugitive Emissions from Material Sources and Smoke Emissions from Flares |

The above methods are described in Appendix A of 40 CFR 60 and are adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Rules 62-204.800, F.A.C.; and Appendix A of 40 CFR 60]

- Visible Emissions:  The test method for visible emissions shall be EPA Method 22 of Appendix A of 40 CFR 60.  The observation period shall be 2-hours.  [Rule 62-204.800(8)(d), F.A.C. and 40 CFR 60.18(f)(1)]

Monitoring Requirements

- Monitoring of Operations – Open Flare:  Each owner or operator seeking to comply with 40 CFR 60.752(b)(2)(iii) using an open flare shall install, calibrate, maintain, and operate according to the manufacturer's specifications the following equipment:

- A heat sensing device, such as an ultraviolet beam sensor or thermocouple, at the pilot light or the flame itself to indicate the continuous presence of a flame.

- A device that records flow to or bypass of the flare.  The owner or operator shall either:

- Install, calibrate, and maintain a gas flow rate measuring device that shall record the flow to the control device at least every 15 minutes; or

- Secure the bypass line valve in the closed position with a car-seal or a lock-and-key type configuration.  A visual inspection of the seal or closure mechanism shall be performed at least once every month to ensure that the valve is maintained in the closed position and that the gas flow is not diverted through the bypass line.

[Rule 62-204.800(b)76., F.A.C., and 40 CFR 60.756(c)]

- Operational Monitoring:  Using colorimetric tubes (Draeger tube or equivalent), the landfill gas shall be sampled each week the flare is operating, upstream of the sulfur treatment system and prior to the flare.  The sulfur removal media shall be replaced in each sulfur removal system as necessary to ensure compliance with the annual SO2 emissions limit specified in Specific Condition 6.  Colorimetric tube samples shall not be used for compliance demonstration or emission calculation purposes.  [Rule 62-4.070(3), F.A.C. and Application No. 0112094-014-AC]

- H2S Monitoring:  Landfill gas shall be sampled at the flare each week and sent to an accredited laboratory to test for H2S using EPA Method 15 or 16.  [Rule 62-4.070(3), F.A.C. and Application No. 0112094-014-AC]

- SO2 Emissions Monitoring:  To ensure compliance with Specific Condition 6., SO2 emissions shall be calculated on a weekly basis whenever the flare is operating.  [Rule 62-4.070(3), F.A.C. and Application No. 0112094-014-AC]

- Gas Flow Monitoring:  To ensure compliance with the restricted flow limitation in Specific Condition 3., the permittee shall totalize the flow to the flare on a weekly basis when the flare is operating.  [Rule 62-4.070(3), F.A.C. and Application No. 0112094-014-AC]

Records and Reports

- Flare Records:  Except as provided in 40 CFR 60.752(b)(2)(i)(B), each owner or operator of a controlled landfill shall keep up-to-date, readily accessible records for the life of the control equipment of the following data as measured during the initial performance test or compliance determination.  Records of subsequent tests or monitoring shall be maintained for a minimum of 5 years.  Records of the control device vendor specifications shall be maintained until removal.  Where an owner or operator subject to the provisions of NSPS Subpart WWW seeks to demonstrate compliance with 40 CFR  60.752(b)(2)(iii)(A) through use of an open flare, the flare type (i.e., non-assisted), all visible emission readings, heat content determination, flow rate or bypass flow rate measurements, and exit velocity determinations made during the performance test as specified in 40 CFR 60.18; continuous records of the flare pilot flame or flare flame monitoring and records of all periods of operations during which the pilot flame of the flare flame is absent.  [Rule 62-204.800(b)76., F.A.C., and 40 CFR 60.758(b)]

- Notification of Flare Arrival:  The permittee shall notify the Compliance Authority of the make, model, and the date of arrival of the open flare, within 30 days of the unit arriving at the facility.  [Application No. 0112094-014-AC]

- Operational Records:  Records of monitoring as required by Specific Conditions 18 to 21. shall be retained at the facility for at least five years.  A log shall be kept and updated at all times that records SO2 emissions calculated on a weekly basis whenever the flare is operational.  [Rule 62-4.070(3), F.A.C. and Application No. 0112094-014-AC]