### TECHNICAL EVALUATION

&

PRELIMINARY DETERMINATION

#### APPLICANT

Wheelabrator North Broward, Inc.

2600 Wiles Road

Pompano Beach, Florida, 33073

Wheelabrator North Broward Waste-to-Energy Facility

Facility ID No. 0112120

#### PROJECT

# Project No. 0112120-012-AC/PSD-FL-112D

Application for Minor Source Air Construction Permit

Activated Carbon Injection System

#### COUNTY

Broward County, Florida

PERMITTING AUTHORITY

Florida Department of Environmental Protection

Division of Air Resource Management

Office of Permitting and Compliance

2600 Blair Stone Road, MS#5505

Tallahassee, Florida  32399-2400

Date

1.  General Project INFORMATION

Air Pollution Regulations

Projects at stationary sources with the potential to emit air pollution are subject to the applicable environmental laws specified in Section 403 of the Florida Statutes (F.S.).  The statutes authorize the Department of Environmental Protection (Department) to establish regulations regarding air quality as part of the Florida Administrative Code (F.A.C.), which includes the following applicable chapters:  62-4 (Permits); 62-204 (Air Pollution Control – General Provisions); 62-210 (Stationary Sources – General Requirements); 62-212 (Stationary Sources – Preconstruction Review); 62-213 (Operation Permits for Major Sources of Air Pollution); 62-296 (Stationary Sources - Emission Standards); and 62-297 (Stationary Sources – Emissions Monitoring).  Specifically, air construction permits are required pursuant to Chapters 62-4, 62-210 and 62-212, F.A.C.

In addition, the U. S. Environmental Protection Agency (EPA) establishes air quality regulations in Title 40 of the Code of Federal Regulations (CFR).  Part 60 specifies New Source Performance Standards (NSPS) for numerous industrial categories.  Part 61 specifies National Emission Standards for Hazardous Air Pollutants (NESHAP) based on specific pollutants.  Part 63 specifies NESHAP based on the Maximum Achievable Control Technology (MACT) for numerous industrial categories.  The Department adopts these federal regulations in Rule 62-204.800, F.A.C.

Glossary of Common Terms

Because of the technical nature of the project, the permit contains numerous acronyms and abbreviations, which are defined in Appendix A of this permit.

Facility Description and Location

Wheelabrator North Broward Waste-to-Energy Facility is an existing large municipal waste combustor facility, which is categorized under Standard Industrial Classification Code No. 4953.  The existing Wheelabrator North Broward Waste-to-Energy Facility is located in Broward County at 2600 NW 48th Street in Pompano Beach, Florida.  The UTM coordinates of the existing facility are Zone 17, 583.541 km East, and 2907.498 km North.  This site is in an area that is in attainment (or designated as unclassifiable) for all air pollutants subject to Ambient Air Quality Standards (AAQS).

Facility Regulatory Categories

- The facility is a major source of hazardous air pollutants (HAP).

- The facility does not operate units subject to the acid rain provisions of the Clean Air Act.

- The facility is a Title V major source of air pollution in accordance with Chapter 62-213, F.A.C.

- The facility is a major stationary source in accordance with Rule 62-212.400, F.A.C. for the Prevention of Significant Deterioration (PSD) of Air Quality.

- Project Description

- The project requests the installation of an activated carbon injection system on existing municipal solid waste combustor units 1, 2, and 3 (E.U. IDs 001, 002, and 003) to enhance mercury control and minimize mercury emissions.  This project will not change the potential emissions or allowable emissions.  Activated carbon injection is being added to ensure compliance with the allowable mercury emission limit.  The carbon injection system includes the installation of a bulk storage silo with a bin vent filter for the onsite storage of activated carbon; a silo fill station; weight loss carbon feeders; pneumatic conveying blowers; and, feeder/blower control systems with requisite outputs and alarms.

The project also requests changing the testing frequency of mercury from semi-annually to annually upon operation of the activated carbon injection system as the facility will no longer be subject to the emissions standards for facilities using waste separation to control mercury under Rule 62-296.416(b), F.A.C.

In addition, the permit still regulates beryllium which was effectively “delisted” as a PSD pollutant in this rule change effective August 15, 1999 and is being removed from the permit.

Processing Schedule

November 20, 2012	Received the application for a minor source air pollution construction permit.

November 20, 2012	Application complete.

2.  PSD Applicability

General PSD Applicability

For areas currently in attainment with the AAQS or areas otherwise designated as unclassifiable, the Department regulates major stationary sources of air pollution in accordance with Florida’s PSD preconstruction review program as defined in Rule 62-212.400, F.A.C.  Under preconstruction review, the Department first must determine if a project is subject to the PSD requirements (“PSD applicability review”) and, if so, must conduct a PSD preconstruction review.  A PSD applicability review is required for projects at new and existing major stationary sources.  In addition, proposed projects at existing minor sources are subject to a PSD applicability review to determine whether potential emissions from the proposed project itself will exceed the PSD major stationary source thresholds.  A facility is considered a major stationary source with respect to PSD if it emits or has the potential to emit:

- 250 tons per year or more of any regulated air pollutant; or

- 100 tons per year or more of any regulated air pollutant and the facility belongs to one of the following 28 PSD-major facility categories:  fossil fuel-fired steam electric plants of more than 250 million British thermal units per hour heat input, coal cleaning plants (with thermal dryers), Kraft pulp mills, Portland cement plants, primary zinc smelters, iron and steel mill plants, primary aluminum ore reduction plants, primary copper smelters, municipal incinerators capable of charging more than 250 tons of refuse per day, hydrofluoric, sulfuric, and nitric acid plants, petroleum refineries, lime plants, phosphate rock processing plants, coke oven batteries, sulfur recovery plants, carbon black plants (furnace process), primary lead smelters, fuel conversion plants, sintering plants, secondary metal production plants, chemical process plants, fossil fuel boilers (or combinations thereof) totaling more than 250 million British thermal units per hour heat input, petroleum storage and transfer units with a total storage capacity exceeding 300,000 barrels, taconite ore processing plants, glass fiber processing plants and charcoal production plants.

Once it is determined that a project is subject to PSD preconstruction review, the project emissions are compared to the “significant emission rates” defined in Rule 62-210.200, F.A.C. for the following pollutants:  carbon monoxide (CO); nitrogen oxides (NOX); sulfur dioxide (SO2); particulate matter (PM); particulate matter with a mean particle diameter of 10 microns or less (PM10); volatile organic compounds (VOC); lead (Pb); fluorides (F); sulfuric acid mist (SAM); hydrogen sulfide (H2S); total reduced sulfur (TRS), including H2S; reduced sulfur compounds, including H2S; municipal waste combustor organics measured as total tetra- through octa-chlorinated dibenzo-p-dioxins and dibenzofurans; municipal waste combustor metals measured as particulate matter; municipal waste combustor acid gases measured as SO2 and hydrogen chloride (HCl); municipal solid waste landfills emissions measured as non-methane organic compounds (NMOC); and mercury (Hg).  In addition, significant emissions rate also means any emissions rate or any net emissions increase associated with a major stationary source or major modification which would construct within 10 kilometers of a Class I area and have an impact on such area equal to or greater than 1 μg/m3, 24-hour average.

If the potential emission equals or exceeds the defined significant emissions rate of a PSD pollutant, the project is considered “significant” for the pollutant and the applicant must employ the Best Available Control Technology (BACT) to minimize the emissions and evaluate the air quality impacts.  Although a facility or project may be major with respect to PSD for only one regulated pollutant, it may be required to install BACT controls for several “significant” regulated pollutants.

PSD Applicability for Project

There will be no change in currently permitted emissions limits for Units 1, 2, and 3 as a result of this project.  The ability to control mercury emissions will increase with the addition of the activated carbon injection system.  As a result, the potential for any future exceedances of the mercury emission limit will be eliminated.  There will be less than one ton per year of PM/PM10/PM2.5 emissions increase due to the baghouse on the activated carbon storage silo.  No increase in PM/PM10/PM2.5 emissions is expected to occur with the injection of activated carbon into each municipal solid waste boiler.  Therefore, PSD review will not apply.

3.  Department review

Brief Discussion of Emissions

In addition to requesting a permit to construct the activated carbon injection system which is part of the project for the Title V air operation permit revision (Project No. 0112120-013-AV), the applicant requested a change to the testing frequency in the Title V air operation permit conditions.  The mercury emission limit has changed due to a revision to Subpart Cb and needs to be updated.  Additionally, it was noted that the permit still regulates beryllium which was effectively “delisted” as a PSD pollutant in this rule change effective August 15, 1999 and should be removed from the permit.  These changes required revisions to the underlying PSD/air construction permit conditions, which are discussed below in this Technical Evaluation and Preliminary Determination.

The only permit requirement for the activated carbon injection system involves language changes to the PSD Permit that:

- Authorize the installation of the activated carbon injection equipment; and

- Amend the provisions of the PSD Permit related to air pollution control equipment to reflect the installation of the activated carbon injection system.

This will allow construction to begin at the earliest date.  The new limits pursuant to Subpart Cb will be incorporated by a revision to the facility’s Title V operation permit, for which Wheelabrator has already applied.

The conditions are in the enclosed draft PSD permit modification and will include the following provisions:

Installation of Powdered Activated Carbon Injection (ACI) System:  The permittee shall install a system to inject powdered activated carbon in the flue gas from the boiler at a location prior to the acid gas control device (SDA) to provide further control of mercury consisting of a bulk storage silo with a bin vent filter for the onsite storage of activated carbon; a silo fill station; weight loss carbon feeders; pneumatic conveying blowers; and, feeder/blower control systems with requisite outputs and alarms.

Permit Being Modified:  	PSD-FL-112B

Affected Emissions Units:  	302.5 MMBtu/hr (maximum) Municipal Waste Combustor & Auxiliary Burners Unit Nos. 1, 2 and 3 (E.U. ID Nos. 001, 002 & 003)

The “Specific Condition No.” cited below refers to the specific condition in PSD-FL-112B.

- Applicant’s Requested Change:

The applicant requested the mercury limit be updated and the test frequency be changed to annual and the use of the activated carbon injection system for mercury control.  Beryllium will also be removed as a regulated pollutant.

Department’s Response:

The mercury, mercury control and beryllium references are changed to read as follows:

Specific Condition No. 1.a.  The following emissions standards apply to the following emissions units after improvements to comply with 40 CFR Subpart Cb are completed and the initial performance tests are completed.  [Rule 62-204.800(8)(b), 40 CFR 60 Subpart Cb]

| EU No. | Brief Description |
| --- | --- |
| 001 | 302.5 MMBtu/hr (maximum) Municipal Waste Combustor & Auxiliary Burners - Unit No.1 |
| 002 | 302.5 MMBtu/hr (maximum) Municipal Waste Combustor & Auxiliary Burners - Unit No.2 |
| 003 | 302.5 MMBtu/hr (maximum) Municipal Waste Combustor & Auxiliary Burners - Unit No.3 |

(Permitting Note:  Each of the three municipal waste combustors (MWCs) has a nominal design rate capacity of 747 tons MSW per day and 280 MMBtu heat input (with MSW having a heating value of 4,500 Btu per pound).  A maximum capacity of 807 tons per day and 302.5 MMBtu per hour heat input (108% rated capacity) is allowed.  Short-term capacity is limited by limiting steam production (maximum of 186,000 lb/hr), which effectively limits heat input.)

|  |  | EQUIVALENT EMISSIONS2 |  |  |
| --- | --- | --- | --- | --- |
| POLLUTANT | EMISSIONS STANDARDS1 | Lb/mmBtu | lb/hr | TPY |
| PM3 Particulate Matter | 27 mg/dscm or 0.012 gr/dscf corrected to 7% O2 | 0.024 | 7.35 | 32.24 |
| VE Visible Emissions | 10% (6 min. block avg.) |  |  |  |
| Cd Cadmium | 0.040 mg/dscm corrected to 7% O2 | 3.6 E-05 | 0.011 | 0.048 |
| Be4 Beryllium | 0.001 mg/dscm corrected to 7% O2 | 9.3 E-07 | 0.0003 | 0.0012 |
| Pb Lead | 0.44 mg/dscm corrected to 7% O2 | 4.4 E-04 | 0.133 | 0.58 |
| Hg Mercury | 70 50 ug/dscm or 85% reduction by weight or volume corrected to 7% O2 (whichever is less stringent) | 6.3 E-05 4.96 E-05 | 0.019 0.015 | 0.08 0.066 |
| SO2 Sulfur Dioxide | 29 ppmvd or 75% reduction corrected to 7% O2 (whichever is less stringent) | 0.11 | 32.8 | 143.5 |
| HCl Hydrochloric Acid | 29 ppmvd or 95% reduction by weight or volume corrected to 7% O2 (whichever is less stringent) | 0.04 | 11.7 | 51.3 |
| Dioxins/Furans | 30 ng/dscm corrected to 7% O2 | 2.7 E-08 | 8.2 E-06 | 3.6 E-05 |
| NOX Nitrogen Oxides | 205 ppmvd corrected to 7% O2 | 0.35 | 106.5 | 466.4 |
| CO Carbon Monoxide | 100 ppmvd corrected to 7% O2 | 0.105 | 31.8 | 139.1 |
| F Fluorides | Not to exceed 0.0040 lb/MMBtu (BACT limit from original permit) | 0.0040 | 1.21 | 5.29 |

- These maximum allowable emission standards are applicable to each MSW combustor unit and shall be used in demonstrating compliance with the compliance procedures specified in specific conditions d.3.  [Rules 62-4.070 and 62-296.416, F.A.C., 40 CFR 60.33b and 40 CFR 60.34b.]

- Permitting note:  These equivalent emissions are listed for the purposes of providing information on the potential to emit for each MWC and not in determining compliance with applicable emission standards.

- This limit for PM is more restrictive than the emission limit for PM in 40 CFR 60.43b.

- Beryllium:  PSD original permit limit.  Not to exceed applicable NESHAP.  40 CFR 61.32(a)(Subpart C).

Specific Condition No. 1.d.  Compliance Tests

1.d.(2)p.  Method 29, Determination of Metals Emissions from Stationary Sources (I) and (A).  Mercury emissions testing shall be conducted semiannually until such time as the activated carbon injection system becomes operational at which time mercury emissions testing shall be conducted annually.  Mercury stack tests shall be performed downstream of the control devices or upstream and downstream of the control devices when determining compliance with the alternative removal requirement.

Specific Condition No. 8.  Air pollution Control Equipment

8.e.  Mercury is controlled by source separation techniques pursuant to Rule 62-296.416 F.A.C. (New Condition)  The facility shall be equipped with an activated carbon injection system consisting of a bulk storage silo with a bin vent filter for the onsite storage of activated carbon; a silo fill station; weight loss carbon feeders; pneumatic conveying blowers; and, feeder/blower control systems with requisite outputs and alarms.

Revisions

The approved revisions are shown in strikethrough (for deletions) and double-underlines (for additions) format within the permit revision itself.  All changes are emphasized with yellow highlight.

State Requirements

This project is subject to the applicable environmental laws specified in Section 403 of the Florida Statutes (F.S.).  The Florida Statutes authorize the Department of Environmental Protection to establish rules and regulations regarding air quality as part of the F.A.C.  The facility is subject to the applicable rules and regulations defined in the following Chapters of the F.A.C.

| Chapter | Description |
| --- | --- |
| 62-4 | Permits |
| 62-204 | Air Pollution Control – General Provisions |
| 62-210 | Stationary Sources – General Requirements |
| 62-212 | Stationary Sources Preconstruction Review |
| 62-213 | Operation Permits for Major Sources of Air Pollution |
| 62-296 | Stationary Sources – Emissions Standards |
| 62-297 | Stationary Sources – Emissions Monitoring |

Federal Requirements

The facility was or is subject to the applicable federal provisions regarding air quality as established by the EPA in the following sections of the Code of Federal Regulations (CFR).

| Title 40, CFR | Description |
| --- | --- |
| Section 52.21 | Prevention of Significant Deterioration of Air Quality |
| Part 60 | Subpart A Standards of Performance for New Stationary Sources – General Provisions. Subpart Cb Emissions Guidelines and Compliance Times for Large Municipal Waste Combustors that are Constructed Before September 20, 1994. |

4.  Preliminary Determination

The Department makes a preliminary determination that the proposed project will comply with all applicable state and federal air pollution regulations as conditioned by the draft permit.  This determination is based on a technical review of the complete application, reasonable assurances provided by the applicant, and the conditions specified in the draft permit.  No air quality modeling analysis is required because the project does not result in a significant increase in emissions.  Edward Svec is the project engineer responsible for reviewing the application and drafting the permit.  Additional details of this analysis may be obtained by contacting the project engineer at the Department’s Office of Permitting and Compliance at Mail Station #5505, 2600 Blair Stone Road, Tallahassee, Florida  32399-2400.