Permittee

| Highlands EnviroFuels, LLC 10027 Water Works Lane Riverview, Florida 33578 Authorized Representative: Dr. Bradley Krohn, President and Managing Member | Air Permit No. 0550063-004-AC Expires: June 30, 2021 PSD-FL-416A Highlands EnviroFuels Facility ID No. 0550063 Biorefinery and Cogeneration Plant |
| --- | --- |

Project

This is the final air construction permit authorizing the construction of a 36 million gallon per year ethanol production facility using sugarcane and sweet sorghum as the feedstock and a cogeneration power plant that will generate electricity utilizing the leftover agricultural residues as its primary fuel source.  The new facility will use natural fermentation processes to produce ethanol from biomass.  The plant is categorized under Standard Industrial Classification (SIC) No. 2869, and will be located approximately 0.5 miles south-southwest of the intersection of U.S. Highway 27 and State Road 70, south of Lake Placid, in Highlands County, Florida.  The UTM coordinates of the facility are Zone 17, 466.407 kilometers (km) East and 3,009.015 km North.

This final permit is organized into the following sections:  Section 1 (General Information); Section 2 (Administrative Requirements); Section 3 (Emissions Unit Specific Conditions); and Section 4 (Appendices).  Because of the technical nature of the project, the permit contains numerous acronyms and abbreviations, which are defined in Appendix A of Section 4 of this permit.  As noted in the Final Determination provided with this final permit, only minor changes and clarifications were made to the draft permit.

Statement of Basis

This air pollution construction permit is issued under the provisions of:  Chapter 403 of the Florida Statutes (F.S.) and Chapters 62-4, 62-204, 62-210, 62-212, 62-296 and 62-297 of the Florida Administrative Code (F.A.C.).  The permittee is authorized to conduct the proposed work in accordance with the conditions of this permit.  This project is subject to the general preconstruction review requirements in Rule 62-212.300, F.A.C. and the preconstruction review requirements for major stationary sources in Rule 62-212.400, F.A.C. for the Prevention of Significant Deterioration (PSD) of Air Quality.

Upon issuance of this final permit, any party to this order has the right to seek judicial review of it under Section 120.68 of the Florida Statutes by filing a notice of appeal under Rule 9.110 of the Florida Rules of Appellate Procedure with the clerk of the Department of Environmental Protection in the Office of General Counsel (Mail Station #35, 3900 Commonwealth Boulevard, Tallahassee, Florida, 32399-3000) and by filing a copy of the notice of appeal accompanied by the applicable filing fees with the appropriate District Court of Appeal.  The notice must be filed within 30 days after this order is filed with the clerk of the Department.

Executed in Tallahassee, Florida

(DRAFT)

For:  Syed Arif, P.E., Program Administrator

Office of Permitting and Compliance

Division of Air Resource Management

## CERTIFICATE OF SERVICE

# The undersigned duly designated deputy agency clerk hereby certifies that this Final Air Construction Permit package was sent by electronic mail, or a link to these documents made available electronically on a publicly accessible server, with received receipt requested before the close of business on the date indicated below to the following persons.

# Bradley Krohn, Highlands EnviroFuels:  Bkrohn@usenvirofuels.com

# David Buff, P.E., Golder Associates:  Dave_Buff@golder.com

# Gary Maier, DEP South District:  Gary.Maier@dep.state.fl.us

# EPA Region 4 NSR/PSD:  NSRsubmittals@epa.gov

# Lynn Scearce, DEP OPC:  Lynn.Scearce@dep.state.fl.us

# Clerk Stamp

# FILING AND ACKNOWLEDGMENT FILED, on this date, pursuant to Section 120.52(7), Florida Statutes, with the designated agency clerk, receipt of which is hereby acknowledged.

(DRAFT)

PROPOSED PROJECT

The project involves the construction of the Highlands EnviroFuels ethanol production facility that will utilize sugarcane and sweet sorghum as its feedstock to produce up to 36 million gallons per year of ethanol.  In addition, the project involves the construction of a cogeneration plant utilizing the leftover cane and sorghum stalk fiber (bagasse) from the ethanol production process as its primary fuel source.  The cogeneration plant will generate up to 30 megawatts of electricity of which up to 20 MW will be available for sale to the grid.  The sugarcane and sweet sorghum feedstock for the HEF facility will be grown on adjacent and surrounding farmland.  Juice will be extracted from the sugarcane and sweet sorghum and processed to increase its sucrose (sugar) concentration.  The concentrated juice will then be fermented to convert the sugars to ethanol.  The distilled ethanol will be blended with gasoline to yield a denatured ethanol product.

The sugarcane and sweet sorghum bagasse will be burned in a biomass boiler with a maximum heat input rate of 504.3 million British thermal units per hour (MMBtu/hr) on a 4-hour average basis and 458.5 MMBtu/hr on a 24-hour average basis.  In addition to cane and sorghum bagasse, the HEF biomass boiler will also burn biomass consisting of energy crops, wood chips and vegetative debris and natural gas.  The biomass boiler will generate steam that will be utilized in the ethanol production process and in a steam turbine electrical generator (STG) to produce electrical power.  The energy crops, wood chips and vegetative debris will be used as a supplemental fuel in the boiler.  The natural gas will be used as the boiler startup, shutdown and flame stabilization fuel, and also in the event of a disruption in the biomass supply.  Ultra-low sulfur distillate (ULSD) fuel oil will be used in emergency equipment (one generator and one fire pump engine).

The project was originally permitted in September 2011, in Permit No. 0550063-001-AC/PSD-FL-416.  However, a period of more than 18 months elapsed between the issuance of the permit and the commencement of construction of the facility.  Therefore, the original determination of Best Available Control Technology (BACT) for the facility has expired.  This new permit supersedes the original air construction permit for this facility (Permit No. 0550063-001-AC/PSD-FL-416).

This project includes the following emissions units.

| EU No. | Emission Unit Description |
| --- | --- |
| 001 | Feedstock and Biomass Material Handling and Preparation |
| 002 | Biomass Boiler |
| 003 | Cooling Towers |
| 004 | Ethanol Production Process |
| 005 | Product Loadout and Flare |
| 006 | Storage Tanks |
| 007 | Miscellaneous Storage Silos |
| 008 | Emergency Equipment |
| 009 | Facility-Wide Fugitive Volatile Organic Compounds (VOC) Equipment Leaks |

Facility Regulatory Classification

- The facility is a major source of hazardous air pollutants (HAP).

- The facility does not operate units subject to the acid rain provisions of the Clean Air Act (CAA).

- The facility is a Title V major source of air pollution in accordance with Chapter 62-213, F.A.C.

- The facility is a major stationary source in accordance with Rule 62-212.400(PSD), F.A.C.

- Permitting Authority:  The Permitting Authority for this project is the Office of Permitting and Compliance in the Division of Air Resource Management of the Department of Environmental Protection (Department).  The mailing address for the Office of Permitting and Compliance is 2600 Blair Stone Road, MS #5505, Tallahassee, Florida  32399-2400.  All documents related to applications for permits to operate an emissions unit shall be submitted to the Office of Permitting and Compliance.

- Compliance Authority:  All documents related to compliance activities such as reports, tests, and notifications shall be submitted to the Department’s South District Office at:  2295 Victoria Avenue, Suite 364, Fort Myers, Florida  33901-3881.

- Appendices:  The following Appendices are attached as a part of this permit:

- Appendix A:	Citation Formats and Glossary of Common Terms

- Appendix B:	General Conditions

- Appendix C:	Common Conditions

- Appendix D:	Common Testing Requirements

- Appendix E:	BACT Determination

- Appendix ASME:  	American Society of Mechanical Engineers (ASME) Form for Abbreviated 		Efficiency Test;

- Appendix BMP:	Best Management Practices;

- Appendix Db:	NSPS, Subpart Db – Standards of Performance for Small Industrial-Commercial- 	Institutional Steam Generating Units;

- Appendix DDDDD:	NESHAP Subpart DDDDD – Industrial, Commercial, and Institutional Boilers and 	Process Heaters at Major Sources of HAP

- Appendix F:	40 Code of Federal Regulations (CFR) Part 75, Appendix F, Section 5 –  	Measurement of Boiler Heat Input Rate;

- Appendix FFFF:	NESHAP Subpart FFFF – Miscellaneous Organic Chemical Manufacturing

- Appendix GP:	Identification of General Provisions, Subpart A from NSPS 40 CFR 60 and Subpart 	A from NESHAP 40 CFR 63;

- Appendix IIII:	NSPS, Subpart IIII – Stationary Compression Ignition Internal Combustion Engines;

- Appendix Kb:	NSPS, Subpart Kb – Standards of Performance for Volatile Organic Liquid Storage 	Vessels;

- Appendix LDAR:	Preliminary Leak Detection and Repair (LDAR) Program;

- Appendix VVa:	NSPS, Subpart VVa – Standards of Performance for Equipment Leaks of Volatile 	Organic Compounds (VOC) in the Synthetic Organic Chemical Manufacturing 	Industry (SOCMI)

- Applicable Regulations, Forms and Application Procedures:  Unless otherwise specified in this permit, the construction and operation of the subject emissions units shall be in accordance with the capacities and specifications stated in the application.  The facility is subject to all applicable provisions of: Chapter 403, F.S.; and Chapters 62-4, 62-204, 62-210, 62-212, 62-213, 62-296 and 62-297, F.A.C.  Issuance of this permit does not relieve the permittee from compliance with any applicable federal, state, or local permitting or regulations.

- New or Additional Conditions:  For good cause shown and after notice and an administrative hearing, if requested, the Department may require the permittee to conform to new or additional conditions.  The Department shall allow the permittee a reasonable time to conform to the new or additional conditions, and on application of the permittee, the Department may grant additional time.  [Rule 62-4.080, F.A.C.]

- Modifications:  No emissions unit shall be constructed or modified without obtaining an air construction permit from the Department.  Such permit shall be obtained prior to beginning construction or modification.  [Rules 62-210.300(1) and 62-212.300(1)(a), F.A.C.]

- Construction and Expiration.  The expiration date shown on the first page of this permit provides time to complete the physical construction activities authorized by this permit, complete any necessary compliance testing, and obtain an operation permit.  Notwithstanding this expiration date, all specific emissions limitations and operating requirements established by this permit shall remain in effect until the facility or emissions unit is permanently shut down.  For good cause, the permittee may request that that a permit be extended.  Pursuant to Rule 62-4.080(3), F.A.C., such a request shall be submitted to the Permitting Authority in writing before the permit expires.  [Rules 62-4.070(3) & (4), 62-4.080 & 62-210.300(1), F.A.C.]

- Source Obligation:

- Authorization to construct shall expire if construction is not commenced within 18 months after receipt of the permit, if construction is discontinued for a period of 18 months or more, or if construction is not completed within a reasonable time.  This provision does not apply to the time period between construction of the approved phases of a phased construction project except that each phase must commence construction within 18 months of the commencement date established by the Department in the permit.

- At such time that a particular source or modification becomes a major stationary source or major modification (as these terms were defined at the time the source obtained the enforceable limitation) solely by virtue of a relaxation in any enforceable limitation which was established after August 7, 1980, on the capacity of the source or modification otherwise to emit a pollutant, such as a restriction on hours of operation, then the requirements of subsections 62-212.400(4) through (12), F.A.C., shall apply to the source or modification as though construction had not yet commenced on the source or modification.

- At such time that a particular source or modification becomes a major stationary source or major modification (as these terms were defined at the time the source obtained the enforceable limitation) solely by exceeding its projected actual emissions, then the requirements of subsections 62-212.400(4) through (12), F.A.C., shall apply to the source or modification as though construction had not yet commenced on the source or modification.

[Rule 62-212.400(12), F.A.C.]

- Title V Permit:  This permit authorizes specific modifications and/or new construction on the affected emissions units as well as initial operation to determine compliance with conditions of this permit.  A Title V operation permit is required for regular operation of the permitted emissions unit.  The permittee shall apply for a Title V operation permit at least 90 days prior to expiration of this permit, but no later than 180 days after completing the required work and commencing operation.  To apply for a Title V operation permit, the applicant shall submit the appropriate application form, compliance test results, and such additional information as the Department may by law require.  The application shall be submitted to the appropriate Permitting Authority with copies to each Compliance Authority.  [Rules 62-4.030, 62-4.050 and Chapter 62-213, F.A.C.]

- Unconfined Emissions of Particulate Matter:  No person shall cause, let, permit, suffer or allow the emissions of unconfined particulate matter from any activity: including vehicular movement; transportation of materials; construction, alteration, demolition or wrecking; or industrially related activities such as loading, unloading, storing or handling without taking reasonable precautions to prevent such emissions.  Any permit issued to a facility with emissions of unconfined particulate matter shall specify the reasonable precautions to be taken by that facility to control the emissions of unconfined particulate matter.  Reasonable precautions include the following:

    - Paving and maintenance of roads, parking areas and yards;

    - Application of water or chemicals to control emissions from such activities as demolition of buildings, grading roads, construction and land clearing;

    - Application of asphalt, water, oil, chemicals or other dust suppressants to unpaved roads, yards, open stock piles and similar activities;

    - Removal of particulate matter from roads and other paved areas under the control of the owner or operator of the facility to prevent re-entrainment, and from buildings or work areas to prevent particulate from becoming airborne;

    - Landscaping or planting of vegetation;

    - Use of hoods, fans, filters and similar equipment to contain, capture and/or vent particulate matter;

    - Confining abrasive blasting where possible; and,

    - Enclosure or covering of conveyor systems.  In determining what constitutes reasonable precautions for a particular facility, the Department shall consider the cost of the control technique or work practice, the environmental impacts of the technique or practice and the degree of reduction of emissions expected from a particular technique or practice.

[See also Appendix BMP; Rule 62-296.320(4)(c), F.A.C.]

- NSPS Subpart VVa:  Emission units associated with the HEF project that can leak VOC are subject to NSPS Subpart VVa – Standards of Performance for Equipment Leaks of VOC in the SOCMI.  Equipment such as pumps, compressors, pressure relief devices, sampling connection systems, open-ended valves, line valves and flanges or other connectors in VOC service and any devices or systems subject to NSPS, Subpart VVa, and the associated emissions unit must be identified.  The permittee must submit a list identifying the devices or systems to the Compliance Authority no later than 90 days before the HEF facility becomes operational.  A requirement of Subpart VVa is the development of a LDAR program.  A preliminary LDAR program plan is included as Appendix LDAR in Section 4 of this permit.  The permittee is required to submit a final LDAR program plan to the Compliance Authority for approval no later than 90 days before the HEF facility becomes operational.  The HEF facility must demonstrate compliance with NSPS, Subpart VVa no later than 180 days after the initial startup of the HEF facility.  [NSPS Subpart VVa and Rule 62-4.070(3), F.A.C.]

- Objectionable Odors Prohibited:  No person shall cause, suffer, allow or permit the discharge of air pollutants which cause or contribute to an objectionable odor.  The permittee shall submit an odor control plan (OCP) to the Compliance Authority no later than 90 days before the HEF facility becomes operational that addresses the procedures and practices that will be used to control facility wide odors.  
[Rule 62-296.320(2), F.A.C. and Rule 62-4.070, F.A.C.]

{Permitting Note:  An objectionable odor is defined in Rule 62-210.200(Definitions), F.A.C., as any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property; or which creates a nuisance.}

- Open Burning Prohibited:  No person shall ignite, cause to be ignited or permit to be ignited any material which will result in any prohibited open burning as regulated by Chapter 62-256, F.A.C.; nor shall any person suffer, allow, conduct or maintain any prohibited open burning.  
[Rule 62-256.300, F.A.C.]

This section of the permit addresses the following emissions unit.

| ID No. | Emission Unit Description |
| --- | --- |
| 001 | Feedstock and biomass material handling and preparation consists of the following major functions: - Feedstock Harvesting: Both sugarcane and sweet sorghum stalks will be harvested as 6-inch to 12-inch billets from adjacent and nearby agricultural lands and transported to the HEF facility by truck or rail. The harvesting methods employed will ensure that “trash”, i.e., cane and sorghum leaves and tops, will be minimized in the delivered feedstock. It is expected that “trash” will constitute less than 8 percent (%) by weight of the delivered feedstock to the facility. - Processing the Feedstock: The loaded trucks/railcars will be weighed on a weighing bridge as they enter the unloading area. The cane or sorghum in the trucks will then be transferred to the feed table via a tipping trailer. Railcars will be bottom dumped into a feed hopper, which feeds the feed table. The feed table is equipped with chains that convey the sugar cane and sweet sorghum billets toward the main conveyor that feeds the juice extraction system. - Juice Extraction: The feedstock will be passed through high efficiency knives and a heavy-duty shredder to increase the surface area of the material. Then the feedstock passes to a belt conveyor and then to the diffuser. The diffuser is designed to carry a uniform layer of feedstock through the diffuser and across the entire width of the diffuser to obtain maximum sucrose removal. Imbibition water is fed into the juice trough and falls onto the processed feedstock mat, percolates through the fibers, passes across the screen and is collected in the last juice receiver. From the juice receiver, this solution with low sucrose concentration is recirculated upstream back to the juice trough and falls again onto the feedstock mat. This recirculation continues to create a countercurrent pattern and a constant sucrose concentration gradient between the feedstock mat moving downstream and the recirculating juice moving upstream. The feedstock exiting the diffuser is termed “bagasse.” The moisture content of the bagasse when it leaves the diffuser is approximately 80%. To reduce the moisture content further, the bagasse is sent through a dewatering mill system. The mill presses the bagasse until the moisture content is reduced to approximately 50%. - Boiler Fuel Feedstock (Biomass): Sugarcane and sweet sorghum bagasse from the juice extraction process will be used as the primary fuel in the HEF biomass boiler. The bagasse will be sent directly to the boiler or stored in a storage pile in the biomass yard. Biomass consisting of energy crops, wood chips and vegetative debris will be used as a supplemental boiler fuel. Natural gas will be used for boiler startup, shut down and flame stabilization and also in the event of a disruption in the biomass supply. - Biomass Fuel Feed System: A single biomass fuel feed system for the boiler will be used. The system will consist of a dewatering system for the cane and sorghum bagasse, covered conveyors, boiler metering bins and biomass storage piles (bagasse and supplemental biomass). The biomass fuel will be fed from the storage piles to the conveyor system using front-end loaders. Only one feed system is required, since bagasse and supplemental biomass may be fired in combination in the boiler. - Biomass Design Throughput: Under normal operation (no supplemental biomass burning), the amount of bagasse burned in the boiler is estimated to be 236,300 tons per year (TPY) each of cane and sorghum bagasse. A maximum 43,368 TPY of supplemental biomass may be burned in combination with 212,670 TPY each of cane and sorghum bagasse. |

Equipment

- Biomass Delivery, Handling and Preparation:  The permittee is authorized to install the following major pieces of equipment for the delivery, handling and processing of the sugarcane and sweet sorghum used in the ethanol production process and the bagasse and supplemental biomass used as boiler fuel:

  - Weighing bridge truck scale(s);

  - Tipping trailer/railcar unloader(s);

  - Sugar cane and sweet sorghum bagasse press drying system;

  - Feed table with transfer chains;

  - Enclosed transfer conveyors consisting of reclaim, return, transfer, distribution and surplus conveyors; and

  - Biomass yard containing biomass fuel storage piles (bagasse and biomass).

[Application Nos. 0550063-001-AC and 0550063-004-AC; Rule 62-4.070(3), F.A.C.]

- Air Pollution Control Equipment:  To minimize fugitive particulate matter (PM), PM with a mean diameter of 10 micrometers (µm) or less (PM10) and PM with a mean diameter of 2.5 µm or less (PM2.5); henceforth called PM, biomass conveyors shall be enclosed.  If required to meet the opacity requirement given in Specific Condition 10 of this subsection, the permittee shall install dust collectors on the conveyor transfer and drop points.  The dust collectors shall be designed to obtain an outlet PM loading of 0.005 grains per dry standard cubic foot (gr/dscf).

{Permitting Note:  Enclosed conveyors means that the conveyance belt for the biomass is totally enclosed from above thus preventing wind from causing fugitive dust emissions.  However, the bottom of the conveyance belt shall be accessible for maintenance and repairs.}

[Rules 62-212.400 (BACT) and 62-4.070(3), F.A.C.]

- Fugitive Dust Control:  HEF shall utilize reasonable precautions for controlling fugitive PM emissions from this emission unit.  These include but are not limited to:

- Enclosing material drop points, transfer points, shredders and screens wherever practical;

- Contouring storage piles to minimize wind erosion;

- Utilizing water sprays on storage piles as needed to prevent fugitive dust caused by biomass from leaving the property;

- Paving all main plant roads;

- Watering of gravel surfaces as needed to control dust; and

- Sweeping and watering of paved surfaces as needed to remove dust.

The permittee shall also comply with additional precautions listed in Appendix BMP- Best Management Practices and Condition 10 of Section 2 of this permit.

[Rules 62-212.400 (BACT) and 62-4.070(3), F.A.C.]

Performance Restrictions

- Roadways:  The plant roadways shall be paved and during dry conditions wetted sufficiently to maintain surface moisture to minimize fugitive dust emissions.  Roadways shall be swept as necessary with a vacuum sweeper in good working order to prevent the buildup of dirt and silt on the roadway surfaces.  A record of the sweeping shall be kept and made available to the Compliance Authority upon request.  
[Rules 62-212.400 (BACT) and 62-4.070(3), F.A.C.]

- Gravel Areas:  The gravel surfaces at the HEF facility shall be wetted sufficiently during dry conditions to maintain surface moisture to minimize fugitive dust emissions.  A record of the wetting shall be kept and made available to the Compliance Authority upon request.  
[Rules 62-212.400 (BACT) and 62-4.070(3), F.A.C.]

- Bagasse and Supplemental Biomass Storage Piles:  The boiler fuel (bagasse and biomass) storage piles will be located in the fuel yard in the southwestern quadrant of the HEF site.  To control odors and minimize the chance of spontaneous combustion, bagasse and biomass in the storage piles shall be used in a first-in first-out (FIFO) basis.  To prevent fugitive dust caused by biomass from leaving the property, the plant shall apply water if necessary; otherwise, the material shall be kept dry to facilitate burning.  Contouring storage piles shall be done to minimize wind erosion.  Overall, fuel storage pile management shall follow the procedures described in Appendix BMP of this permit.  
[Application Nos. 0550063-001-AC and 0550063-004-AC; Rules 62-212.400 (BACT) and 62-4.070(3), F.A.C.]

- Authorized Ethanol Production Feedstock:  Feedstock used in the ethanol production process at the HEF facility shall be sugarcane and sweet sorghum.  In addition, sweet sorghum syrup/molasses and/or sugarcane molasses may be used as the feedstock when sugarcane and sweet sorghum feedstocks are in low supply or not available.  [Application Nos. 0550063-001-AC and 0550063-004-AC; Rule 62-4.070(3), F.A.C.]

- Authorized Boiler Fuel Biomass:  Biomass fuel authorized to be used in the biomass boiler at the HEF facility consists of sugarcane and sweet sorghum bagasse and supplemental biomass consisting of energy crops, wood chips and vegetative debris.  Appendix BMP further defines the types of biomass that shall and shall not be used at the HEF facility in the ethanol production process and as boiler fuel and includes quality assurance (QA) procedures to ensure the biomass used meets the requirements specified in this permit.  [Application Nos. 0550063-001-AC and 0550063-004-AC; Rule 62-4.070(3), F.A.C.]

- Hours of Operation:  The hours of operation of this emission unit are not limited (8,760 hours per year).  [Application Nos. 0550063-001-AC and 0550063-004-AC; Rules 62-4.070(3) and 62-210.200(PTE), F.A.C.]

##### Emissions Standards

- Opacity Standard:  As determined by EPA Method 9, there shall be no visible emissions (VE) greater than 5% opacity at drop points, transfer points and dust collector outlets that are required to meet this VE standard.  [Rule 62-212.400(5)(c), F.A.C.]

- Best Management Practices (BMP):  A plan to control PM emissions from biomass (sweet sorghum bagasse, sweet sorghum bagasse and supplemental biomass) delivery, handling and preparation is given in Appendix BMP and shall be followed at all times by the permittee.  This plan also addresses measures to minimize the chance of the spontaneous combustion of biomass storage piles and QA measures for biomass delivered to the HEF facility.  As the engineering details of the Feedstock Delivery, Handling and Preparation emissions unit become finalized, the permittee shall submit an updated BMP plan to the Compliance Authority no later than 90 days before the HEF facility becomes operational.  
[Rules 62-212.400 (BACT) and 62-4.070(3), F.A.C.]

{Permitting Note:  PM emissions from biomass deliveries, bagasse handling and supplemental biomass handling during operation of the HEF facility are estimated to be 7.9 tons in any consecutive twelve month period., per Application No. 0550063-001-AC.}

Testing AND Monitoring Requirements

- Initial Compliance Tests:  The drop points, transfer points and dust collector outlets (if installed) of this emissions unit shall be tested to demonstrate initial compliance with the emissions standards for opacity given in Specific Condition 10 of this subsection.  The initial tests shall be conducted within 60 days after achieving permitted capacity, but not later than 180 days after initial operation of the unit.  
[Rules 62-4.070(3) and 62-297.310(8)(b)1, F.A.C.]

- Annual Compliance Tests:  During each calendar year (January 1 to December 31), the drop points, transfer points and dust collector outlets (if installed) of the emissions unit shall be tested to demonstrate compliance with the emissions standards for opacity given in Specific Condition 10 of this subsection.  [Rules 62-4.070(3) and 62-297.310(8)(a)4, F.A.C.]

- Test Requirements:  The permittee shall notify the Compliance Authority in writing at least 15 days prior to any required tests.  Tests shall be conducted in accordance with the applicable requirements specified in Appendix D (Common Testing Requirements) of this permit.  [Rule 62-297.310(9), F.A.C.]

- Test Methods:  Required tests shall be performed in accordance with the following reference methods.

| Method | Description of Method and Comments |
| --- | --- |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources. |

The above method is described in Appendix A of 40 CFR 60 and is adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Rule 62-204.800, F.A.C.; Appendix A of 40 CFR 60]

Records and Reports

- Test Reports:  The permittee shall prepare and submit reports for all required tests in accordance with the requirements specified in Appendix D (Common Testing Requirements) of this permit.  For each test run, the report shall also indicate the operating rate.  [Rule 62-297.310(10), F.A.C.]

- Notification, Recordkeeping and Reporting Requirements:  The permittee shall maintain records of the amount of biomass consisting of sugarcane, sweet sorghum, sweet sorghum syrup/molasses, sugarcane syrup/molasses, energy crops, wood chips and vegetative debris delivered, handled and processed on a daily, monthly, quarterly and 12-month rolling average basis.  These records shall be submitted to the Compliance Authority on a semi-annual basis or upon request.  [Rule 62-4.070(3), F.A.C.]

This section of the permit addresses the following emissions unit.

| ID No. | Emission Unit Description |
| --- | --- |
| 002 | Description: The boiler will be a hybrid suspension/stoker (grate) type boiler wherein biomass (sugarcane bagasse, sweet sorghum bagasse and supplemental biomass) and natural gas are combusted to generate high temperature and high pressure steam. The steam will then be used in the ethanol production process and also sent to a STG to generate up to 30 MW (gross) of electrical power. Fuels: Sugarcane and sweet sorghum bagasse, a residual from the ethanol production process, will be used as the primary fuel in the biomass boiler with biomass consisting of energy crops, wood chips and vegetative debris used as a supplemental fuel. In addition, the boiler will be capable of combusting natural gas for startup, shutdown and flame stabilization and also in the event of a disruption in the biomass supply. Capacity: The maximum design heat input capacity to the boiler is 504.3 MMBtu/hr on a 4-hour basis and 458.5 MMBtu/hr on a 24-hour basis. Steam production capability will be approximately 275,000 pounds per hour (lb/hr) on a 4-hour basis and 250,000 lb/hr on a 24-hour basis. The maximum heat input capacity using natural gas in the biomass boiler shall be physically constrained by burner design to be less than 250 MMBtu/hr so the boiler is not subject to 40 CFR 60 NSPS, Subpart Da. Controls: Good combustion practices (GCP) leading to the efficient combustion of biomass in the boiler, including an over-fired air (OFA) system, to minimize formation of PM, nitrogen oxides (NOX), carbon monoxide (CO), VOC and HAP; Selective Non-Catalytic Reduction (SNCR) with urea or anhydrous ammonia (NH3) injection to destroy NOX; an oxidation catalyst (Ox-cat) system to control VOC, CO and organic HAP; use of natural gas fired in low-NOX burners (LNB) for boiler startup, shutdown and flame (bed) stabilization to minimize formation of PM, NOX, sulfur dioxide (SO2) and HAP; and a wet sand separator (cyclone) and a electrostatic precipitator (ESP) to further control PM and opacity. If necessary to meet limits for SO2, a dry sorbent injection system (DSIS) utilizing sodium bicarbonate, hydrated lime, or trona to control SO2, sulfuric acid mist, (SAM) and acid gas HAP may be added. Stack Parameters: Flue gas from the biomass boiler will discharge to the atmosphere via a stack with a design height of 150 feet and a design diameter of 14 feet. The flue gas exit temperature will be approximately 340 degrees Fahrenheit (°F) with a design volumetric flow rate of 204,080 actual cubic feet per minute (acfm). Continuous Emissions and Opacity Monitoring Systems (CEMS): Emissions of CO, NOX, SO2 and CO2 will be monitored and recorded by CEMS. Applicability of 40 CFR 60 Subpart Db: This unit is subject to NSPS Subpart Db - Industrial-Commercial-Institutional Steam Generating Units because it has a maximum heat input capacity greater than 100 MMBtu/hr from combusted fuels, and it is not subject to NSPS Subpart Da because it has a maximum heat input capacity less than 250 MMBtu/hr from combusted fossil fuels. [Application Nos. 0550063-001-AC and 0550063-004-AC] Applicability of 40 CFR 63 Subpart DDDDD: This unit is subject to NESHAP Subpart DDDDD for boilers at major sources of HAP. [Application No. 0550063-004-AC] |

{Permitting Note:  In accordance with Rule 62-212.400, F.A.C., the Department established permit standards for the biomass-fueled boiler that represent the BACT for emissions of NOX, PM, PM10, PM2.5, VOC, SO2, CO, and greenhouse gases (GHG).  The biomass-fueled boiler is subject to the federal NSPS in Subpart Db (industrial boilers) of 40 CFR 60, which is adopted by reference in Rule 62-204.800, F.A.C.  NSPS Subpart Db for Industrial Boilers is provided in Appendix Db of this permit.  The boiler is also subject to the NESHAP in 40 CFR 63 Subpart DDDDD, for boilers at major sources of HAP.}

Equipment

- Construction of Biomass-Fueled Boiler:  The permittee is authorized to construct one biomass-fueled hybrid suspension/stoker (grate) type boiler at the HEF facility with maximum steam generation rates of 275,000 pounds per hour (lb/hr) on a 4-hour average basis and 250,000 lb/hr on a 24-hour average basis for steam and power generation.  The boiler shall have a multi-stage superheater, air heater and economizer.  LNBs shall be utilized for natural gas firing. The boiler shall include:

- Biomass fuel feeders;

- High-performance OFA system consisting of air headers, air nozzles, dampers and an OFA fan;

- Soot blowers;

- Forced draft (FD) fan;

- Induced draft (ID) fan;

- Pneumatic distribution air fans; and

- Vibrating grate for ash removal.

- One steam turbine electrical generator (STG).

[Application Nos. 0550063-001-AC and 0550063-004-AC]

- Air Pollution Control Equipment:  To comply with the emission standards of this subsection, the permittee shall install the following air pollution control equipment on the biomass boiler.

- Wet Sand Separator (Cyclone):  The permittee shall design, install, operate and maintain a wet sand separator to remove fine sand particles from the flue gas exhaust prior to the ESP.  The wet sand separator shall be on line and functioning properly whenever the boiler is in operation.  If necessary, the wet sand separator shall be modified to aid in the removal of acid gases to meet the emission limits specified in this subsection.

- ESP:  The permittee shall design, install, operate and maintain an ESP to remove PM from the flue gas exhaust and achieve the PM standards specified in this subsection.  During startup conditions, the ESP shall be on line and functioning properly prior to combusting any biomass.  During normal operation, the ESP shall be on line and functioning properly at all times.

- SNCR:  The permittee shall design, install, operate and maintain a urea or NH3 based SNCR system to reduce NOX emissions in the flue gas exhaust and achieve the NOX emissions standard specified in this subsection.  The SNCR system shall be on line and functioning properly whenever the boiler is in operation, other than during startup conditions.  During startup conditions, the SNCR manufacturer’s instructions shall be followed regarding operation of the system.

- Ox-cat:  The permittee shall install an Ox-cat system to control, in conjunction with GCP, emissions of CO to the standards specified in this subsection.  The installation of the Ox-cat system is initially experimental in nature to determine if the Ox-cat catalyst lifetime is adversely effected by the alkali nature of the flue gas stream.  After 24 months of initial Ox-cat operation, a test report per Specific Condition 11 of this subsection will be submitted to the Department describing Ox-cat performance versus time with regard to CO emissions.

- Circumvention:  The permittee shall not circumvent the air pollution control equipment or allow the emission of air pollutants without this equipment operating properly.  [Rule 62-210.650, F.A.C.]

- DSIS:  The permittee shall leave space for the installation of a DSIS to inject lime, trona or sodium bicarbonate into the flue gas to control SO2 emissions to the limit specified in this subsection.  The DSIS will also help control acid gas HAP emissions.  The SO2 CEMS output data expressed in lbs/hr averaged over a 24-hour period shall be reviewed by plant personnel on a daily and monthly basis to determine if installation and operation of a DSIS is necessary to ensure the HCl and SO2 emission.  CEMS-based SO2 emissions data shall be reported to the Department on a quarterly basis.  The DSIS will be required only if the applicable emission limits in this permit cannot be met without it.

[Application Nos. 0550063-001-AC and 0550063-004-AC; Rules 62-212.400(10) (PSD), 62-4.070(3), and 62-210.200(PTE), F.A.C.]

NSPS Applicability

- Subpart Db – Steam Generating Units:  The HEF biomass boiler must meet all applicable requirements of NSPS 40 CFR 60, Subpart Db – Industrial-Commercial-Institutional Steam Generating Units.  Subpart Db is contained in Appendix Db of this permit.  For the HEF biomass boiler, NSPS Subpart Db contains limits for SO2 and NOX.  Subpart Db also contains applicable limits for PM and visible emissions if the boiler fires wood or wood chips in any quantity.  [Application Nos. 0550063-001-AC and 0550063-004-AC; 40 CFR 60, Subpart Db]

Neshap Applicability

- Subpart DDDDD – Industrial, Commercial, and Institutional Boilers and Process Heaters at Major Sources of HAP:  The HEF biomass boiler must meet all applicable requirements of 40 CFR 63, Subpart DDDDD – NESHAP for Major Sources:  Industrial, Commercial, and Institutional Boilers and Process Heaters.  Subpart DDDDD is contained in Appendix DDDDD of this permit.  Subpart DDDDD includes emission limits for hydrogen chloride (HCl), mercury (Hg), CO, and PM and requires an annual tune-up of the boiler.  The Subpart also includes work practices for startup and shutdown.  [Application Nos. 0550063-001-AC and 0550063-004-AC; 40 CFR 63, Subpart DDDDD]

Performance Requirements

- Authorized Fuels:  The biomass boiler is authorized to combust as its primary fuels sugarcane and sweet sorghum bagasse that is a byproduct from the ethanol production process.  Biomass consisting of energy crops, wood chips and vegetative debris will be used as a supplemental boiler fuel.  In addition, the boiler is authorized to combust natural gas for startup, shutdown and flame stabilization and also in the event of a disruption in the biomass supply.  [Application Nos. 0550063-001-AC and 0550063-004-AC; Rules 62-4.070(3) and 62-210.200(PTE), F.A.C.]

- Boiler Heat Input Rate:  The maximum heat input rate from all fuel combinations in the biomass boiler is 504.3 MMBtu/hr on a 4-hour average basis and 458.5 MMBtu/hr on a 24-hour average basis.  Emission rates are based on the heat input of 458.5 MMBtu/hr.  The permittee shall use the thermal efficiency method to calculate the boiler heat input rate, using the steam rate, steam pressure, and steam temperature measurements required per Specific Condition 22 of this subsection, and feedwater temperature and pressure, to determine net enthalpy.  The design boiler efficiency shall be used provided the boiler efficiency test required in Specific Condition 21 of this subsection is at least 90% of the design boiler efficiency.  The procedure given in Appendix ASME of this permit shall be used to measure the boiler efficiency.  As an alternative, the procedures given in Appendix F of this permit may be used to calculate boiler heat input.  [Application Nos. 0550063-001-AC and 0550063-004-AC; Rules 62-4.070(3) and 62-210.200(PTE), F.A.C.]

- Heat Input from Fossil Fuels:  The maximum heat input capacity from combusting natural gas in the biomass boiler, as determined by the physical design of the boiler and design characteristics of the boiler burners shall be less than 250 MMBtu/hr.  The maximum amount of natural gas that shall be fired in the boiler in any 12-month consecutive period is 1,021 million standard cubic feet (MMscf).  [Application Nos. 0550063-001-AC and 0550063-004-AC; NSPS Subpart Db; Rules 62-4.070(3); and 62-210.200(PTE), F.A.C.]

- Hours of Operation:  The hours of operation for the biomass boiler are restricted to 8,040 hours in any consecutive 12-month period.  [Application Nos. 0550063-001-AC and 0550063-004-AC; Rules 62-4.070(3) and 62-210.200(PTE), F.A.C.]

- GCP:  The emission standards established by this permit rely on “good combustion practices” to reduce emissions.  Therefore, all operators and supervisors shall be properly trained to operate and maintain the steam generating unit and pollution control systems in accordance with the guidelines and procedures established by each manufacturer.  The training shall include GCP as well as methods of minimizing excess emissions.  [Rules 62-4.070(3) and 62-212.400(5), F.A.C.]

Ox-cat catalyst lifetime testing

- Ox-Cat Catalyst Testing:  An Ox-cat system shall be installed on the biomass boiler prior to the HEF facility becoming operational.  The Ox-cat system will help control CO (and organic HAP) emissions from the boiler.  An initial 24-month test period will be conducted to determine if the alkali nature of the boiler flue gas stream will poison the Ox-cat catalyst.  During this test period, the CO emission limit as given in Specific Condition 12 of this subsection is 0.30 lb CO/MMBtu of boiler heat input on a 30-day rolling average basis.  Also during this test period, the VOC emission limit as given in Specific Condition 12 of this subsection is 0.017 lb VOC/MMBtu based on initial and annual stack tests.  After 24 months of initial Ox-cat operation, a test report per Specific Condition 11 of this subsection will be submitted to the Permitting Authority and Compliance Authority describing Ox-cat performance versus time with regard to CO and VOC emissions.  Based on this report, after public notice and comment, the Department shall modify the AC permit to either: 1) adjust the CO and VOC BACT emissions limits downward to reflect the actual long-term CO and VOC removal effectiveness of the Ox-cat system; or 2) authorize removal of the Ox-cat system.  If removal of the Ox-cat system is authorized, the CO and VOC emission limits will remain 0.30 lb/MMBtu on a 30-day rolling average basis and 0.017 lb/MMBtu based on stack tests, respectively.  [Rules 62-212.400(10); 62-210.200(PTE); and 62-4.070(3), F.A.C.]

- Ox-Cat Catalyst Testing Report:  Ninety days after completion of the Ox-cat system catalyst lifetime testing period, a test report shall be submitted to the Permitting Authority and Compliance Authority.  At a minimum, for the duration of the testing, the report shall include:  24-hour (midnight to midnight) averages of boiler operating parameters to include heat input, steam generation, fuel mixtures (cane bagasse, sorghum bagasse, supplemental biomass fuel and natural gas) and corresponding weights of each biomass fuel used including each supplemental fuel (energy crops, wood chips and vegetative debris) and MMscf of natural gas burned; 24-hour NOX and CO CEMS data in lb/MMBtu and lb/hr; all VOC stack tests results in lb/MMBtu and lb/hr from the boiler stack; all HAP stack test results from both the boiler stack and ethanol process scrubber stacks in lb/MMBtu and lb/hr; all maintenance actions performed on the Ox-cat system and; if necessary, a recommendation for the Ox-cat system removal with supporting justification or any requested permit modification to allow the continued use of the Ox-cat system.  Based on all the data (boiler parameters, pollutant and HAP emissions and maintenance actions) in the test report, the Department will either adjust the CO and VOC emission limits downward to reflect the CO and VOC BACT standards with the Ox-cat or allow removal of the Ox-cat system.  If the Ox-cat system is removed, the CO and VOC emission limits will remain 0.30 lb/MMBtu on a 30-day rolling average basis and 0.017 lb/MMBtu based on stack tests, respectively.  [Rules 62-212.400(10); 62-210.200(PTE); and 62-4.070(3), F.A.C]

Emissions Standards

- Emission Limits:  Emissions from the biomass boiler shall not exceed the following standards.

| Pollutant | Emission Standard | Basis | Compliance Method | Averaging Time a |
| --- | --- | --- | --- | --- |
| NOX | 0.10 lb/MMBtu | BACT (Rule 62-212.400(BACT), F.A.C.) | NOX CEMS | 30-operating-day rolling |
|  | 0.15 lb/MMBtu |  |  | 24-operating-hour rolling, excluding startup and shutdown |
|  | 0.20 lb/MMBtu | NSPS Subpart Db (40 CFR 60.44b(l)(1) |  | 30-operating-day rolling, including malfunction |
| SO2 | 0.060 lb/MMBtu | BACT (Rule 62-212.400(BACT), F.A.C.) | SO2 CEMS | 30-operating-day rolling |
|  | 0.078 lb/MMBtu |  |  | 1-hour block |
| GHGs (CO2) | 0.42 lb/lb steam | BACT (Rule 62-212.400(BACT), F.A.C.) | CO2 CEMS (or O2 monitor with F-factor correction) b | 12-operating-month rolling |
| PM (filterable) c | 0.026 lb/MMBtu | NESHAP Subpart DDDDD (Table 1, Row 13) | Initial and annual stack tests |  |
|  | 0.015 lb/MMBtu | BACT (Rule 62-212.400(BACT), F.A.C.) |  |  |
| PM10 (filterable & condensable) | PM (filterable) and PM2.5 (filterable + condensable) serve as proxies. |  |  |  |
| PM2.5 (filterable & condensable) | 0.022 lb/MMBtu (See Specific Condition 13.) | BACT (Rule 62-212.400(BACT), F.A.C.) | Initial and annual stack tests |  |
| Visible Emissions (VE) d | 30 percent opacity | Rule 62-296.410(2)(b), F.A.C. | Initial and annual stack tests |  |
| HCl | 0.022 lb/MMBtu | NESHAP Subpart DDDDD (Table 1, Row 1) | Stack tests, monthly fuel sampling, or CEMS |  |
| Hg | 8.0 x 10-7 lb/MMBtu | NESHAP Subpart DDDDD (Table 1, Row 1) | Stack tests, monthly fuel sampling, or CEMS |  |
| CO | 900 ppmvd @ 3% O2 e | NESHAP Subpart DDDDD (Table 1, Row 13) | CO CEMS | 30-operating-day rolling, excluding startup and shutdown, including malfunctions |
|  | 0.30 lb/MMBtu, for first 24 months of operation (See Specific Condition 10.) | BACT (Rule 62-212.400(BACT), F.A.C.) |  | 30-operating-day rolling, excluding startup and shutdown |
| VOC | 0.017 lb/MMBtu, for first 24 months of operation (See Specific Condition 10.) | BACT (Rule 62-212.400(BACT), F.A.C.) | Initial and annual stack tests |  |
| NH3 | 25 ppmvd @ 7% O2 f | BACT (Rule 62-212.400(BACT), F.A.C.) | Initial and annual stack tests |  |
| - Unless otherwise specified, averaging periods include periods of startup and shutdown, and do not include periods of documented malfunction. - Emissions of non-CO2 GHGs are expected to be negligible for this boiler. - NSPS Subpart Db includes an additional limit on filterable PM for boilers that fire wood or wood chips in any quantity. Rule 62-296.410, F.A.C., also contains limits on filterable PM. However, the PM limits in these rules are less stringent than the PM limit in Subpart DDDDD and the BACT PM limit. Additionally, following the Subpart DDDDD work practice requirements assures that there is an effective limitation on PM at all times. - By Rule 62-296.410, F.A.C., visible emissions shall not exceed 30 percent opacity except that visible emissions not exceeding 33 percent opacity shall be allowed for one six-minute period in any one-hour period. If the boiler fires wood or wood chips in any quantity, the boiler becomes subject to a VE limit of 20% opacity, except for one 6-minute period per hour of not more than 27% opacity, under Subpart Db. - Parts per million by volume, dry, corrected to 3% O2. For the purposes of demonstrating compliance with the Subpart DDDDD CO limit, the procedures contained in 40 CFR 63, Subpart DDDDD, shall be utilized. This limit does not apply during periods of startup or shutdown, as defined in 40 CFR 63.7575. During these periods, the permittee shall follow the work practices in Subpart DDDDD. - Parts per million by volume, dry, corrected to 7% O2. |  |  |  |  |

[Application Nos. 0550063-001-AC and 0550063-004-AC; Rules 62-212.400(10) (PSD) and 62-296.410, F.A.C.; 40 CFR 60, Subpart Db; 40 CFR 63, Subpart DDDDD]

- Emission Limit for PM2.5:  The emission limit for PM2.5 (filterable + condensable) is initially 0.022 lb/MMBtu.  If the initial test for PM2.5 indicates that this limit cannot be achieved, then quarterly tests for PM2.5 are required for the first year of operation.  These tests shall use EPA Methods 201A (for filterable PM2.5) and 202 (for condensable PM).  In this case, the Department will re-evaluate the PM2.5 BACT limit based on these five tests, in consultation with the Permittee.  [Application No. 0550063-004-AC; Rules 62-212.400 (BACT) and 62-4.070, F.A.C.]

- Continuous Monitoring Requirements:  The permittee shall install, calibrate, maintain and operate CEMS and a diluent monitor to measure and record the emissions of SO2, NOX, CO2, and CO from the biomass boiler stack in a manner sufficient to demonstrate continuous compliance with the CEMS-based emission standards in Specific Condition 12 above.  Each CEMS shall be installed, calibrated and properly functioning within 60 calendar days of achieving permitted capacity as defined in Rule 62-297.310(3), F.A.C., but no later than 180 calendar days after initial startup and prior to the initial performance tests.  Within one working day of discovering emissions in excess of a SO2, NOX, CO2, or CO emission limit (and subject to the specified averaging period), the permittee shall notify the Compliance Authority.

- SO2 CEMS:  The SO2 CEMS shall be certified, operated and maintained in accordance with the requirements of 40 CFR 75.  Record keeping and reporting shall be conducted pursuant to Appendix B and F in 40 CFR 60.

- NOX CEMS:  The NOX CEMS shall be certified, operated and maintained in accordance with the requirements of 40 CFR Part 75.  Recordkeeping and reporting shall be conducted pursuant to Subpart Db in 40 CFR 60 and Appendix B and F in 40 CFR 60.

{Permitting Note:  While the NOX and SO2 CEMS shall be operated and maintained in accordance with the requirements of 40 CFR Part 75, this emission unit is not subject to the requirements of the Acid Rain Program.}

- CO CEMS:  The CO CEMS shall be certified pursuant to 40 CFR 60, Appendix B, Performance Specification 4 or 4A.  Quality assurance procedures shall conform to the requirements of 40 CFR 60, Appendix F.  The Data Assessment Report of Section 7 shall be made each calendar quarter and reported semiannually to the Compliance Authority.  The RATA tests required for the CO monitor shall be performed using EPA Method 10 in Appendix A of 40 CFR 60 and shall be based on a continuous sampling train.  The CO monitor span values shall be set appropriately, considering the allowable methods of operation and corresponding emission standards.

- Diluent Monitor:  The carbon dioxide (CO2) or oxygen (O2) content of the flue gas shall be monitored at the location where CO and NOX are monitored.  Each monitor shall comply with the performance and quality assurance requirements of Appendix B and F of 40 CFR 60.  This monitor shall be used to demonstrate compliance with the GHG BACT emission limit.  If a CO2 monitor is not used, an appropriate correction factor shall be used to calculate CO2 concentrations from O2 concentrations.

- 30-Day Averages:  30-day averages shall be determined as follows:

- NOX and SO2:  The 30-operating-day rolling average shall be determined by averaging all 1-hour averages for 30 successive boiler operating days. A boiler operating day begins and ends at midnight of each day and includes any day that fuel is combusted.

- CO:  The 30-operating-day rolling average means the arithmetic mean of the previous 720 hours of valid CO CEMS data.

[Rules 62-212.400(10), 62-210.200(PTE), and 62-4.070(3), F.A.C.; 40 CFR 60, Subpart Db; 40 CFR 63.7575]

- ESP Secondary Power:  The permittee shall monitor secondary voltage and secondary amperage for the ESP in accordance with 40 CFR 63, Subpart DDDDD.  The ESP total secondary power operating limit shall be established in accordance with Subpart DDDDD.  [40 CFR 63.7530(b)(4)(iv), 40 CFR 63.7575, and Tables 4, 5, and 7 to 40 CFR 63, Subpart DDDDD]

- NSPS Subpart Db Opacity Monitoring:  If the boiler fires wood or wood chips in any quantity, the permittee shall comply with the opacity monitoring requirements of 40 CFR 60, Subpart Db.  Options for compliance include a continuous opacity monitoring system (COMS), a continuous emissions monitoring system for particulate matter (PM CEMS), or an ESP predictive model.  Stack tests for visible emissions are required, at the frequency given in 40 CFR 60.48b(a), if a COMS is not used.  The chosen method of compliance shall be identified in the application for a Title V air operation permit for this unit.  [40 CFR 60.48b(a) and 60.48b(j)]

Startup, Shutdown, and Malfunction Requirements

- Malfunction Notifications:  In case of excess emissions resulting from malfunctions, each owner or operator shall notify the Compliance Authority in accordance with the following.  If the permittee is temporarily unable to comply with any of the conditions of the permit due to breakdown of equipment or destruction by hazard of fire, wind or by other cause, the permittee shall immediately (within one working day) notify the Compliance Authority.  Notification shall include pertinent information as to the cause of the problem; and what steps are being taken to correct the problem and to prevent its recurrence; and, where applicable, the owner’s intent toward reconstruction of destroyed facilities.  Such notification does not release the permittee from any liability for failure to comply with Department rules.  If requested by the Compliance Authority, the owner or operator shall submit a quarterly written report describing the malfunction.  
[Rules 62-210.700(5) and 62-4.130, F.A.C.]

- Excess Emissions Prohibited:  Excess emissions caused entirely or in part by poor maintenance, poor operation or any other equipment or process failure that may reasonably be prevented during startup, shutdown or malfunction shall be prohibited.  All such preventable emissions shall be included in any compliance determinations based on CEMS data.  [Rule 62-210.700(1), F.A.C.]

- Applicability of Primary BACT for CO and 24-hour BACT Limit for NOX:  The Primary BACT limit for CO and the 24-hour BACT limit for NOX apply at all times, except for the operating conditions given in this condition.  CO or NOX emission data exclusions resulting from startup, shutdown, or documented malfunctions shall not exceed two hours in any 24-hour period except for the specific cases listed below.  A “documented malfunction” means a malfunction that is documented within one working day of detection by contacting the Compliance Authority by telephone, facsimile transmittal or electronic mail.

- Cold Startup:  For a cold startup of the boiler-steam turbine system, CO emission data exclusions shall not exceed six hours in any 24-hour period.  A cold “startup of the steam turbine system” is defined as startup of the boiler following a shutdown lasting at least 24 hours.

- Warm Startup:  For a warm startup of the boiler-steam turbine system, CO emission data exclusions shall not exceed three hours in any 24-hour period.  A warm “startup of the steam turbine system” is defined as startup of the boiler following a shutdown lasting less than least 24 hours.

- Shutdown:  For shutdown of the boiler, CO emission data exclusions shall not exceed two hours in any 24-hour period.  Shutdown is defined as the cessation of the operation of the boiler for any purpose after steam generation drops below 100,000 lb/hr.

[Rules 62-210.700(4) and 62-212.400(BACT), F.A.C.]

- Secondary BACT for CO:  The startup and shutdown work practices in 40 CFR 63, Subpart DDDDD, are adopted as Secondary BACT for CO during periods of startup and shutdown.  Demonstrating compliance with Subpart DDDDD is sufficient to demonstrate compliance with the Secondary BACT standard.  [Rules 62-210.700(4) and 62-212.400(BACT), F.A.C.]

Testing Requirements

- Boiler Performance Test:  Within 180 days of first fire on the primary fuel (sugarcane or sweet sorghum bagasse) with natural gas used for flame stabilization, the HEF facility shall conduct a test to determine the boiler thermal efficiency.  Within 180 days of first fire with sugarcane or sweet sorghum bagasse as the primary fuels and biomass (energy crops, wood chips and vegetative debris) as a supplemental fuel with natural gas for flame stabilization, the HEF facility shall conduct a test to determine the boiler thermal efficiency.  Each test shall be conducted in general accord with ASME PTC 4, 1998.  See Appendix ASME of this permit.  The abbreviated test procedure shall be agreed upon by all parties.  The test shall be conducted when firing only the specified fuels with as close of fuel mix and heating values to the boiler design fuel mix and heating values as practical and shall be at least three hours long.  The boiler steam conditions and production rate shall be monitored and recorded during the test.  The primary fuel firing rate (in tons per hour and cubic feet per minute as appropriate) shall be calculated and recorded based on the steam parameters.  Samples of the as-fired sugarcane or sweet sorghum bagasse and energy crops, wood chips and vegetative debris shall be analyzed for the heating value (Btu/lb) and moisture content (%).  The actual heat input rate (MMBtu/hour) shall be determined using the method given in Specific Condition 22 below.  Results of the test shall be submitted to the Compliance Authority within 45 days of completion.  The boiler thermal efficiency test shall be repeated during the 12-month period prior to renewal of any operation permit.  If the tested boiler thermal efficiency is less than 90% of the design boiler thermal efficiency, then the tested thermal efficiency shall be used in any future calculations of the heat input rate until a new test is conducted.  [Rule 62-4.070(3), F.A.C.]

- Boiler Heat Input Rate Calculation:  The permittee shall use the thermal efficiency method in Specific Condition 6 of this subsection to calculate the boiler heat input rate.  The procedure given in Appendix ASME of this permit shall be used to measure the boiler efficiency.  As an alternative, the procedures given in Appendix F of this permit may be used to calculate boiler heat input.  If used, Section 5 of Appendix F of 40 CFR 75 provides a methodology for calculation of the heat input rate to a boiler using F-Factors.  The applicable portions of 40 CFR 75 for the calculation of the heat input rate to the biomass boiler at the HEF facility is contained in Appendix F of this permit.  This procedure may be used to calculate the heat input rate in MMBtu/hr to the biomass boiler.  [Rule 62-4.070(3), F.A.C.]

- Initial and Annual Stack Tests:  In accordance with test methods specified in this permit, the boiler shall be tested to demonstrate initial compliance with the emission standards for filterable PM, PM2.5, VOC, VE, HCl, Hg, and ammonia slip given in Specific Condition 12 of this subsection.  The tests shall be conducted within 60 days after achieving permitted capacity, but not later than 180 days after the initial startup of the boiler.  Subsequent compliance stack tests for filterable PM, PM2.5, VOC, VE, HCl, Hg, and ammonia slip shall also be conducted during each calendar year (January 1 to December 31).  Tests shall be conducted between 90% and 100% of the maximum heat input rate when firing only the primary fuels.  CEMS data for CO, NOX and SO2 shall be reported for each run of the required stack tests for ammonia slip, HCl, Hg, PM, PM2.5, VE, and VOC.  If the permittee chooses to demonstrate compliance with the Hg or HCl limit through the fuel analysis option in NESHAP Subpart DDDDD, stack tests for that pollutant are not required.  [Rules 62-212.400(5)(c) and 62-297.310(7)(a) and (b), F.A.C.; 40 CFR 60.8 and 63.7510(b)]

{Permitting Note:  All initial tests must be conducted between 90% and 100% of permitted capacity; otherwise, this permit will be modified to reflect the true maximum capacity as constructed.  If the boiler fires wood or wood chips, more frequent VE testing may be required by Subpart Db.}

- PM2.5 Test Methods:  The emission limit for PM2.5 in Specific Condition 12 is for the sum of filterable PM2.5 and condensable PM.  For the initial test, filterable PM2.5 shall be measured using Method 201A.  If the initial tests indicate that the emissions rate of filterable PM, by Method 5, is greater than or equal to the emissions rate for filterable PM2.5, by Method 201A, then annual compliance tests may use Method 5 for the filterable PM2.5 measurement.  If Method 5 is used, all measured filterable PM shall be assumed to be filterable PM2.5.  Condensable PM shall be measured using Method 202.  [Rules 62-4.070(3), 62-212.400(PSD), and 62-297.310(8)(b)1, F.A.C.]

- Test Methods:  Any required stack tests shall be performed in accordance with the following methods.

| EPA Method | Description of Method and Comments |
| --- | --- |
| 1-4 | Determination of Traverse Points, Velocity and Flow Rate, Gas Analysis and Moisture Content {Note: Methods shall be performed as necessary to support other methods.} |
| 5 | Determination of Particulate Matter Emissions from Stationary Sources |
| 6C | Measurement of SO2 Emissions (Instrumental) |
| 7E | Measurement of NOX Emissions (Instrumental) |
| 8 | Determination of Sulfuric Acid and Sulfur Dioxide Emissions from Stationary Sources |
| 9 | Visual Determination of Opacity |
| 10 or 10B | Determination of Carbon Monoxide Emissions from Stationary Sources or Measurement of CO Emissions (Instrumental) {Note: The method shall be based on a continuous sampling train.} |
| 18 | Measurement of Gaseous Organic Compound Emissions (Gas Chromatography) {Note: EPA Method 18 may be used (optional) concurrently with EPA Method 25A to deduct emissions of methane and ethane from the total hydrocarbons (THC) emissions measured by Method 25A.} |
| 19 | Calculation Method for NOX, PM and SO2 Emission Rates |
| 25 or 25A | Determination of Total Gaseous Nonmethane Organic Emissions as Carbon |
| 26 or 26A | Hydrogen Chloride, Halides, Halogens, OR Hydrogen Halide & Halogen-Isokinetic |
| 29 | Metals Emissions from Stationary Sources |
| 30A, 30B, 101A, or ASTM-D6784 | Mercury Emissions from Stationary Sources |
| CTM-027 or 320 | Procedure for Collection and Analysis of Ammonia in Stationary Source. {Notes: This is an EPA conditional test method. The minimum detection limit shall be 1 ppm.}, OR Measurement of Vapor Phase Organic and Inorganic Emissions by Extractive Fourier Transform Infrared (FTIR) Spectroscopy |
| 201A | Determination of PM10 and PM2.5 Emissions from Stationary Sources. {Note: If the gas filtration temperature exceeds 30 °C (85 °F), Method 201A measures only filterable particulate matter.} |
| 202 | Dry Impinger Method for Determining Condensable Particulate Emissions from Stationary Sources |

Method CTM-027 is published on EPA’s Technology Transfer Network Web Site at http://www.epa.gov/ttn/emc/ctm.html .  The other methods are specified in Appendix A of 40 CFR 60, adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Compliance Authority and the Office of Permitting and Compliance.  [Rules 62-204.800, F.A.C. and 40 CFR 60, Appendix A]

- Continuous Compliance:  Continuous compliance with the permit standards for emissions of NOX, SO2, GHGs, and CO shall be demonstrated with data collected from the required CEMS.  [Rules 62-4.070 and 62-210.200(BACT), F.A.C.; 40 CFR 60.48b(a) and (b); 40 CFR 63.7525(a)]

OTHER Monitoring Requirements

- Steam Parameters:  In accordance with the manufacturer’s recommendations, the permittee shall install, calibrate, operate and maintain continuous monitoring and recording devices on the biomass boiler for the following parameters:  feedwater temperature and pressure, steam temperature (°F), steam pressure (psig) and steam production rate (lb/hour).  In addition, the hourly heat input rate to the biomass boiler shall be recorded and reported. Records shall be maintained on site and made available upon request.  
[Application No. 0550063-001-AC; Rules 62-4.070(3) and 62-212.400(5), F.A.C.]

- Fuel Flow Meter:  A fuel flow meter shall be installed on the biomass boiler to record the amount of natural gas used in the boiler on a monthly and 12-month rolling average basis.  
[Rule 62-4.070(3), F.A.C.]

- SNCR Urea or NH3 Injection Rate:  In accordance with the manufacturer’s specifications, the permittee shall install, calibrate, operate and maintain a flow meter to measure and record the urea or NH3 injection rate for the SNCR system for the biomass boiler.  The permittee shall document the general range of urea or NH3 flow rates required to meet the NOX standard over the range of load conditions by comparing NOX emissions with urea or NH3 flow rates.  During NOX CEMS downtimes or malfunctions, the permittee shall operate at a urea or NH3 flow rate that is consistent with the documented flow rate for the given load condition.  Urea or NH3 injection records shall be maintained on site and made available upon request.  
[Rules 62-4.070(3) and 62-212.400(5), F.A.C.]

- Wet Sand Separators:  In accordance with the manufacturer’s recommendations, the permittee shall calibrate, operate and maintain the following equipment: flow meter to monitor the water flow rate (gph) for each wet sand separator and a manometer (or equivalent) to monitor the pressure drop (inches of water) across each separator.  [Rule 62-212.400 (PSD), F.A.C.]

- ESP Power:  The permittee shall install, calibrate, operate, and maintain a system to measure and record secondary power (voltage and amperage) to the ESP.  The permittee shall conduct a performance evaluation of the power monitoring system in accordance with the monitoring plan required by Subpart DDDDD at the time of each PM performance test, but no less frequently than annually.  [40 CFR 63.7525(h) and Rule 62-212.400 (PSD), F.A.C.]

- Monitoring Plan:

- Subpart DDDDD:  The permittee shall develop a site-specific monitoring plan for the use of each continuous monitoring system used for compliance with NESHAP Subpart DDDDD.  This includes the CO CEMS, diluent monitor, and ESP power monitoring system.  The permittee shall also develop a site-specific fuel monitoring plan for chloride and mercury in bagasse and wood, if the fuel sampling option for compliance with Subpart DDDDD will be used.  [40 CFR 63.7505(d) and 63.7521(b)]

- Subpart Db:  If an ESP predictive model is used for compliance with NSPS Subpart Db, a monitoring plan for the ESP predictive model is required.  The monitoring plan for an ESP predictive model shall be submitted to the Permitting Authority for approval with the application for a Title V air operation permit.    [40 CFR 60.48b(j)(6) and 60.48Da(o)(3)(ii)]

- Additional Requirements:  The monitoring plan for other measurement systems shall be available for inspection at the facility and shall be submitted to the Department upon request.  [Rule 62-212.400 (PSD), F.A.C.]

Records and Reports

- Stack Test Reports:  In addition to the information required in Rule 62-297.310(8), F.A.C., each stack test report shall also include the following information:  steam production rate (lb/hour), heat input rate (MMBtu/hour), calculated authorized fuels firing rate (tons/hour and cubic feet per minute as appropriate) and emission rates (lb/MMBtu, ppmvd @ 7% or 3% oxygen, and lb/hr as appropriate).  Results from any HAP emission rate stack tests conducted during the period addressed by the stack test report shall be included.  [Rule 62-4.070(3), F.A.C.]

- Monthly Operations Summary:  By the tenth calendar day of each month, the permittee shall record the following parameters for the biomass boiler in a written or electronic log for the previous month of operation: hours of operation, tons of sugarcane and sweet sorghum bagasse, tons of supplemental biomass and cubic feet of natural gas, pounds of steam, total heat input rate and the updated 12-month rolling totals for each of these operating parameters.  Cubic feet of natural gas used shall be recorded in a written or electronic log for the previous month of operation along with the updated 12-month rolling total.  The Monthly Operations Summary shall be maintained on site and made available for inspection when requested by the Department.  [Rules 62-4.070(3) and 62-212.400(BACT), F.A.C.]

- Emissions Reporting:

- Malfunction Notification:  If emissions in excess of a standard (subject to the specified averaging period) occur due to malfunction, the permittee shall notify the Compliance Authority within one working day of the following:  the nature, extent, and duration of the excess emissions; the cause of the excess emissions; and the actions taken to correct the problem.  In addition, the Department may request a written summary report of the incident.  [Rules 62-4.130 and 62-210.700(5), F.A.C.]

- Quarterly Report – CO, SO2, NOX, and GHG Emissions:  Within 30 days following the end of each calendar quarter, the permittee shall submit a report to the Compliance Authority summarizing CO, SO2, NOX, and GHG emissions including periods of startups, shutdowns, and malfunctions, periods of exclusion from Primary BACT compliance demonstrations, and CEMS systems monitor availability for the previous quarter.  The report shall also include the 12-month average CO2 emissions rates for all compliance periods that end during the reporting period.  If CEMS data are excluded from a compliance determination during the quarter due to a malfunction, the permittee shall include a description of the malfunction, the actual emissions recorded, and the actions taken to correct the malfunction.  [Rules 62-4.070(3), 62-4.130, and 62-212.400 (PSD), F.A.C.]

- Semi-Annual Report – Subpart DDDDD and Subpart Db:  The permittee shall subpart semi-annual reports as required by NESHAP Subpart DDDDD and NSPS Subpart Db.  Subpart DDDDD requires electronic submission of some reports via the Compliance and Emissions Data Reporting Interface (CEDRI).  [40 CFR 60.7(c) and 63.7550]

{Permitting note:  All reports submitted electronically to EPA must also be submitted to the Compliance Authority.}

This section of the permit addresses the following emissions units.

| ID No. | Emission Unit Description |
| --- | --- |
| 003 | Cooling Towers: The HEF facility will have up to three mechanical draft cooling towers. The cooling towers will be used for the cooling of miscellaneous machinery, the condensing set and the process equipment used in ethanol production at the HEF facility. [Application No. 0550063-001-AC] |

Equipment

- Cooling Towers:  The permittee is authorized to construct up to three cooling towers to provide cooling to miscellaneous machinery, the condensing set and process equipment used in ethanol production at the HEF facility.  Typical design parameters for the cooling towers are:  one cell with a stack height of 35 feet, a circulating water flow rate of 34,000 gallons per minute (gpm), a temperature of 77 °F and a design drift rate of 0.001%.  [Application No. 0550063-001-AC and Rule 62-210.200 (PTE), F.A.C.]

Performance restrictions

- Hours of Operation:  The hours of operation of this emission unit are not limited (8,760 hours per year).  [Application No. 0550063-001-AC and Rules 62-4.070(3) and 62-210.200(PTE), F.A.C.]

- Total Dissolved Solids (TDS):  The makeup water used in the cooling towers shall contain no more than 500 parts per million by weight (ppmw) of TDS on an annual basis.  The makeup water in the cooling towers must be tested weekly for TDS using any of the five approved methods in 40 CFR, Part 136.  These methods are:  US EPA 160.2; US Geological Survey Method I-3765-85; Standard Method 2540 D 18th Edition; Standard Method 2540 D 19th Edition; and Standard Method 2540 D 20th Edition.  Records of each test must be kept on site and made available to the Compliance Authority upon request.  [62-4.070(3), F.A.C.]

Emissions STANDARDS

- Drift Rate:  Within 60 days of commencing operation, the permittee shall certify that the cooling towers were constructed to achieve the specified drift rate of no more than 0.001% of the circulating water flow rate.  [Rule 62-212.400(BACT), F.A.C.]

{Permitting Note:  The applicant estimates PM and PM10 emission from the cooling towers to be 0.37 and 0.19 TPY, respectively.}

- VOC Emissions:  The permittee shall control VOC emissions by promptly repairing any leaking components in accordance with the approved LDAR plan.  The permittee shall collect a sample of cooling water on a weekly basis from miscellaneous machinery and process equipment cooling towers and analyze it for VOCs to enable the early detection of leaking heat exchangers and thereby minimizing VOC emissions from the cooling towers.  
[Application No. 0550063-001-AC; Rules 62-210.200 (PTE), 62-212.400(BACT) and 62-4.070, F.A.C. Reasonable Assurance; 40 CFR 60 NSPS, Subpart VVa]

{Permitting Note: These work practice standards are established as BACT for PM, PM10, PM2.5, and VOC emissions from the cooling towers.}

Testing AND Monitoring Requirements

- VOC Cooling Water Monitoring Plan:  A monitoring plan in compliance with NSPS Subpart VVa detailing how the cooling tower water shall be monitored for VOC contamination from leaking heat exchangers as required by Specific Condition 5 above shall be submitted to the Compliance Authority for approval no later than 180 days before the HEF facility becomes operational.  
[Application No. 0550063-001-AC; Rules 62-210.200 (PTE), 62-212.400(BACT), and 62-4.070, F.A.C.]

- VOC Water Testing Frequency:  Testing of the cooling water shall be conducted weekly unless VOC contamination is found during one of the weekly tests as compared to the baseline VOC concentration of the makeup water.  Then daily testing will be required until the mechanical leak is corrected and no VOC contamination is detected in the cooling tower water as compared to the makeup water baseline.  
[Application No. 0550063-001-AC; Rules 62-210.200 (PTE), 62-212.400(BACT), and 62-4.070, F.A.C.]

- Notification:  The permittee shall notify the Compliance Authority in writing within one working day after VOC contamination of the cooling tower water is discovered.  Additionally, the permittee shall submit a plan to correct the problem within 7 calendar days for the approval of the Compliance Authority.  
[Application No. 0550063-001-AC; Rules 62-210.200 (PTE), 62-212.400(BACT), and 62-4.070, F.A.C.]

Records and Reports

- Monitoring Test Reports:  The permittee shall prepare and submit reports for all required monitoring tests in accordance with the requirements specified in Appendix D (Common Testing Requirements) of this permit, including descriptions of any VOC contamination discovered and the corrective action taken.  
[Rule 62-297.310(8), F.A.C.]

This section of the permit addresses the following emissions unit.

| ID No. | Emission Unit Description |
| --- | --- |
| 004 | Ethanol Production Process: The maximum design ethanol production rate is 120,000 gallons per day and 36 million gallons per year. This emission unit consists of the following major processes: Juice Filtration and Juice Evaporation: After juice extraction, the juice is pumped to a juice screen which separates fine particles prior to evaporation. Fine particles are recycled into the diffuser where they ultimately become part of the bagasse. The screened juice is then sent to the juice storage tank. The juice pH is adjusted as necessary to control corrosion. The evaporation process concentrates the sucrose juices extracted in the diffuser. The extracted juice is pumped from the juice storage tank to a multiple effect evaporator, where the juice is concentrated from 14% to 22% total solids. Pre-Fermentation and Fermentation: During fermentation, sugars contained in the concentrated juice are transformed to ethyl alcohol, CO2 and various secondary products utilizing yeast. The fermentation process is a four-step continuous fermentation preceded by an agitated pre-fermenter, which serves as a yeast propagator and to initially acclimate the yeast to the fermentation conditions. Sulfuric acid is used to adjust the pH. The cooled, concentrated juice along with the yeast and urea (added as a nutrient) are fed to the pre-fermenter. The pre-fermenter continuously recirculates the ferment through a heat exchanger to keep the temperature in the optimum range for fermentation. The ferment is continuously transferred from the pre-fermenter to the first fermenter based on level. There are a total of four agitated fermenters in the series, each having controlled temperature and controlled additions of urea and yeast to maintain optimum fermentation conditions. Flow is maintained from one fermenter to another based on level. The product of fermentation, called “beer,” has a weak ethanol solution along with the residue of fermentation components. Distillation: In distillation, the filtered beer from fermentation, with an alcohol concentration of approximately 8% by weight, is distilled to approximately 96% hydrated alcohol. The alcohol stream is increased to 91% by weight of ethanol concentration in the rectifier column. Rectifier overhead vapor is sent to the molecular sieve units to further remove water to less than 0.7% by weight in the ethanol product. Propanol and fusel oils are removed from the lower section of the rectifier column and combined with the 91% ethanol vapor which goes to the molecular sieves. Vinasse Evaporation: The beer column bottom stillage, called vinasse, is cooled using the incoming beer as the heat sink and sent to storage. From the storage, the vinasse is evaporated to 40% solids using a combination of several waste heat sources and live steam in three sets of multiple effect evaporators. The concentrated vinasse is stored and then loaded onto trucks for shipment to be utilized for animal feed. Dehydration: The final stage in the ethanol production process is dehydration. Hydrated alcohol from the distillation process, at about 96% by volume alcohol, undergoes dehydration with a molecular sieve to produce ethanol at 99.3% by weight purity. The process is performed in a continuous operation where the hydrated alcohol is superheated by steam in a shell and tube heat exchanger to ensure that the ethanol stream is always in the vapor phase as it passes through molecular sieve zeolite beds. The final ethanol product is condensed, cooled and sent to the 200-proof storage tank |

Equipment

The permittee is authorized to construct the following equipment used during the production of ethanol and to control VOC emissions from the process:

- Juice Extraction:  The permittee is authorized to construct the following major components of a juice extraction system: revolving cane and sorghum high efficiency knives; heavy-duty shredder; high speed belt conveyor; chainless horizontal diffuser; various juice receivers; juice heaters; lime mixing tank; dewatering drum; and raw juice tank.

- Juice Treatment and Evaporation:  The permittee is authorized to construct the following major components of a juice treatment and evaporation system: rotary screens; juice evaporator; and clean and foul condensate tanks.

- Pre-Fermentation and Fermentation: The permittee is authorized to construct the following major components of a pre-fermentation and fermentation system: a sulfuric acid tank; a urea tank; yeast mixing tank; pre-fermenter; pre-fermenter cooler; fermenters; fermenter coolers; beer well tank; beer/sucrose heat exchanger; and CO2 scrubbing column.

- Distillation:  The permittee is authorized to construct the following major components of a distillation system: beer distillation column; degassing column; degassing condenser; stripping column; rectification column; heat exchangers; fusel oil decanter; hydrated alcohol tank; CO2 washing column; and scrubber water degasser.

- Dehydration:  The permittee is authorized to construct the following major components of a dehydration system: hydrated alcohol heater; zeolite absorber (molecular sieve); condensers and coolers; filter; dehydrated alcohol holding tank; and tie-in to CO2 scrubbing column.

- Vinasse Evaporation:  The permittee is authorized to construct the following major components of a vinasse evaporation system: multiple effect evaporators; raw and concentrated vinasse storage vessels; and a load out system.

- Air Pollution Control Equipment:  The permittee shall install one liquid scrubber to control VOC emissions from the pre-fermentation and fermentation system, and one liquid scrubber to control VOC emissions from the distillation/dehydration systems.  The liquid scrubbers shall have a design control efficiency of 98% and use a liquid with additives, as necessary, that ensures this degree of control is achievable.  Emissions from the pre-fermentation/fermentation liquid scrubber shall discharge through a stack with a design height of 25 ft (minimum), a design diameter of 4.9 ft (maximum) at a design exit temperature of 70 °F and a design flow rate of 4,223 acfm.  Emissions from the distillation/dehydration liquid scrubber shall discharge through a vent with a flow rate of 120 acfm.

[Application No. 0550063-001-AC; Rules 62-212.400 (BACT); 62-4.070, and 62-210.200(PTE), F.A.C.]

Performance Restrictions

- Hours of Operation:  The hours of operation of the ethanol production process are limited to 8,040 hours in any consecutive 12-month period.  [Application No. 0550063-001-AC; Rules 62-212.400 (BACT), 62-4.070, and 62-210.200(PTE), F.A.C.]

##### Emissions Standards

- VOC Standard:  The ethanol process emission unit shall not discharge VOC through the fermentation liquid scrubber stack in excess of 19.01 lb/hr, nor through the distillation/dehydration liquid scrubber vent in excess of 2.78 lb/hr.  [Application No. 0550063-001-AC; Rules 62-212.400 (BACT), 62-4.070, and 62-210.200(PTE), F.A.C.]

- GHG Emissions:

- Initial Standard:  For the first 12 months of operation, the ethanol process emission unit shall not emit CO2 in excess of 8.14 lb per gallon of anhydrous ethanol product, on a 12-month rolling basis, rolled monthly.  Compliance with this limit shall be determined from the total CO2 emitted over the 12-month period, as measured by the CO2 CEMS, and from the total amount of anhydrous ethanol product produced over the 12-month period.

- Report After First Year of Operation:  Within 60 days after the completion of 12 months of operation, the permittee shall submit to the Permitting and Compliance Authorities a report detailing CO2 emissions and ethanol production for the first 12 months of operation.  Based on these first 12 months of operation, the Department may adjust the GHG emission limit, in consultation with the permittee.

[Application No. 0550063-004-AC; Rule 62-212.400 (BACT), F.A.C.]

##### Continuous Emission monitoring

- CO2 CEMS:  The permittee shall install, calibrate, maintain and operate a CEMS for CO2 on the fermentation liquid scrubber stack in a manner sufficient to demonstrate continuous compliance with the CEMS-based GHG emission standard in Specific Condition 10 above.  The monitor shall comply with the performance and quality assurance requirements of Appendix B and F of 40 CFR 60.  This monitor shall be used to demonstrate compliance with the GHG BACT emission limit.  [Rule 62-212.400(10), F.A.C.]

##### Testing Requirements

- Initial VOC Compliance Tests:  The fermentation liquid scrubber stack and the distillation/dehydration liquid scrubber vent shall be tested to demonstrate initial compliance with the emissions standards for VOC given in Specific Condition 9 of this subsection.  The initial tests shall be conducted within 60 days after achieving permitted capacity, but not later than 180 days after initial operation of the unit.  During scrubber VOC testing, the water temperatures of each scrubber shall be measured and recorded.  VOC testing shall be performed using EPA Method 25 or 25A.  [Rules 62-212.400 (BACT), 62-4.070, 62-210.200(PTE), and 62-297.310(8)(b)1, F.A.C.]

- Annual and Quarterly VOC Compliance Tests:

- First 24 Months of Operation:  During the first 24 months of the HEF facility operation, VOC testing shall be conducted annually during each calendar year (January 1 to December 31) to demonstrate compliance with the emissions standard for VOC given in Specific Condition 9 of this subsection.

- Subsequent Operation:  If after 24 months, the Ox-cat system is removed per Specific Condition 10 of Section 3B, above, quarterly VOC testing shall be required thereafter to demonstrate compliance with the emissions standard for VOC.  If the Ox-cat system is not removed, VOC testing shall continue on an annual basis during each calendar year.

- Test Method:  All tests for VOC shall be conducted using EPA Method 25 or 25A.  During scrubber VOC testing, the water temperatures of each scrubber shall be measured and recorded.

[Rules 62-212.400 (BACT), 62-4.070, 62-210.200(PTE), and 62-297.310(8)(a)2, F.A.C.]

- Test Requirements:  The permittee shall notify the Compliance Authority in writing at least 15 days prior to any required tests.  Tests shall be conducted in accordance with the applicable requirements specified in Appendix D (Common Testing Requirements) of this permit.  [Rule 62-297.310(7)(a)9, F.A.C.]

- Test Methods:  Required tests shall be performed in accordance with the following reference methods.

| Method | Description of Method and Comments |
| --- | --- |
| 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis and Moisture Content |
| 25 | Determination of Total Gaseous Nonmethane organic Emissions as Carbon |
| 25A | Method for Determining Gaseous Organic Concentrations (Flame Ionization) |

The above methods are described in Appendix A of 40 CFR 60 and are adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Rule 62-204.800, F.A.C.; and Appendix A of 40 CFR 60]

Monitoring Requirements

- Liquid Scrubbers Monitoring Requirements:

  - Scrubber Operating Parameters:  The permittee shall install, calibrate, operate and maintain monitoring devices that continuously measure and record the total pressure drop across each scrubber.  If the total pressure drop cannot be measured for the scrubber, then the liquid flow rate and the fan amps shall be measured and recorded for the scrubber.  Accuracy of the monitoring devices shall be ± 5% over the operating range.  The temperature of each scrubber’s water shall be measured daily and recorded.  All records pertaining to the scrubbers shall be provided to the compliance authority upon request.

  - Scrubber Guarantee:  Prior to installation of the scrubber, the permittee shall submit to the Compliance Authority the proposed design information, including water additives, along with a manufacturer’s guarantee that the scrubbers are capable of meeting the emission limitations established by the VOC BACT determination.

[Rules 62-212.400 (BACT) and 62-4.070(3), F.A.C.]

Records and Reports

- Quarterly GHG BACT Emissions Reporting:  Within 30 days following the end of each calendar quarter, the permittee shall submit a report to the Compliance Authority summarizing CO2 emissions and CEMS systems monitor availability for the previous quarter.  The report shall also include the rolling 12-month total CO2 emissions and ethanol production for all 12-month periods that end during the quarter, for comparison with the GHG BACT emission limit.  [Rules 62-4.070(3), 62-4.130, and 62-212.400 (PSD), F.A.C.]

- Test Reports:  The permittee shall prepare and submit reports for all required tests in accordance with the requirements specified in Appendix D (Common Testing Requirements) of this permit.  In addition, the test reports shall include each scrubber’s water temperature during VOC testing and the preceding 12 monthly averages of each scrubber’s water temperature.  [Rule 62-297.310(10), F.A.C.]

- Notification, Recordkeeping and Reporting Requirements:  The permittee shall maintain records of the amount of ethanol produced on a daily, monthly and 12-month rolling total basis along with the feed rate (sugarcane, sweet sorghum, sweet sorghum syrup and molasses and sugarcane syrup and molasses) into the ethanol production process emission unit on a monthly basis and 12-month rolling total basis.  These records shall be submitted to the Compliance Authority on an annual basis or upon request.  [Rule 62-4.070(3), F.A.C.]

This section of the permit addresses the following emissions unit.

| ID No. | Emission Unit Description |
| --- | --- |
| 005 | Storage Tanks: This emissions unit consists of volatile organic liquid (VOL) storage tanks for ethanol, denaturant/gasoline, and corrosion inhibitor. Up to 1 million gallons of fuel ethanol will be stored. The tanks will be internal floating roof design, except for the small corrosion inhibitor storage tank, ethanol process tanks and miscellaneous tanks. |

Tanks will be used during the ethanol production process to store ethanol, byproducts and intermediate products.  In addition, the purified ethanol and gasoline (denaturant) will be stored in tanks and then blended, resulting in a denatured product.  The denatured ethanol product will have dedicated storage tanks.  Anhydrous ammonia or urea will be stored in a tank for use in the SNCR system for boiler NOX control.  ULSD fuel oil will be stored in a tank for use in emergency equipment.

Equipment

- The permittee is authorized to construct the following tanks to store VOL at the HEF facility:

- VOL Blending and Storage Tanks:

- Fuel Ethanol Tank:  The permittee is authorized to construct one nominal 1,000,000 gallon ethanol product storage tank with a fixed roof and internal floating roof to minimize VOC emissions per 40 CFR 60.110b(a)(2).

- 200 Proof Ethanol Tank:  The permittee is authorized to construct one nominal 100,000 gallon, 200 proof ethanol storage tank with a fixed roof and internal floating roof to minimize VOC emissions per 40 CFR 60.110b(a)(2).

- Off-Specification Tank:  The permittee is authorized to construct one nominal 100,000 gallon tank to store off-specification ethanol product with a fixed roof and internal floating roof to minimize VOC emissions per 40 CFR 60.110b(a)(2).

- Denaturant /Gasoline Product Storage Tank:  The permittee is authorized to construct one nominal 100,000 gallon denatured/gasoline storage tank with a fixed roof and an internal floating roof to minimize VOC emissions as per 40 CFR 60.110b(a)(2).

[Application No. 0550063-001-AC and NSPS 40 CFR 60, Subpart Kb]

- Ethanol Production Process Tanks:  As required, the permittee is authorized to install the following storage tanks required by the ethanol production process:  Fusel Oil Storage Tank; Hydrated Alcohol Storage Tank; Final Product Metering Tank; Second Grade Alcohol Storage Tank; and Fusel Oil Alcohol Storage Tank.  [Application No. 0550063-001-AC]

- Other Tanks:

- Anhydrous Ammonia or Urea Storage Tank:  The permittee is authorized to construct one nominal 5,000 gallon tank to store anhydrous ammonia or urea for the SNCR system.  In accordance with 40 CFR 60.130, the storage of anhydrous ammonia or urea shall comply with all applicable requirements of the Chemical Accident Prevention Provisions in 40 CFR 68.

- ULSD Fuel Oil Storage Tank:  The permittee is authorized to construct one nominal 5,000 gallon tank to store ULSD fuel oil for use in emergency equipment.

- Sulfuric Acid Storage Tank:  The permittee is authorized to construct one tank to store sulfuric acid for use in the ethanol production process to adjust pH.  In accordance with 40 CFR 60.130, the storage of sulfuric acid shall comply with all applicable requirements of the Chemical Accident Prevention Provisions in 40 CFR 68.

- Corrosion Inhibitor Tank:  The permittee is authorized to construct one nominal 2,300 gallon tank to store methanol, xylene and ethylbenzene that will be used as a corrosion inhibitor at the HEF facility.

[Application No. 0550063-001-AC]

Performance Restrictions

- Permitted Capacity:  The maximum throughput (process) rate in gallons per year for this emissions unit is 36 million gallons of pure ethanol and 37.62 million gallons of denatured ethanol product in any consecutive twelve month period.  [Application No. 0550063-001-AC and Rule 62-4.070, F.A.C.]

- Hours of Operation:  The hours of operation of this emissions unit are not restricted (8,760 hours per year).  [Application No. 0550063-001-AC and Rule 62-210.200(PTE), F.A.C.]

NSPS Subpart Kb Applicability

- VOL Blending and Storage Tanks:  The four Blending and Storage tanks at the HEF facility are subject to NSPS Subpart Kb which applies to any storage tank for which construction, reconstruction, or modification is commenced after July 23, 1984 with a capacity greater than or equal to 151 cubic meters (m3) or 39,990 gallons that is used to store a VOL with a maximum true vapor pressure greater than or equal to 3.5 kilopascals (kPa) or 0.51 pounds per square inch (psi).  The four Blending and Storage tanks each have a capacity greater than 40,000 gallons and store liquids with maximum true vapor pressures greater than 3.5 kPa and consequently are subject to and must comply with the provisions of NSPS 40 CFR 60, Subpart Kb.
[Application No. 0550063-001-AC and NSPS 40 CFR 60, Subpart Kb]

- Ethanol Production Process, Ammonia/Urea and Sulfuric Acid Storage and Corrosion Inhibitor Tanks:  The five Ethanol Production Process storage tanks, the ammonia or urea storage tank, the sulfuric acid storage tank and corrosion inhibitor tank at the HEF facility are not subject to NSPS Subpart Kb.  These tanks are exempt because either they have a capacity less than 75 m3 or 19,813 gallons or they have a capacity greater than or equal to 19,813 gallons but less than 39,990 gallons (151 m3) and store a liquid with a maximum true vapor pressure less than 15 kPa (2.18 psi).  [Application No. 0550063-001-AC]

- ULSD Fuel Oil Storage Tank:  The ULSD fuel oil storage tank at the HEF facility is not subject to NSPS Subpart Kb because it has a capacity of less than 19,813 gallons (75 m3) and stores a liquid with a maximum true vapor pressure less than 3.5 kPa (0.51 psi).  [Application No. 0550063-001-AC]

Emissions Standards

- VOC Standard for Blending and Storage Tanks:  Emissions of VOC from the Blending and Storage tanks will be controlled by the proper construction of the tanks per 40 CFR 60.110b(a)(2) which requires internal floating roofs in the tanks or the equivalent.  In lieu of internal floating roofs in the Blending and Storage tanks, HEF may use pressure relief valves provided that these meet the equivalency requirements of NSPS, Subpart Kb.  If HEF decides to use pressure relief valves in lieu of internal floating roofs, it must provide to the Compliance Authority, 90 days before construction of the Blending and Storage VOL tanks commences, proof of the valves equivalency as defined in the NSPS.  [Application Nos. 0550063-001-AC and 0550063-004-AC; Rules 62-212.400 (BACT) and 62-4.070, F.A.C.]

- VOC Standard for Ethanol Production Process Storage Tanks:  Emissions of VOC from the Ethanol Production Process storage tanks will be controlled by the use of pressure relief valves or vapor condensers.  
[Application Nos. 0550063-001-AC and 0550063-004-AC; Rules 62-212.400 (BACT) and 62-4.070, F.A.C.]

Records and Reports

- Storage Tank Records:  The permittee shall keep readily accessible records showing the dimension of the storage tanks and an analysis showing the capacity of the storage tanks.  Records shall be retained for the life of the facility.  The permittee shall also keep records sufficient to determine the annual throughput of the various liquids for the storage tanks for use in the Annual Operating Report.  [Rule 62-4.070(3), F.A.C]

- NSPS Subpart Kb Reporting and Recordkeeping for Blending and Storage Tanks:  The owner or operator of each storage vessel as specified in §60.112b(a) shall keep records and furnish reports as required by paragraphs (a), (b), or (c) of §60.115b Reporting and Recordkeeping Requirements.  The owner or operator shall keep copies of all reports and records required by§60.115b, except for the record required by (c)(1), for at least 2 years.  The record required by (c)(1) will be kept for the life of the control equipment.
[Rule 62-4.070(3), F.A.C., and NSPS 40 CFR 60, Subpart Kb]

This section of the permit addresses the following emissions unit.

| ID No. | Emission Unit Description |
| --- | --- |
| 006 | Truck Rack Product Loadout and Flare: The denatured blended ethanol product from the VOL Blending and Storage tanks will be loaded out to tanker trucks or railcars with displaced vapors sent to a product loadout flare for destruction. |

The denatured ethanol product will be loaded onto tank trucks or railcars at a maximum rate of 600 gpm.  Also E-85 product (85% ethanol and 15% gasoline fuel blend) may be loaded out via in-line blending.  The maximum throughput rate of denatured ethanol product is 37,620,000 gallons per year (gpy).  Vapors displaced from the trucks/railcars will be combusted by a product loadout flare.  The product loadout flare will have a nominal rated heat input capacity of 9.8 MMBtu/hr to control vapors displaced from the tanker trucks or railcars during the loading of the denatured ethanol product.  The flare will have a design control efficiency of 98%.

Equipment

- Loading Rack:  The permittee is authorized to construct a loading rack that is designed to transfer 600 gpm (37,620,000 gpy) of denatured ethanol product or E-85 product to tanker trucks or railcars.

[Application No. 0550063-001-AC and 62-210.200(PTE), F.A.C.]

- Flare System:  The permittee is required to construct one flare system with a continuous pilot and combustion chambers to destroy displaced vapors during truck/railcar loadout.  The flare shall be operated with a pilot flame present at all times.  The presence of a flare pilot flame shall be monitored using a thermocouple or any other equivalent device to detect the presence of a flame.
[Application No. 0550063-001-AC; Rules 62-212.400(PSD) and 62-210.200(PTE), F.A.C.]

Neshap Applicability

- Subpart FFFF – NESHAP for Miscellaneous Organic Chemical Manufacturing:  The product loadout system is subject to the requirements for transfer racks in 40 CFR 63, Subpart FFFF, for Miscellaneous Organic Chemical Manufacturing.  This subpart requires the control of vapor emissions from loading rack operations through several possible options, one of which is a closed vent system and flare.  Subpart FFFF refers to 40 CFR 63, Subpart SS, for some closed vent system and flare requirements (See 40 CFR 63.982(b)).  Additionally, these subparts refer to 40 CFR 63, Subpart A (40 CFR 63.11(b)), for some requirements.  These subparts include requirements for inspection and leak detection, flare monitoring, visible emissions testing, recordkeeping, and reporting.  [Application Nos. 0550063-001-AC and 0550063-004-AC; 40 CFR 63, Subpart FFFF]

Performance Restrictions

- Approximate Capacities:  The flare system is designed to combust vapors displaced from the trucks/railcars during the loading of the denatured ethanol product or E-85 product.  The trucks and railcars are assumed to not be in dedicated denatured ethanol product service (i.e., some trucks/railcars will have returned from delivering gasoline and gasoline vapors will be displaced).  The product loadout flare will have a rated capacity of 9.8 MMBtu/hr.  Natural gas or propane will be used as the fuel for the pilot flame.  The pilot fame will have a rated capacity of 0.184 MMBtu/hr and will utilize natural gas.  
[Application No. 0550063-001-AC and Rule 62-210.200(PTE), F.A.C.]

- Hours of Operation:  The flare shall be operated at all times when truck or railcar loading operations are taking place. Only denatured ethanol product or E-85 product shall be loaded into the trucks or railcars.  Although the hours of operation of the pilot for the flare system are not limited (8,760 hours per year) the flare itself and product loadout is limited to 3,120 hours per year.  [Application No. 0550063-001-AC; Rules 62-4.070(3), 62-210.200(PTE), and 62-212.400(PSD), F.A.C.]

Emissions Standards

- VE Standard:  The flare shall be designed for and operated with no VE except for periods not to exceed a total of 5 minutes during any 2 consecutive hours.  If the loading cycle is less than 2 hours, then the observation period shall be run for the entire loading cycle, and if additional loading cycles are initiated within the 2-hour period, then visible emissions observations shall be conducted for the additional cycles.  [Rules 62-4.070(3) and 62-212.400(BACT), F.A.C.; 40 CFR 63.2450(e)(2), 63.982(b), 63.987, and 63.11(b)(4)]

##### Testing and Monitoring Requirements

- VE Compliance Tests:  The flare system exhaust shall be tested to demonstrate initial compliance with the VE standard given in Specific Condition 6 of this subsection no later than 180 days after initial operation and during each calendar year (January 1 to December 31) thereafter.  [Rule 62-4.070(3), 62-212.400 (BACT), and 62-297.310(8)(a)3., F.A.C.]

- Test Requirements:  The permittee shall notify the Compliance Authority in writing at least 15 days prior to any required tests.  Tests shall be conducted in accordance with the applicable requirements specified in Appendix D (Common Testing Requirements) of this permit.  [Rule 62-297.310(9), F.A.C.]

- Test Methods:  Any required stack tests shall be performed in accordance with the following methods:

| Method | Description of Method and Comments |
| --- | --- |
| 22 | Visual Determination of Fugitive Emissions from Material Sources and Smoke Emissions from Flares (2-Hour Duration) |

- Work Practice:  Good combustion practices will be utilized at all times to ensure emissions from the flare system are minimized.  Therefore, all operators and supervisors shall be properly trained to operate and ensure maintenance of this system in accordance with the guidelines and procedures established by the manufacturer.  The training shall include good operating practices as well as methods for minimizing excess emissions.  The flare pilot shall be operated with a flame present at all times when the loadout system is operating.  [Rules 62-4.070(3) F.A.C.]

Records and Reports

- Records:  The permittee shall record in a written log the duration of each flare event and the reason for flaring.  If requested by the Compliance Authority, the permittee shall provide a copy of these records or a summary of these records.  [Rule 62-4.070(3), F.A.C.]

- Test Reports:  The permittee shall prepare and submit reports for all required tests in accordance with the requirements specified in Appendix D (Common Testing Requirements) of this permit.  [Rule 62-297.310(10), F.A.C.]

- NESHAP Requirements:  The permittee shall submit all notifications and reports required by NESHAP Subpart FFFF, including those required by its references to Subparts SS and A.  [Rule 62-210.800, F.A.C.; 40 CFR 63, Subpart FFFF]

This section of the permit addresses the following emissions units.

| ID No. | Emission Unit Description |
| --- | --- |
| 007 | Miscellaneous Storage Silos: Silos at HEF will be used to store lime for the water treatment system, limestone, hydrated lime or trona for the possible DSIS system; urea for the SNCR (if used); and fly ash from the boiler. |

The HEF will include equipment and silos for the handling and storage of dry materials.

CONSTRUCTION

- Equipment:  The permittee is authorized to construct the following silos each with a baghouse (bin vent filters) to control PM emissions:

  - One limestone, hydrated lime or trona storage silo for the DSIS;

  - One lime storage silo for the water treatment system;

  - If used in SNCR system, one urea storage silo; and

  - Fly ash storage silo.

[Application No. 0550063-001-AC]

##### PERFORMANCE RESTRICTION

- Hours of Operation:  The hours of operation of this emission unit are not limited (8,760 hours per year).  [Application No. 0550063-001-AC; Rules 62-210.200 (PTE), 62-212.400(BACT), and 62-4.070, F.A.C.]

##### Emissions Standards

- PM Standard:  The bin vent filter baghouses (or equivalent) for each storage silo shall be designed, installed and maintained to remove PM from the storage silos exhaust during loading operations.  The baghouses shall be installed and operational before the silos become operational.  The baghouses shall be designed to achieve a dust outlet loading of 0.01 gr/dscf.  Depending on the final equipment selection, the permittee may demonstrate to the Permitting Authority that the final baghouse design specification is equivalent to a dust outlet loading of 0.01 gr/dscf.  [Application Nos. 0550063-001-AC and 0550063-004-AC; Rules 62-210.200 (PTE) and 62-212.400(BACT), F.A.C.]

- VE Standard:  VE from the silo baghouses shall not exceed 5% opacity as demonstrated by initial and annual compliance tests.  [Application Nos. 0550063-001-AC and 0550063-004-AC; Rule 62-212.400(BACT), F.A.C.]

Testing and Monitoring Requirements

- Initial Compliance Tests:  Each silo shall be tested to demonstrate initial compliance with the VE emissions standard specified in Condition 4 of this subsection.  The initial test shall be conducted within 180 days after initial operation.  [Application No. 0550063-001-AC; Rule 62-212.400(BACT), F.A.C.]

- Annual Compliance Tests:  During each calendar year (January 1 to December 31), each silo shall be tested to demonstrate compliance with the VE emissions standard specified in Condition 4 of this subsection.  [Application No. 0550063-001-AC; Rule 62-212.400(BACT), F.A.C.]

- Test Requirements:  The permittee shall notify the Compliance Authority in writing at least 15 days prior to any required tests.  Tests shall be conducted in accordance with the applicable requirements specified in Appendix D (Common Testing Requirements) of this permit.  [Rule 62-297.310(9), F.A.C.]

- Test Methods:  Any required stack tests shall be performed in accordance with the following methods.

| Method | Description of Method and Comments |
| --- | --- |
| 9 | Method 9 - Visual Determination of the Opacity of Emissions from Stationary Sources (60 Minute Test) |

The above methods are described in Appendix A of 40 CFR 60 and are adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Rule 62-204.800, F.A.C.; and Appendix A of 40 CFR 60]

Records and Reports

- Test Reports:  The permittee shall prepare and submit reports for all required tests in accordance with the requirements specified in Appendix D (Common Testing Requirements) of this permit.  For each test run, the report shall also indicate the operating rate.  [Rule 62-297.310(10), F.A.C.]

This section of the permit addresses the following emissions units.

| ID | Emission Unit Description |
| --- | --- |
| 008 | One emergency generator rated at 2,000 kilowatts (kW) or 2,682 horsepower (hp) and one emergency diesel fire pump engine rated at 600 hp (448 kW) |

One emergency generator rated at 2,000 kW will be installed to provide backup electrical power in the event of a power outage at the HEF facility.  The generator will fire ULSD fuel oil.  The unit will be operated no more than 100 hours per year for testing and maintenance purposes per 40 CFR 60, Subpart IIII.  The engine will be designed to meet US EPA’s emission standards listed in 40 CFR Part 60 Subpart IIII.

One 600 hp diesel fire pump engine will be installed to provide firewater during power outages.  This unit will fire ULSD fuel oil.  This unit will be operated no more than 100 hours per year for testing and maintenance purposes per 40 CFR 60, Subpart IIII.  The engine will be designed to meet US EPA’s emission standards listed in 40 CFR Part 60 Subpart IIII.

EQUIPMENT

- Emergency Generator:  The permittee is authorized to install, operate and maintain one 2,000 kW or less emergency generator.  [Application No. 0550063-001-AC and Rule 62-210.200 (PTE), F.A.C.]

- Diesel Engine Driven Fire Pump Engine:  The permittee is authorized to install, operate and maintain one diesel engine driven fire pump engine of 600 hp or less.  [Application No. 0550063-001-AC and Rule 62-210.200(PTE), F.A.C.]

nsps APPLICABILITY

- NSPS Subpart IIII Applicability:  The emergency generator and the fire diesel fire pump engine are Stationary Compression Ignition Internal Combustion Engines (Stationary ICE) and shall comply with applicable provisions of 40 CFR 60, Subpart IIII, including emission testing or certification.  [40 CFR 60, Subpart IIII - Standards of Performance for Stationary Compression Ignition Internal Combustion Engines]

NESHAP APPLICABILITY

- NESHAP Subpart ZZZZ Applicability:  The emergency generator and the diesel fire pump engine are subject to 40 CFR 63, Subpart ZZZZ.  Pursuant to 40 CFR 63.6590(c) the generator and engine meet the requirements of Subpart ZZZZ by meeting the requirements of 40 CFR 60, Subpart IIII.  [40 CFR 63, Subpart ZZZZ - National Emission Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines (RICE)]

Performance Restrictions

- Hours of Operation:

- Emergencies:  The hours of operation during emergencies are not limited.  [Application No. 0550063-001-AC; Rule 62-210.200 (PTE), F.A.C. and NSPS 40 CFR 60, Subpart IIII]

- Non-Emergency Situations:  The emergency generator and fire pump engine may operate up to 100 non-emergency hours per year for generator maintenance and testing purposes.

[Application Nos. 0550063-001-AC and 0550063-004-AC; Rule 62-210.200 (PTE), F.A.C., 40 CFR 60, Subpart IIII]

- Authorized Fuel:  These units shall fire ULSD fuel oil.  The ULSD fuel oil shall contain no more than 0.0015% sulfur by weight.  [Application Nos. 0550063-001-AC and 0550063-004-AC; Rule 62-210.200 (PTE), F.A.C., 40 CFR 60, Subpart IIII]

EMISSION STANDARDS

- Emergency Generator Emissions Limits:  The emergency generator shall comply with the following emission limits and demonstrate compliance in accordance with the procedures given in NSPS 40 CFR 60, Subpart IIII the language of which is given in Appendix IIII.  Manufacturer certification can be provided to the Department in lieu of actual stack testing.  [40 CFR 60.4211 and Rule 62-4.070(3), F.A.C.]

| Source (model year) | CO (g/kW-hr) | PM (g/kW-hr) | SO2a (% S) | Non-Methane Hydrocarbons + NOX (g/kW-hr) |
| --- | --- | --- | --- | --- |
| Subpart IIII (2006 and later) | 3.5 | 0.20 | 0.0015 | 6.4 (NMHCb+NOX) |

- SO2 emission standard will be met by using biodiesel or ULSD fuel oil in the emergency generator with vendor certification of sulfur content of 0.0015% or less.

- NMHC means Non-Methane Hydrocarbons.

[Application No. 0550063-001-AC; NSPS 40 CFR 60, Subpart IIII and Rule 62-4.070(3), F.A.C.]

- Emergency Fire Pump Engine Emissions Limits:  The emergency fire pump engine shall comply with the following emission limits and demonstrate compliance in accordance with the procedures given in NSPS 40 CFR 60, Subpart IIII.  Manufacturer certification may be provided to the Department in lieu of actual testing.  [40 CFR 60.4211 and Rule 62-4.070(3), F.A.C.]

| Model Year | CO (g/hp-hr) | SO2a (% S) | NMHCb + NOX (g/hp-hr) | PM (g/hp-hr) |
| --- | --- | --- | --- | --- |
| Subpart IIII (2009 or later) | 2.6 | 0.0015 | 3.0 | 0.15 |

- SO2 emission standard will be met by using biodiesel or ULSD fuel oil in the emergency generator with vendor certification of sulfur content of 0.0015% or less.

- NMHC means Non-Methane Hydrocarbons.

[Application No. 0550063-001-AC; NSPS 40 CFR 60, Subpart IIII and Rule 62-4.070(3), F.A.C.]

RECORDS AND REPORTS

- Notification, Recordkeeping and Reporting Requirements:  The permittee shall adhere to the compliance testing and certification requirements listed in 40 CFR 60.4211 and maintain records demonstrating fuel usage and quality.  [Rule 62-212.400 (BACT), F.A.C. and 40 CFR 60.4211]

This section of the permit addresses the following emissions unit.

| ID | Emission Unit Description |
| --- | --- |
| 009 | Facility-Wide Fugitive VOC Emission Leaks: This emission unit consists of the fugitive VOC emissions from equipment leaks involved in the ethanol production process and associated processes at the HEF facility. Total fugitive VOC emissions from equipment leaks at the HEF facility were estimated to be 6.52 TPY. Total HAP emissions from equipment leaks at the HEF facility were estimated to be 0.33 TPY. To minimize VOC fugitive emissions, HEF shall implement a monthly LDAR program. The plan to implement the LDAR program shall be approved by the Compliance Authority in accordance with NSPS 40 CFR Part 60, Subpart VVa. The following emission units are either subject to the requirements of NSPS 40 CFR Part 60, Subpart VVa and must be addressed in the LDAR program plan or addressed by the plan as part of the BACT to minimize emissions of VOC from the HEF facility: - EU-003: Cooling Towers; - EU-004: Ethanol Production Process; - EU-005: Storage Tanks; and - EU-006: Truck Rack Product Loadout and Flare. |

NSPS SUBPART VVa

- LDAR Program:  HEF is subject to NSPS 40 CFR 60, Subpart VVa - VOC Equipment Leaks in the SOCMI, for projects that commence construction or modifications after November 7, 2006.  NSPS Subpart VVa requires a LDAR program.  HEF must demonstrate compliance with Subpart VVa, including the LDAR program, no later than 180 days after HEF becomes operational.  [40 CFR 60, Subpart VVa, and Rule 62-4.070, F.A.C.]

- Equipment Subject to NSPS, Subpart VVa:  As per Condition 11 of Section 2 of this permit, a list of all the pumps, compressors, pressure relief devices in gas/vapor service, sampling connection systems, open-ended valves or lines and valves at HEF that are subject to NSPS Subpart VVa must be submitted to the Compliance Authority no later than 90 days prior to commencing operation.  [Rules 62-212.400 (BACT), and 62-4.070, F.A.C.]

##### Testing and Monitoring Requirements

- LDAR Program Plan Implementation:  As per Condition 11 of Section 2 of this permit, the permittee must submit for approval a final LDAR program plan no later than 90 days prior to commencing operation.  Once the program plan is approved by the Compliance Authority, the permittee shall implement the program within 180 days of initial startup of the HEF.  A preliminary LDAR program plan is contained in Appendix LDAR of this permit.  [40 CFR 60, Subpart VVa ; Application No. 0550063-001-AC; Rules 62-210.200(PTE) and 62-4.070(3), F.A.C.]

- Compliance with NSPS VVa:  The permittee shall demonstrate compliance with the requirements of §§60.482–1a through 60.482–10a or §60.480a(e) for all equipment subject to NSPS Subpart VVa within 180 days of initial startup of the HEF.  [Application No. 0550063-001-AC; Rules 62-210.200(PTE) and 62-4.070(3), F.A.C.; NSPS Subpart VVa]

- Test Methods and Procedures:  The permittee shall demonstrate that the HEF facility is in compliance with the requirements of NSPS Subpart VVa following the test methods and procedures specified in §60.485a.  [Application No. 0550063-001-AC; Rules 62-210.200(PTE) and 62-4.070(3), F.A.C.; NSPS Subpart VVa]]

Records and Reports

- NSPS VVa Recordkeeping Requirements:  The permittee shall follow the recordkeeping requirements specified in §§60.486a to show compliance with NSPS Subpart VVa and submit the records to the Compliance Authority 180 days after the initial startup of the HEF and annually thereafter.  [Application No. 0550063-001-AC; Rules 62-210.200(PTE), and 62-4.070(3), F.A.C.; NSPS Subpart VVa]