### TECHNICAL EVALUATION

&

PRELIMINARY DETERMINATION

#### APPLICANT

Highlands EnviroFuels, LLC

10027 Water Works Lane

Riverview, Florida 33578

Highlands EnviroFuels

ARMS Facility ID No. 0550063

#### PROJECT

# Draft Permit No. 0550063-004-AC/PSD-FL-416A

Sugarcane/Sweet Sorghum-to-Ethanol Advanced Biorefinery and Cogeneration Plant

#### COUNTY

Highlands County, Florida

PERMITTING AUTHORITY

Florida Department of Environmental Protection

Division of Air Resource Management

Office of Permitting and Compliance

2600 Blair Stone Road, MS#5505

Tallahassee, Florida  32399-2400

July 12, 2017

- General Project INFORMATION

  - Facility Description and Location

The Highlands EnviroFuels (HEF) facility is a planned sugarcane- and sweet sorghum-to-ethanol advanced biorefinery with a maximum ethanol production rate of 36 million gallons per year.  The HEF facility will be located approximately 0.5 miles southwest of the intersection of U.S. Highway 27 and State Route 70, south of Lake Placid in Highlands County.  The UTM coordinates are Zone 17; 466.407 kilometers (km) East and 3,009.015 km North.  The locations of Highlands County and the proposed site are shown in Figure 1 and Figure 2.

Highlands County

Figure 1.  Location of Highlands County.	Figure 2.  Proposed HEF Location.

  - Primary Regulatory Categories

- The proposed facility is a major source of hazardous air pollutants (HAP).

- The facility will not operate units subject to the acid rain provisions of the Clean Air Act.

- The proposed facility is a Title V major source of air pollution in accordance with Chapter 62-213, F.A.C.

- The proposed facility is a major stationary source in accordance with Rule 62-212.400, F.A.C. for the Prevention of Significant Deterioration (PSD) of Air Quality.

  - Project Description

- HEF submitted an application for an air construction permit subject to the preconstruction review requirements of the PSD of Air Quality pursuant to Rule 62-212.400, F.A.C.  HEF has already received an air construction permit (Permit No. 0550063-004-AC/PSD-FL-416A, subsequently extended twice) for the proposed project; however, more than 18 months have elapsed without the beginning of work on the project.  Hence, the evaluation of Best Available Control Technology (BACT) for the project must be revisited.

This project entails the construction of a sugarcane and sweet sorghum-to-ethanol advanced biorefinery.  The cane (i.e. the sugarcane and sorghum) will be grown on nearby farmland.  The juice will be squeezed from the feedstock stalks, fermented, distilled and blended to make a range of ethanol/gasoline products, including E-85 (an 85/15 ethanol/gasoline blend).  The leftover stalk fiber (bagasse) will be combusted in a cogeneration biomass boiler to make process steam and up to 30 megawatts (MW, gross) of electricity.  In addition to bagasse, HEF will use supplemental biomass consisting of energy crops, wood chips and vegetative debris.  Natural gas will be used for startup shutdown and flame stabilization and during a disruption in the biomass supply.

The HEF process is akin to conventional sugar production practiced in South Florida, except that the juice is fermented and distilled to produce ethanol rather than evaporated and refined to produce sugar.  Sugarcane and sweet sorghum (cane) for the proposed HEF facility will be grown on nearby farms comprising about 30,000 to 36,000 acres.

The main process steps are:

- Cane and other biomass receiving, handling and feeding;

- Juice extraction and evaporation;

- Ethanol production (including fermentation, distillation and dehydration);

- Product storage, blending and loadout; and

- Steam and electrical production.

Table 1 indicates the emissions units (EU) associated with this project.

Table 1 -- Process Steps Comprising the HEF by EU.

| EU ID No. | Emissions Unit Description |
| --- | --- |
| 001 | Feedstock and Biomass Material Handling and Preparation |
| 002 | Biomass Boiler |
| 003 | Cooling Towers |
| 004 | Ethanol Production Process |
| 005 | Product Loadout and Flare |
| 006 | Storage Tanks |
| 007 | Miscellaneous Storage Silos |
| 008 | Emergency Equipment |
| 009 | Facility-Wide Fugitive Volatile Organic Compounds (VOC) Equipment Leaks |

- The proposed facility is essentially unchanged since the original air permit application.  The original BACT determination is included in the original Technical Evaluation and Preliminary Determination and the original permit for the project.  However, since that permit was issued, several changes have been made to the PSD permitting process.  When the original permit was issued, the Department had not yet adopted particulate matter with aerodynamic diameter less than 2.5 micrometers (PM2.5) as a separate PSD pollutant.  Furthermore, the Department now includes condensable PM in calculations of PM2.5 and PM10 (PM with aerodynamic diameter less than 10 micrometers).  Additionally, greenhouse gases (GHGs) are now included as a PSD pollutant.  Finally, the applicant has decided not to adopt synthetic limits to keep its status as an area source of HAP, rather than a major source of HAP.  As a result of its status as a major source of HAP, this facility with be subject to the “Boiler MACT” in 40 CFR 63, Subpart DDDDD, rather than the limits to maintain synthetic area-source status from the original permit.

Figure 3, provided by HEF, is a simplified process flow diagram for the project with only the key EU indicated.

001

002

003

006

005

001

004

Figure 3.  Simplified diagram of HEF sugarcane- and sorghum-to-ethanol and power facility.

  - Processing Timelines

- March 17, 2017		Applicant submitted PSD permit application.

- April 11, 2017		Department issued Request for Additional Information.

- May 19, 2017		Applicant submitted additional information; application complete.

- Process Description

  - (E.U. 001) Feedstock and Biomass Material Handling and Preparation

Cane receiving.  Refer to Figure 3.  Harvested cane stalks in the form of 6 to 12 inch billets will arrive via trucks or rail from nearby agricultural fields to the production facility.  The trucks and railcars will be weighed on a weighing bridge as they enter the unloading area.  The cane in the trucks is then transferred to the feed table via a tipping trailer.  Railcars will be bottom dumped into a feed hopper, which feeds the feed table.  The feed table is equipped with chains that convey the cane billets toward the main conveyor that feeds the juice extraction system.

Supplemental boiler fuel receiving.  Energy crops, wood chips and vegetative debris will be received from local suppliers.

Sorghum cutting, shredding and conveyance.  The cane passes through several sets of revolving cane knives and one heavy-duty shredder.  From the shredder, the cane passes to a high-speed belt carrier then to the diffuser feed carrier.  Any excess cane is returned to the high-speed belt conveyor via the excess sorghum carrier and a chute.

The diffuser consists of a horizontal slat-type conveyor with a fixed bottom consisting of perforated screens.  Beneath the screens, several semi-cylindrical transversal juice receivers will be installed.  Imbibition water is fed into the juice trough and falls onto the shredded cane mat, percolates through the fibers, passes across the screen, and is collected in the last juice receiver.

As the sorghum moves across the diffuser it is progressively washed of its sucrose content.  The wash water is circulated in a countercurrent manner such that it is progressively concentrated in sucrose in the direction of the incoming shredded cane.

The washed and shredded cane (now bagasse) is pressed in a roller system to approximately 50 percent (%) moisture and is then transferred to the biomass boiler.  The juice is pumped to a juice screen which separates fine particles prior to evaporation.  The fine particles are recycled to the diffuser.  The pH of the filtered juice is adjusted and the product is stored in the juice storage tank.

  - (E.U. 002) Biomass Boiler Steam and Power Production

The project will employ one biomass hybrid suspension grate boiler with a maximum capacity of 504.3 million Btu per hour (MMBtu/hr on a 4-hr basis) and 485.5 MMBtu/hr on a 24-hr basis.  The boiler primary fuel will be sugarcane bagasse and sweet sorghum bagasse.  Biomass consisting of energy crops, wood chips and vegetative debris will be used as a supplemental boiler fuel.  Natural gas will be used as a startup, shutdown and flame stabilization fuel and during a disruption in the biomass supply.

A simplified process flow diagram for the steam and power operations including proposed pollution control equipment is shown in Figure 4.

Oxidation Catalyst
(Ox-cat)

SNCR and OFA Systems

Dry Sorbent Injection System

(DSIS)

Figure 4.  Simplified diagram of applicant’s proposed HEF steam and electricity production cycles.

The proposed pollution control systems as described by the applicant include:

- Selective non-catalytic reduction (SNCR) based on urea [(NH2)2CO] or ammonia (NH3) injection and a high performance overfire air (OFA) system for minimizing emissions of nitrogen oxides (NOX);

- Low-NOX burners (LNB) for firing natural gas;

- Mechanical collectors and an electrostatic precipitator (ESP) will be used for control of particulate matter (PM) and metals emissions;

- Use of very low-sulfur fuels to control emissions of sulfur dioxide (SO2) and other acid gases;

- Use of clean biomass and natural gas will also control emissions of mercury (Hg) and lead (Pb);

- The modern OFA system will also control emissions of carbon monoxide (CO) and volatile organic compounds (VOC); and

- Oxidation catalyst (Ox-cat) will be used to provide further CO and VOC control as well as control of organic hazardous air pollutants (HAP).

For reference, control of PM also accomplishes control of PM with a diameter less than 10 micrometers (PM10) and less than 2.5 micrometers (PM2.5).  Control/minimization of PM, PM10, PM2.5, NOX, SO2, VOC and sulfuric acid mist (SAM – H2SO4) emissions will also control PM with an aerodynamic diameter less than 2.5 micrometers (PM2.5).  Measures such as OFA and LNB fall into the category of good combustion practices (GCP).

  - (E.U. 003) Cooling Towers

The proposed HEF facility will utilize up to three mechanical draft cooling towers.  The cooling towers will be used for the cooling of miscellaneous machinery, the condensing set and the process equipment used in ethanol production at the HEF facility.  The design parameters for the cooling towers are:  one cell with a stack height of 35 feet, a combined circulating water flow rate of 34,000 gallons per minute (gpm), a temperature of 77 °F and a design drift rate of 0.001%.  Cooling tower make up water will be primarily a suitable recycled process water stream.  Cooling tower blowdown will be treated to remove accumulated dissolved solids and then reused for cooling tower makeup.

  - (E.U. 004) Ethanol Process

The ethanol process is shown in Figure 5 and consists of juice extraction, evaporation, fermentation, distillation and dehydration.  The process description is paraphrased from the application.

004a

001

002

004b

004c

004d

004f

005

004e

Figure 5.  Simplified diagram of the HEF sugarcane- and sorghum-to-ethanol production process.

Juice Evaporation (004a).  The evaporation process concentrates the sucrose juices extracted in the diffuser.  The extracted juice is pumped from the juice storage tank to a five-effect multiple-effect evaporator, where the juice is concentrated from 14% to 22% total solids.  The concentrated juice is stored in the concentrated juice storage tank.  The steam condensate is recovered and returned to the boiler feed water system.  The condensed vapor condensate is collected and is then pumped to the diffuser as imbibition water for juice extraction.

Pre-fermentation (004b).  Concentrated juice from the concentrated juice storage tank is first cooled using the beer feed to distillation followed by a trim heater using cooling water.  The cooled, concentrated juice along with the yeast and urea (added as a nutrient) are fed to an agitated pre-fermenter.  The pre-fermenter serves as a yeast propagator and initially acclimates the yeast to the fermentation conditions.  Sulfuric acid is used to adjust the pH.  The pre-fermenter continuously recirculates the ferment through a heat exchanger to keep the temperature in the optimum range for fermentation.

Fermentation (004c).  During fermentation, sugars contained in the concentrated juice are transformed to ethyl alcohol, carbon dioxide (CO2) and various secondary products.  Secondary products include other alcohols, aldehydes, glycerin, etc.  There are a total of four agitated fermenters in series, each having controlled temperature and controlled additions of urea and yeast to maintain optimum fermentation conditions.  The ferment is continuously transferred from the pre-fermenter to the first fermenter based on level.  Flow is maintained from one fermenter to another based on level.

The product of fermentation, called “beer,” is a weak ethanol solution and contains the residue of fermentation components.  The beer is pumped to a holding tank, designated as the beer well.  The alcohol concentration in the clean beer is generally 8%.  Solid substances include yeast, bacteria, non-fermentable solids, mineral salts, albuminoidal substances and other miscellaneous substances.  Dissolved gases include CO2 and SO2.

The off-gases from the fermentation vessels are collected and sent to a packed scrubbing column, called the CO2 scrubber.  The CO2 scrubber uses water, fortified with sodium bisulfite (NaHSO3), to remove water soluble components, such as ethanol, and to chemically remove acetaldehyde.  The off-gases, which are composed primarily of CO2 with minor traces of ethanol and other organic compounds, are released to the atmosphere.  The CO2 scrubber effluent is sent to the stripper column for removal of ethanol and related compounds.

The following equipment will be used in steps 004b and 004c:  rotary screens; juice evaporator; clean and foul condensate tanks; a sulfuric acid tank; a urea tank; yeast mixing tank; pre-fermenter; pre-fermenter cooler; fermenters; fermenter coolers; beer well tank; beer/sucrose heat exchanger; and CO2 scrubbing column.

Distillation (004d).  From the beer storage, the beer is sent to a pre-heater and then to a beer/stillage heat exchanger.  The gas removed in the degassing column is cooled, scrubbed in the distillation scrubber and then released to atmosphere.  The beer column overhead is transferred in the vapor phase to the rectifier column.

The alcohol stream is increased to 91% by weight ethanol concentration in the rectifier column.  Rectifier overhead vapor is sent to the molecular sieve units to further remove water to less than 0.7% by weight in the ethanol product.  Propanol and fusel oils (non-ethanol fermentation products) are removed from the lower section of the rectifier column and combined with the 91% ethanol vapor which goes to the molecular sieves.

Rectifier bottoms are sent to a stripper column to strip remaining traces of ethanol from the rectifier bottoms.  The bottoms from the stripper column consist of almost pure water, and are reused in the process.  The stripper column overhead vapor is sent back to the rectifying column.

The following equipment will be used in step 004d:  beer distillation column; degassing column; degassing condenser; stripping column; rectification column; heat exchangers; fusel oil decanter; hydrated alcohol tank; CO2 washing column; and scrubber water degasser.

Vinasse Evaporation (004e).  The beer column bottom stillage, called vinasse, is cooled using the incoming beer as the heat sink and sent to storage.  From the storage, the vinasse is evaporated to 40% solids using a combination of several waste heat sources and live steam in three sets of multiple effect evaporators.  The concentrated vinasse is stored and then loaded onto trucks for shipment to be utilized for animal feed.

Vinasse evaporator vapor condensates will normally be less than 3,000 parts per million (ppm) chemical oxygen demand (COD) with 70 pounds per hour (lb/hr) dissolved solids, 26 lb/hr alcohol and 44 lb/hr liquid fermentation byproducts.  The condensed vinasse vapor condensate stream will be processed as necessary for reuse as cooling tower make-up.

The zeolite beds must be regenerated periodically by vacuum.  The molecular sieve bed being regenerated is first isolated from the incoming hydrated ethanol steam and the inlet of this bed is valved to a regeneration condenser.  A purge stream consisting of a portion of the dehydrated product from the on-line molecular sieve is fed into the outlet of the regenerating molecular sieve.  The non-condensable vapors from the regeneration condenser are removed via a two-stage steam ejector or a liquid ring vacuum pump.  The cooled non-condensable vapors are then fed to the distillation vent scrubber.  The condensed liquid from the regeneration condenser is reclaimed by sending it back to the rectifier column.

The following equipment will be used in step 004e:  multiple effect evaporators; raw and concentrated vinasse storage vessels; and a load out system.

Dehydration (004f):  The final stage in the ethanol production process is dehydration.  Hydrated alcohol from the distillation process, at about 96% by volume alcohol, undergoes dehydration with a molecular sieve to produce ethanol at 99.3% by weight purity.  The process is performed in a continuous operation where the hydrated alcohol is superheated by steam in a shell and tube heat exchanger to ensure that the ethanol stream is always in the vapor phase as it passes through molecular sieve zeolite beds.  The final ethanol product is condensed, cooled, and sent to the 200-proof storage tank.

The following equipment will be used in step 004f:  hydrated alcohol heater; zeolite absorber (molecular sieve); condensers and coolers; filter; dehydrated alcohol holding tank; and tie-in to CO2 washing column.

Air Pollution Control Equipment.  Two wet scrubbers will be used in the ethanol production area to control emissions of ethanol, other VOC and organic HAP.  One will be incorporated into the fermentation step (with NaHSO4) and the other will be incorporated into the distillation and dehydration steps.  According to the applicant, the two scrubbers will have ethanol/VOC removal efficiencies of 98%.

  - (E.U. 005) Volatile Organic Liquid Storage Tanks:  Denaturant/Gasoline, Alcohol, Blends

The facility will contain several volatile organic liquids (VOL) organic storage tanks for ethanol, second grade alcohol, denaturant/gasoline and blending tanks.  The following tanks will be controlled by internal floating roofs and are subject to Title 40 of the Code of Federal Regulations (CFR), Part 60, Subpart Kb (40 CFR 60, Subpart Kb):

- One fuel ethanol storage tank with a capacity of 1,000,000 gallons (gal);

- One 200 proof ethanol storage tank with a capacity of 100,000 gal;

- One off-specification (off-spec) tank with a capacity of 100,000; and

- One denaturant/gasoline tank with a capacity of 100,000 gal.

The following tanks are not subject to 40 CFR 60, Subpart Kb and will have a vertical fixed roof (VFR):

- One corrosion inhibitor tank with a capacity of 2,500 gal.

The facility will include several liquid chemical storage tanks to store sulfuric acid, phosphoric acid and ammonia or urea.  All of these tanks will be of a VFR design except for an anhydrous NH3 storage tank, which will be of a horizontal pressurized design.

  - (E.U. 006) Truck and Rail Loadout and Flare

Loading racks will be used to load out denatured fuel ethanol from the product storage tank to trucks and railcars.  In-line blending for gasoline and ethanol to produce a denatured product may also take place at the loading rack.  One loading rack will be provided for trucks, and one for railcars.  The maximum truck loading rate of each rack will be 600 gpm.  During ethanol loadout, ethanol and gasoline vapors can be generated.  The vapors are sent to the loading racks flare for destruction.  The loading racks and the flare will be permitted to operate up to 3,120 hr/yr.  A truck loading rack will be used to load ethanol and ethanol blends from the product storage tank to trucks.  The product loadout flare will have a rated capacity of 9.8 MMBtu/hr to control VOC vapors displaced from the trucks during the loading of denatured ethanol product.

  - (E.U. 007) Miscellaneous Materials Storage Silos

Materials storage silos will be installed to store material for the DSIS (if necessary) and to store ash, as well as lime for the water treatment system.  Each silo will be controlled by a baghouse or a bin vent filter.

  - (E.U. 008) Emergency Equipment

There will be one diesel or natural gas-fired electric generator of 2,000 kilowatt (kW) capacity, for purposes of supplying electric power to the facility during a black start or a power failure.  The generator will be limited to 500 hr/yr of operation during emergencies and 100 hr/yr for maintenance and testing.  There will be one diesel or natural gas-fueled 600 horsepower (hp) diesel fire pump will also be installed to provide firewater during emergencies.  This engine will be limited to 500 hr/yr of operation during emergencies and 100 hr/yr for maintenance and testing.

  - (E.U. 009) Facility-wide Fugitive VOC Equipment Leaks

Fugitive VOC emissions are grouped for the entire process and will be minimized by implementation of a monthly leak detection and repair (LDAR) monitoring program.

  - Project Emissions

Tabulations of project emissions are given and discussed in conjunction with major source review applicability in Section 4.2 below.

- Applicable Regulations

  - State Regulations

- This project is subject to the applicable environmental laws specified in Section 403 of the Florida Statutes (F.S.).  The Florida Statutes authorize the Department of Environmental Protection to establish rules and regulations regarding air quality as part of the Florida Administrative Code (F.A.C.).  This project is subject to the applicable rules and regulations defined in the following Chapters of the F.A.C.:  62-4 (Permitting Requirements); 62-204 (Ambient Air Quality Requirements, PSD Increments, and Federal Regulations Adopted by Reference); 62-210 (Permits Required, Public Notice, Reports, Stack Height Policy, Circumvention, Excess Emissions, and Forms); 62-212 (Preconstruction Review, PSD Review and BACT, and Non-attainment Area Review); 62-213 (Title V Air Operation Permits for Major Sources of Air Pollution); 62-296 (Emission Limiting Standards); and 62-297 (Test Methods and Procedures, Continuous Monitoring Specifications, and Alternate Sampling Procedures).  PSD applicability and the preconstruction review requirements of Rule 62-212.400, F.A.C. are discussed in Section 2 of this report.  Additional details of the other state regulations are provided in Section 3 of this report.

  - Federal Regulations

- The Environmental Protection Agency (EPA) establishes air quality regulations in Title 40 of the Code of Federal Regulations (CFR).  Part 60 identifies New Source Performance Standards (NSPS) for a variety of industrial activities.  Part 61 specifies National Emissions Standards for Hazardous Air Pollutant (NESHAP) based on specific pollutants.  Part 63 specifies NESHAP provisions based on the Maximum Achievable Control Technology (MACT) for given source categories.  Federal regulations are adopted in Rule 62-204.800, F.A.C.  Additional details of the applicable federal regulations are provided in Section 5 of this report.

- PSD Applicability Review

  - General PSD Applicability

The Department regulates major stationary sources in accordance with Florida’s PSD program pursuant to Rule 62-212.400, F.A.C.  PSD preconstruction review is required in areas that are currently in attainment with the Ambient Air Quality Standards (AAQS) or areas designated as “unclassifiable” for these regulated pollutants.  As defined in Rule 62-210.200, F.A.C., a facility is considered a “major stationary source” if it emits or has the potential to emit 5 tons per year of lead, 250 tons per year or more of any PSD pollutant, or 100 tons per year or more of any PSD pollutant and the facility belongs to one of the 28 listed PSD major facility categories.  PSD pollutants include:  carbon monoxide (CO); nitrogen oxides (NOX); sulfur dioxide (SO2); particulate matter (PM); particulate matter with a mean particle diameter of 10 microns or less (PM10); PM2.5; volatile organic compounds (VOC); lead (Pb); Fluorides (Fl); sulfuric acid mist (SAM); hydrogen sulfide (H2S); total reduced sulfur (TRS), including H2S; reduced sulfur compounds, including H2S; municipal waste combustor organics measured as total tetra- through octa-chlorinated dibenzo-p-dioxins and dibenzofurans; municipal waste combustor metals measured as particulate matter; municipal waste combustor acid gases measured as SO2 and hydrogen chloride (HCl); municipal solid waste landfills emissions measured as nonmethane organic compounds (NMOC); and mercury (Hg).

Once it is determined that a facility is a PSD major source, PSD applicability for any project at the facility is based on emissions thresholds known as the “significant emission rates” (SER) as defined in Rule 62-210.200(Definitions), F.A.C.  Emissions of PSD pollutants from the project meet or exceed these rates are considered “significant” and the Best Available Control Technology (BACT) must be employed to minimize emissions of each PSD pollutant.  Although a facility may be “major” for only one PSD pollutant, a project must include BACT controls for any PSD pollutant that equals or exceeds the corresponding SER.  SER threshold by pollutants are given in Table 2.

Table 2 – List of SER by PSD Pollutant.

| Pollutant | SER (TPY) | Pollutant | SER (TPY) |
| --- | --- | --- | --- |
| CO | 100 | NOX | 40 |
| PM/PM10/PM2.5 | 25/15/10 | Ozone (VOC) 2 | 40 |
| PM2.5 (NOX) | 40 | PM2.5 (SO2) | 40 |
| Ozone (NOX) 2 | 40 | Sulfuric Acid Mist (SAM) | 7 |
| SO2 | 40 | Lead (Pb) | 0.6 |
| Hg | 0.1 | GHG | 75,000 (CO2e) 3 |
| - Excluding fluoride and those pollutants defined for Pulp and Paper, MWC, MSW landfills. - Ozone (O3) is regulated by its precursors (VOC and NOX). PSD for PM2.5 can be triggered by its precursors (NOX and SO2). - In making the CO2e calculation, the values listed in 40 CFR 98, Subpart A, Table A-1 are used to weight emissions by their respective Global Warming Potential (GWP). For example, the current GWP factors for four of the GHGs are: CO2 = 1; CH4 = 25; N2O = 298 and SF6 = 22,800. |  |  |  |

Rule 62-210.200, F.A.C. defines “BACT” as:

An emission limitation, including a visible emissions standard, based on the maximum degree of reduction of each pollutant emitted which the Department, on a case by case basis, taking into account:

- Energy, environmental and economic impacts, and other costs;

- All scientific, engineering, and technical material and other information available to the Department; and

- The emission limiting standards or BACT determinations of Florida and any other state;

determines is achievable through application of production processes and available methods, systems and techniques (including fuel cleaning or treatment or innovative fuel combustion techniques) for control of each such pollutant.

If the Department determines that technological or economic limitations on the application of measurement methodology to a particular part of an emissions unit or facility would make the imposition of an emission standard infeasible, a design, equipment, work practice, operational standard or combination thereof, may be prescribed instead to satisfy the requirement for the application of BACT.  Such standard shall, to the degree possible, set forth the emissions reductions achievable by implementation of such design, equipment, work practice or operation.

Each BACT determination shall include applicable test methods or shall provide for determining compliance with the standard(s) by means which achieve equivalent results.

In no event shall application of best available control technology result in emissions of any pollutant which would exceed the emissions allowed by any applicable standard under 40 CFR Parts 60, 61, and 63.

In addition, applicants must provide an Air Quality Analysis that evaluates the predicted air quality impacts resulting from the project for each PSD pollutant.

  - PSD Applicability for the Project

The project is located in Highlands County, which is in an area that is currently in attainment with the AAQS or otherwise designated as unclassifiable.  The facility emits or has the potential to emit 250 tons per year or more of at least one PSD pollutant.  Therefore, the facility is a major stationary source and the project is subject to a PSD applicability review.  Table 3 identifies the estimated project emissions based on the application.

Table 3 – Applicant’s Estimated PTE (tons per year) of Key PSD Pollutants.

| Operation/EU | Pollutant |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | CO | NOX | PM a | PM10 | PM2.5 | SO2 | SAM | VOC | Hg | Pb | GHG |
| Biomass Material Handling (001) |  |  | 14.2 | 3.4 | 0.7 |  |  |  |  |  |  |
| Boiler (002) | 552.9 | 184.3 | 27.7 | 49.8 | 40.1 | 200.4 | 6.8 | 31.3 | 0.025 | 0.18 | 406,582 |
| Cooling Towers (003) |  |  | 0.37 | 0.19 | 0.19 |  |  |  |  |  |  |
| Ethanol Production (004) |  |  |  |  |  |  |  | 87.6 |  |  | 124,976 |
| Storage Tanks (005) |  |  |  |  |  |  |  | 3.9 |  |  |  |
| Product Loadout and Flare (006) | 5.64 | 1.04 | 0.052 | 0.052 | 0.052 | 0.009 |  | 7.0 |  |  | 2,429 |
| Miscellaneous Storage Silos (007) |  |  | 0.85 | 0.85 | 0.85 |  |  |  |  |  |  |
| Emergency Equipment (008) | 1.29 | 8.84 | 0.087 | 0.087 | 0.087 | 0.0063 |  | 0.26 |  |  |  |
| Fugitive Equipment Leaks (009) |  |  |  |  |  |  |  | 6.5 |  |  |  |
| Totals | 559.8 | 8.8 | 43.3 | 54.4 | 42.0 | 200.4 | 6.8 | 136.6 | 0.025 | 0.18 | 533,987 |
| SER | 100 | 40 | 25 | 15 | 10 | 40 | 7 | 40 | 0.1 | 0.6 | 75,000 |
| PSD Applies? | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | No | Yes |
| - PM includes only filterable particulate matter. PM10 and PM2.5 include both filterable and condensable particulate matter. |  |  |  |  |  |  |  |  |  |  |  |

As shown in the table, the project is subject to PSD preconstruction review for emissions of CO, NOX, PM, PM10, PM2.5, SO2, VOC, and GHG.

The applicant estimates HAP emissions to be 55.0 tons per year.  The highest emissions of any single HAP are expected to be 41 tons per year of hydrogen chloride, using the NESHAP Subpart DDDDD emission limit as the emission factor for the boiler.

- Department’s Project Review

  - Applicable State Regulations

- For this project, the following state regulations are applicable.

# Chapter 62-4, F.A.C.

# Rule 62-4.070(1), F.A.C., Standards for Issuing or Denying Permits; Issuance; Denial.

# This rule applies to all permitting decisions:

- A permit shall be issued to the applicant upon such conditions as the Department may direct, only if the applicant affirmatively provides the Department with reasonable assurance based on plans, test results, installation of pollution control equipment, or other information, that the construction, expansion, modification, operation, or activity of the installation will not discharge, emit, or cause pollution in contravention of Department standards or rules.

# Chapter 62-204, F.A.C.

# Rule 62-204.220(1), F.A.C., Ambient Air Quality Protection.

# This rule applies to all air permitting decisions.

- The Department shall not issue an air permit authorizing a person to build, erect, construct, or implant any new emissions unit; operate, modify, or rebuild any existing emissions unit; or by any other means release or take action which would result in the release of an air pollutant into the atmosphere which would cause or contribute to a violation of an ambient air quality standard established under Rule 62-204.240, F.A.C.

# Rule 62-204.240, F.A.C., Ambient Air Quality Standards.

# This rule applies to all air permitting decisions.  Refer to list of pollutants and ambient air quality standards provided therein and discussed in the Ambient Air Quality Section of this evaluation.

# Rule 62-204.800(8), F.A.C., 40 CFR 60, NSPS.

# The federal NSPS are incorporated by reference in Rule 62-204.800(8), F.A.C.  The applicable NSPS provisions are summarized below under “Applicable Federal Regulations.”

# Rule 62-204.800(11), F.A.C., 40 CFR 63, NESHAP.

# Federal NESHAP standards of 40 CFR 63 are incorporated by reference in Rule 62-204.800(11), F.A.C.  The applicable NESHAP provisions are summarized below under “Applicable Federal Regulations.”

# Chapter 62-210, F.A.C.

# 62-210.200, F.A.C., Definitions.

- The project is a Title V or “Major Source” of air pollution because the PTE of at least one regulated pollutant will exceed 100 TPY.

- The project is a major source of HAP because it will have PTE of 10 TPY or more of any one HAP or 25 TPY or more of any combination of HAP.

- The project is classified as a “Major Stationary Source” (PSD-source) because it emits 100 TPY or more of a PSD pollutant and is one of the 28 facility categories listed in the definition with the PSD applicability threshold of 100 TPY.

# Rule 62-210.300, F.A.C., Permits Required.

- Unless exempted, the owner or operator of any facility or emissions unit which emits or can reasonably be expected to emit any air pollutant shall obtain appropriate authorization (i.e. a permit) from the Department prior to undertaking any activity at the facility or emissions unit for which such authorization is required.

# Rule 62-210.350, F.A.C. Public Notice and Comment.

- A notice of proposed agency action on permit application, where the proposed agency action is to issue the permit, shall be published by any applicant.

- The rule details additional public notice requirements for emissions units subject to PSD.  Examples include:  the location and nature of the project; whether BACT has been determined; PSD increment consumption; and notification to the public of the opportunity to submit comments or request a public hearing (meeting).

# Chapter 62-212, F.A.C.

# Rule 62-212.300, F.A.C., General Preconstruction Review Requirements.

- This rule generally applies to the construction or modification of air pollutant emitting facilities in those parts of the state in which the state ambient air quality standards are being met.

# Rule 62-212.400, F.A.C., PSD.

- The rule applies because the project is a major stationary (PSD) source.

# Chapter 62-213, F.A.C.

- Because the facility is a Title V source, the applicant will be required to apply for and obtain a Title V operation permit in the future.

# Chapter 62-296, F.A.C.

# Rule 62-296.320, F.A.C., General Pollutant Emission Limitation Standards.

- This rule prohibits the discharge of air pollutants which cause or contribute to an objectionable odor;

- This rule specifies a visible emissions standard of 20 percent (%) opacity; and

- The rule prohibits emissions of unconfined PM provisions without taking reasonable precautions to prevent such emissions.

# Rule 62-296.410, F.A.C., Carbonaceous Fuel Burning Equipment.

- Cane bagasse is carbonaceous fuel when directly combusted and this rule requires that the carbonaceous component of fuel combustion comply with a PM standard of 0.2 lb/MMBtu.  Visible emissions are limited to 30% opacity except that 40% opacity is permissible for not more than 2 minutes in any hour.

  - Applicable Federal Regulations

- For this project, the following federal regulations are applicable.

- NSPS in 40 CFR 60

- 40 CFR 60, Subpart A – General Provisions which regulates all EU that are subject to a NSPS standard and, in particular, flare pilot flames (EU 005);

- 40 CFR 60, Subpart Db – Industrial-Commercial-Institutional Steam Generating Units (EU 002);

- 40 CFR 60, Subpart Kb - Standards of Performance for Volatile Organic Liquid Storage Vessels for Which Construction, Reconstruction, or Modification Commenced After July 23, 1984 (EU 006);

- 40 CFR 60, Subpart IIII – Stationary Compression Ignition Internal Combustion Engines (ICE) (EU 008);

- 40 CFR 60, Subpart VVa – VOC Equipment Leaks from SOCMI Processes (EU 002, 003,004, 005, 006, 007 and 009).

# NESHAP in 40 CFR 63

- 40 CFR 63, Subpart A – General Provisions (to the extent explicitly identified within each applicable 40 CFR 63 standard);

- 40 CFR 63, Subpart ZZZZ – Stationary Reciprocating Internal Combustion Engines (RICE).  This subpart requires all affected area source units to meet the applicable emission standards of 40 CFR 60, Subpart IIII.  40 CFR 63, Subpart A is explicitly excluded when applying this standard.

- 40 CFR 63, Subpart DDDDD – Industrial, Commercial, and Institutional Boilers and Process Heaters (EU 002);

- 40 CFR 63, Subpart FFFF – Miscellaneous Organic Chemical Manufacturing (which references Subparts H, Q, SS, TT, UU, WW, and GGG).

- BACT Review for Roadway Emissions and feedstock and Biomass Handling (EU 001):  PM, PM10, and PM2.5 Emissions

  - Discussion

PM, PM10, and PM2.5 represent the only pollution of concern from EU 001.  Refer to the description of EU 001 in Section 2.1 above.  The trucks that will be used to deliver sweet sorghum feedstock and supplemental boiler fuel biomass along with the biomass handling and processing itself will generate fugitive dust.

Figure 6 below is a diagram of the bagasse and supplemental boiler biomass feed system.  Because of the biomass high moisture content, fugitive emissions are expected to be minimal from this part of the process.

The boiler biomass (bagasse and supplemental) will be stored in piles located in the biomass yard in the southwestern quadrant of the HEF site.  When required, the material will be reclaimed using a mobile front wheel loader, and placed onto the live reclaim area from which it will be conveyed to a scalping screen or shaker screen and then transported to the boiler feed bin and fed into the biomass boiler.

Figure 6.  Boiler Biomass Feed System.

  - Applicant’s Proposal

HEF proposes to utilize reasonable precautions and a best management practices (BMP) plan approved by the Department for controlling fugitive dust emissions from this emission unit. These precautions include the following:  enclosing conveyors (e.g. that the conveyance belt for the biomass is totally enclosed from above thus preventing wind from causing fugitive dust emissions with the bottom of conveyance belt accessible for maintenance and repairs) and material drop points, shredders and screens wherever practical; contouring storage piles to minimize wind erosion; utilizing water sprays on storage piles as needed; paving all main plant access roads; sweeping and watering of paved surfaces as needed to remove dust; and utilizing water sprays on ash material from the boiler, as necessary.

  - Department’s Review

The Department accepts the procedures described by the applicant as BACT for sweet sorghum feedstock and supplemental biomass receiving and handling, with the addition of wetting the gravel areas, as necessary, during dry conditions.  In addition, where practical, dust collectors must be installed at drop and transfer points in the biomass handling systems and the paved areas must be vacuumed swept as needed to prevent fugitive dust emissions.

- BACT Review for Biomass-Fueled Boiler (EU 002)

  - NOX Emissions

    - Discussion

# NOX formation in the boiler may occur by three different mechanisms:  fuel NOX is formed from nitrogen compounds contained in fuel (fuel nitrogen); thermal NOX is formed from molecular or atomic nitrogen (N2) and oxygen (O2) present in combustion air; and prompt NOX is formed in the proximity of the flame front as intermediate combustion products.

# Bubbling Fluidized bed (BFB) Boiler Principles.  The applicant proposes to install a grate stoker boiler and not a BFB boiler.  However, it is useful to discuss the alternative design of a BFB boiler due to its inherently lower emission characteristics.

# BFB boiler beds are typically maintained at temperatures on the order of 1,350 to 1,700 degrees Fahrenheit (°F).  This minimizes thermal NOX formation but not fuel NOX formation.  The furnace temperature is higher above the fluidized bed where the OFA is introduced but not high enough to form thermal NOX.

# Combustion within the BFB bed occurs under reducing (O2 starved) conditions provided by the primary air.  The fuel in the bed undergoes drying, and partial combustion.  Following is the Department’s theoretical and simplified explanation of the manner by which combustion proceeds, focusing on the formation and destruction of NOX.  The process involves literally hundreds of steps or reactions expressed as the simplified and unbalanced equations (Eq.) below.

Equation 1.  The fuel immediately above and within the bed is heated and pyrolyzed releasing hydrocarbon radicals (CHi*).  These, in turn, catalytically or otherwise react with NO to form hydrogen cyanide (HCN) according to:

Eq. 1

Where:

i = 1, 2, 3

Equation 2.  HCN in turn destroys more NOX in the reducing environment according to:

Eq. 2

Equation 3.  Ammonia-like radicals (NHi*) are also released during pyrolysis.  Under reducing conditions these radicals destroy NO according to:

Eq. 3

This mechanism suppresses formation of NO by the pyrolyzed fuel nitrogen and recruits that nitrogen to combat NOX in reactions that at first glance look much like SCR or selective non-catalytic reduction (SNCR) discussed further below.

Reactions 2 and 3 can be catalytically enhanced based on the presence of various species within such an environment.  Also, they can be accelerated by attaining a relatively high temperature within the reducing atmosphere but well below that which would promote thermal NOX formation.  Other reactions involving CO or hydrogen (H2) also destroy NOX in this reducing atmosphere and can be to varying degrees catalytically enhanced.  Additional volatile and char combustion occurs in the higher temperature free board region above the bed.  CharC denotes char carbon and CharN denotes char nitrogen.

Equation 4 and 5.  Under the reducing conditions, even the char can assist on NOX destruction as follows:

Eq. 4

Eq. 5

Eventually the NOX destruction reactions will proceed much more slowly and some of the remaining fuel nitrogen forms additional NOX.

Equations 6, 7, 8 and 9.  In the presence of the progressively oxidizing environment effected by the two OFA levels, NOX formation rather than destruction predominates.

Eq. 6

Eq. 7

Eq. 8

Eq. 9

# The management of NOX formation and destruction involves promotion of Eq. 1 through 5 to form N2 before the inevitable and progressive addition of OFA causes Eq. 6 through 9 to dominate.  This can be accomplished to the greatest degree by delaying and then adding the OFA in stages.

It was previously mentioned that peak flame temperatures will increase when lower moisture content biomass fuels are combusted and during low load boiler operations.  During these periods, flue gas recirculation (FGR) will be employed to lower the peak flame temperatures thus avoiding the tendency to form thermal NOX.

The NOX formation and destruction considerations must also be coupled with CO, PM and VOC management in a combined strategy that constitutes GCP.

Stoker Principles.  Modern stoker units for biomass firing are normally mechanical rotating grates or water/air-cooled vibrating grates depending on the fuel moisture content.  Fuel is typically introduced into the boiler through multiple fuel chutes.  Preheated combustion air is supplied under the grate as well as above via an OFA system.  Depending on the fuel moisture content, the combustion air is pre-heated to 350 to 650 °F.  The furnace temperature is greater than experienced in a BFB boiler and thus it is possible to form both fuel and thermal NOX.

Due to high shaft velocities in the lower furnace and the manner by which fuel is spread or thrown onto the grate, some unburned fuel (carbonaceous ash) is carried out of the furnace.  In order to recover the energy value of this carbonaceous ash, stoker-fired boilers typically include a re-injection system that recycles the carbonaceous ash back into the furnace.

Because of the hot particle carryover and possible effects on fabric filters, ESP technology is usually incorporated into wood biomass stoker technology projects.  A mechanical dust collector is also typically installed to prevent heavy (possibly abrasive) particle carryover from reaching the ESP.

Figure 7 includes a diagram of a Detroit Hydro-Grate and a typical stoker-based process schematic.  Sized fuel is metered to a series of distribution devices which spread it uniformly over the stoker grate surface.  Fine particles of fuel are rapidly burned in suspension assisted by OFA.  Coarser, heavier fuel particles are spread evenly on the grate forming a thin, fast-burning fuel bed.

ESP

Figure 7.  Detroit Hydro-Grate and Typical Stoker-based Process Schematic.

The Detroit Hydro-Grate stoker includes an automatic ash discharge system and water-cooled grates.  The higher combustion air temperature needed to burn high moisture fuel can be maintained without damaging the grates.

While the spreader stoker technology results in higher uncontrolled NOX emissions than BFB technology, a stoker can achieve similarly low emissions through the use of GCP and add-on controls.  Basically, all of the NOX formation and destruction phenomena described for the BFB boiler in Eq. 1 through 9 exist for the stoker to varying degrees.  The technology, known as VLN, employs combustion system design, which in addition to conventional primary and secondary air streams, also features a new internal stream of gas called “VLN gas,” which is drawn from the combustor and re-injected into the furnace.  The gas flow distribution between the primary and secondary air, as well as the VLN gas, is controlled to yield the optimal flue gas composition and furnace temperature profile to minimize NOX formation and optimize combustion.  HEF has proposed to build a stoker boiler but with volatilization, drying and partial combustion occurring above the grate in a manner analogous to a BFB.

Add-on NOX Control.  One add-on NOX control is SNCR, whereby NH3 or urea is injected at a point in the process characterized by a suitable temperature window between about 1,500 and 1,900 F depending on residence time, turbulence, oxygen content, and a number of other factors specific to the given gas stream.  The reaction products are N2 and water vapor (H2O).  SNCR destroys NOX by a multi-step process as which is simplified in the equations below.

Equation 10.  NH3 reacts with available hydroxyl radicals (OH*) to form amine radicals (NH2*) and water per the following theoretical equation:

Eq. 10

Equation 11.  Amine radicals combine with NO to form nitrogen and water as follows:

Eq. 11

Equation 12.  The two steps are typically expressed as a single “global reaction”.

Eq. 12

Similar simplified reactions describe the destruction of NO2, which is present in much less concentrations than NO.  One drawback with SNCR is that some of the NH3 can be converted to NOX and excessive NH3 injection is occasionally required to effect good reduction.  Excess NH3 (called slip) can combine with chloride and sulfate species in the exhaust and cause visible emissions.  Additionally good CO control is necessary when employing SNCR due to interference with the reaction as described.

Equation 13.  CO competes with NH3 for available OH radicals needed to effect Eq. 10.

Eq. 13

In the case of selective catalytic reduction (SCR) technology, the NH3 is injected in the presence of catalyst and at a lower temperature than encountered in the furnace.  The reactions are more complete and efficient and NH3 slip is minimized.  When an SCR is located downstream of other control devices, it is sometimes necessary to heat the exhaust stream to the appropriate temperature range for effective operation.

A variation of clean-side SCR called regenerative SCR (RSCR) was developed by Babcock Power, Inc. (BPI) for the purpose of optimizing the efficiency and reducing the cost of such reheat.  Ox-cat is usually part of the RSCR package.

Basically a relatively cool exhaust stream is heated by passing through preheated thermal media (Cycle 1) called a heat recovery bed before passing through the SCR catalyst at a moderate temperature.  The exhaust gas is then slightly heated by a gas-fueled duct burner.  The higher heat of the exhaust gas is then imparted to a second thermal media bed.  Eventually the second bed reaches a greater temperature than the first and the flow through the RSCR unit is reversed as shown in Cycle 2.

The RSCR unit is essentially heat engine that operates at a moderate temperature while using and expelling low temperature exhaust gas.  Thermodynamic losses to the environment are minimized by their arrangement.  According to BPI, the RSCR system results in a net increase (system inlet to system outlet) of only 7 °F compared with 50 to 75 °F for more typical heat exchanger arrangements.

One practical benefit of a cool SCR arrangement such as RSCR is that the air can be located right after the economizer.  This reduces the actual temperature and volumetric flow rate of gas through the control equipment.  RSCR systems have been retrofitted downstream of PM control devices at four existing biomass power plants in Maine (Boralex Stratton and Boralex Fort Fairfield) and New Hampshire (Whitefield Power and Bridgewater Power).  RSCR was also installed at a facility in Vermont (McNeil Burlington).  In addition to retrofits, RSCR has been specified for several proposed biomass and WTE projects including the small (38 MW) Palmer Energy biomass project in Massachusetts and the larger Fairfield WTE facility in Maryland.  RSCR is often the benchmark against which costs and controls for new projects are weighed.

Despite perceptions to the contrary, application of SCR downstream of a low temperature PM control device do not necessarily require reheating of the exhaust gases prior to the SCR unit.  CRI Catalyst (Shell Group) has for years provided low temperature SCR catalyst for use in combustion sources at chemical and refining plants as well as gas turbines and waste-to-energy plants.  The possibility of low temperature SCR without reheat has been confirmed by the Department’s inquiries regarding the operation of at least two of the RSCR installations in New England.  According to discussions with the operator at Whitefield Power, NH, the duct burners are not actually used although the NOX limit is continuously achieved.  Operators at the Bridgewater Power, NH, facility has made the same determination and this finding has been documented in a permit modification that provides for a lower minimum operating temperature for the RSCR system.

Under NSPS Subpart Db, the boiler will be subject to a limit of 0.20 lb NOx per MMBtu, on a 30-day rolling average basis, including all periods of operation.  Compliance with this limit is to be demonstrated by CEMS.

    - Applicant’s Proposal

The applicant’s BACT proposal is 0.10 lb/MMBtu on a 30-day rolling basis based on selection of a hybrid suspension/grate boiler and incorporation of GCP and SNCR.  This limit would not apply during periods of startup and shutdown.  Additionally, because there is a one-hour ambient standard for NO2 concentrations, the applicant has proposed short-term NOX limits, on a 24-hour basis.  The applicant has requested that this 24-hour limit equal 0.15 lb/MMBtu if startup, shutdown, and malfunction (SSM) events may be excluded, or 0.18 lb/MMBtu if startup and shutdown events are not excluded.

The applicant performed a cost effectiveness analysis for both SNCR and SCR.  The applicant estimates that SCR has a cost of $3,584 per ton of NOX removed, while SNCR has a cost of $1,200 per ton of NOX removed.

To ensure proper operation of the SNCR system, the applicant has proposed a limit on ammonia slip of 25 ppmvd @ 7% O2.  This is a reduction from the current limit of 30 ppmvd @ 7% O2.

    - Department’s Review

According to its definition, BACT is based on the technology the “Department determines is achievable through application of production processes and available methods, systems and techniques (including fuel cleaning or treatment or innovative fuel combustion techniques)”.

The use of a BFB boiler versus stoker boiler involves just variations within the same production process which in the present case is combustion of biomass in a furnace to produce steam and electric power.  Furthermore the key feature of the stoker grate designs for bagasse stokers is drying, volatilization and partial combustion in suspension (prior to falling on the grate).

Consideration of a BFB boiler versus a grate stoker with suspension drying, volatilization and partial combustion (combustion technique) is within the scope of a BACT definition and review.  BACT also includes treatment techniques and a combination of such techniques can improve the emission profile of a stoker to a level where is equals that of a BFB boiler.  Therefore it is allowable to specify a BFB boiler as the basis of BACT emission limits while allowing installation of a stoker boiler.

The proposed limit is in line with other recently issued BACT determinations for biomass-fueled boilers.  The proposed limit is essentially identical to the limit issued recently for the U.S. Sugar Clewiston Mill Boiler No. 9.  The 468 MMBtu/hr wood-fueled boiler at the Sierra Pacific facility near Anderson California, received a limit of 0.13 lb/MMBtu, based on the use of SNCR.

The Department accepts the applicant’s BACT proposal for this project of 0.10 lb NOX/MMBtu (30-day average) on the basis of incorporating GCP and SNCR in a hybrid suspension grate boiler.  Compliance will be demonstrated by a NOX continuous emission monitoring system (CEMS).  Inclusion of Ox-cat to control CO, VOC and HAP will provide flexibility to achieve the NOX BACT by GCP and SNCR.  The Department does not reject BFB and SCR and these remain options for consideration in future projects.  To help assure that there is no exceedance with the NO2 ambient standard, the Department will set an additional BACT limit for NOX of 0.15 lb/MMBtu, on a 24-hour rolling basis, which will not apply during startup and shutdown.

To assure that periods of startup and shutdown are covered by an emissions limit, the Department will adopt as a “Secondary BACT” standard the Subpart Db NOX emission limit of 0.2 lb/MMBtu, which applies at all times.

Further, the Department will set a limit on ammonia slip of 25 ppmvd @ 7% O2, to be demonstrated by initial and annual stack tests.

  - VOC and CO Emissions

    - Discussion

Refer to the previous descriptions of the BFB boiler and stoker boiler operation.  CO and VOC (including organic HAP) are products of incomplete combustion.  Combustion in the lower furnace occurs in sub-stoichiometric conditions.  Also, there often exist localized sub-stoichiometric pockets or cells even if overall excess oxygen conditions are maintained in the lower furnace.

A great deal of CO is evolved as well as VOC (including hydrocarbon radicals and other species).  The CO, hydrocarbon radicals and reduced nitrogen compounds (as previously mentioned) participate in reactions that assist in primary NOX control.

Sufficient OFA, temperature and turbulence is necessary to complete the burnout of CO, fine char and VOC.  Clearly throttling NOX formation by staging combustion using the OFA ports affects CO and VOC formation in the furnace.  Basically, the manner by which the boiler is operated (e.g. favoring NOX over CO/VOC control) is part of an overall source emission strategy that considers the emissions limits and costs of add-on controls.

# If GCP are geared primarily to control NOX then there is less freedom when also controlling CO and VOC by the same GCP.  If GCPs are not sufficient to achieve low CO and VOC emissions, an oxidation catalyst (Ox-cat) is an option.  As in the case of SCR catalyst, the preferred location of an Ox-cat system is after the PM control device (e.g. ESP).

Ox-cat can be effective for CO removal at temperatures as low as 300 °F, and the application indicates a stack exit temperature of 340 °F, suggesting that there should be minimal to no need for additional heating of the exhaust gas.  Moreover, Ox-cat is even more effective in destroying formaldehyde (HCHO - the HAP emitted in the greatest amount from the HEF boiler) than its effectiveness in destroying CO.

Under NESHAP Subpart DDDDD, this boiler will be subject to a CO limit of 900 ppmvd @ 3% O2, with compliance demonstrated by CO CEMS.  This limit does not apply during periods of startup or shutdown.

    - Applicant’s Proposal

The applicant has proposed the use of the most stringent control option available, oxidation catalyst.  The original BACT determination for this unit required the installation of an ox-cat system for an initial 24-month test period, along with a CO limit of 0.30 lb/MMBtu on a 30-day rolling average basis (by CEMS) and a VOC limit of 0.017 lb/MMBtu, based on annual stack test.  After the 24-month period, the facility would submit a report to the Department, which would adjust these limits based on the initial tests, or allow for the removal of the ox-cat system.  The applicant has proposed that this original BACT determination be re-validated.

To cover periods of startup and shutdown, the applicant has a requested an annual limit of 552.9 tons per year.  Furthermore, the applicant notes that the Subpart DDDDD work practices will limit emissions of CO during these periods.

    - Department’s Review

There have been essentially no changes in the appropriate degree of CO and VOC control since the original BACT determination for this facility.  In the original permit application submitted in 2011, the applicant’s estimated cost effectiveness was $1,044 per ton of CO and VOC removed, assuming a 60% control efficiency.  This is a very reasonable cost to incur for this degree of control.  The Department re-affirms its original BACT determination for this project.

In June 2017, the applicant received a quote for a catalyst system, resulting in an estimate of total annualized costs of $373,300.  If 50% control of CO and VOC is assumed, this would result in a combined cost effectiveness of $1,283/ton; however, this 50% control estimate is likely a lower bound on system performance.  A 75% control assumption results in a cost of $852/ton, and a 90% control assumption leads to a cost of $751/ton.  Also, note that the oxidation catalyst would have co-benefits for HAP (formaldehyde) reduction, though these are not quantified here.

In Permit No. 0530380-010-AC for the wood-fueled Brooksville Power Plant, the Department determined that an oxidation catalyst was not technically feasible in a space-constrained retrofit situation, but that this would not be a concern for a greenfield facility, such as Highlands EnviroFuels.

The Department has determined that BACT for this project is the requirement to install ox-cat with a final permit CO and VOC limits to be set in the future.  The initial permit limits will be 0.30 lb CO/MMBtu (30-day average) and 0.017 lb VOC/MMBtu.

The ox-cat system will be installed and tested for a 24-month test period to determine if catalyst poisoning occurs due to the bagasse fuels.  At the end of the 24-month test period, a test report will be submitted to the Compliance and Permitting Authorities.  The report will include:

- Daily averages of boiler operating parameters to include heat input, steam generation, fuel mixtures (cane bagasse, sorghum bagasse, supplemental biomass fuel and natural gas) and corresponding weights of each biomass and MMscf of natural gas burned as fuel used including each supplemental fuel (energy crops, wood chips and vegetative debris);

- Daily NOX and CO CEMS data in lb/MMBtu and lb/hr, all HAP and VOC stack test results from both the boiler stack and ethanol process scrubber stacks in lb/MMBtu and lb/hr, all maintenance actions performed on the ox-cat system; and

- If necessary, a recommendation for the ox-cat system removal with supporting justification or any requested permit modification for the continued use of the ox-cat system.

Based on all the data (boiler parameters, pollutant and HAP emissions and maintenance actions) in the test report, the Department will either adjust the CO and VOC emission limits downward to reflect the actual CO and VOC emission rates or allow removal of the ox-cat system.  If the ox-cat system is removed, the CO emission limit will remain 0.30 lb/MMBtu on a 30-day rolling average basis and the VOC limit will remain at 0.017 lb/MMBtu.

Compliance with the CO limit shall be demonstrated by a CO CEMS.  Initial and annual VOC compliance tests will be required.

While the supplier and applicant have expressed some doubts regarding the lifetime of the catalyst, the Department notes that the biomass fired will be fairly consistent and there should be few unknown or unexpected species that will get past the ESP and poison the catalyst.

As a secondary BACT limit, the Department will adopt the work practice standards to which the boiler will be subject in NESHAP Subpart DDDDD (the “Boiler MACT”).  These include the use of a handful of clean fuels for startup and the requirement for a periodic boiler tune-up.

  - SO2 Emissions

    - Discussion

SO2 is formed from sulfur contained in fuels.  Sulfur in the fuel reacts with atmospheric oxygen to form SO2.  SAM is formed by further oxidation of SO2 to sulfur trioxide (SO3) prior to exiting the process. SO3 readily combines with water vapor (H2O) available in flue gas to form SAM.  SO2 is an important precursor of secondary particulate matter formed in the atmosphere, frequently in the form of ammonium sulfate, (NH4)2SO4.  In the absence of add-on controls or internal scrubbing in the process, the amount of sulfur emitted from the process in the form of SO2 or SAM is generally equal to the amount of sulfur entering the process with fuels.

Potential technically feasible control technologies for SO2 include wet or dry sorbent injection, wet flue gas desulfurization, a spray dryer, regenerative flue gas desulfurization, and low-sulfur fuels.  These were evaluated in the original BACT determination for this project and have not changed appreciably since 2011.

For boilers that combust natural gas, or a mixture of natural gas and other fuels, Subpart Db imposes a limit for SO2 emissions of 0.20 lb/MMBtu.  However, units firing only natural gas and a mix of other fuels with a potential SO2 emissions rate of 0.32 lb/MMBtu or less are exempt from this SO2 limit.  The natural gas/bagasse mixture meets this exemption criterion, so the boiler is not subject to a limit on SO2 under Subpart Db.

    - Applicant’s Proposal

The applicant requests that the current SO2 BACT limit of 0.060 lb/MMBtu, on a 30-day rolling basis, by CEMS, be reaffirmed.  This limit relies primarily on the low sulfur content of bagasse and the inherent alkalinity and scrubbing potential of this fuel.  The original BACT determination also included the use of dry sorbent injection; however, this was primarily for the control of HCl emissions, in order to avoid the status of a major source of HAP emissions.  Because the facility has decided to accept major HAP status, the dry sorbent injection to reduce HCl emissions is no longer necessary.  Therefore the applicant has requested that dry sorbent injection not be considered part of BACT for SO2 for this project.

To ensure that the short-term (1-hour) ambient standard for SO2 is met, the applicant has proposed a 1-hour limit of 0.078 lb/MMBtu, including all operation.  Emissions of SO2 are expected to be unaffected by startup conditions, since SO2 emissions should depend only on the amount of fuel consumed and the sulfur content of the fuel.

    - Department’s Review

The applicant’s requested limit is in line with recent SO2 BACT determinations for biomass-fueled boilers in Florida.  The limit for U.S. Sugar Boiler No. 9, issued in 2016, is 0.064 lb/MMBtu, with compliance by annual stack test, without any add-on SO2 controls.  The U.S. Sugar Boiler No. 9 SO2 limit is 0.06 lb/MMBtu, which rounds to 0.064 lb/MMBtu.  These limits are based on an annual three-hour stack test, so they are essentially three-hour limits.  The applicant’s proposed limit of 0.060 lb/MMBtu, on a 30-day basis, is consistent with these limits.  This limit will apply at all times, including periods of startup and shutdown.  Dry sorbent injection will not be required unless the SO2 limit cannot be met without it.  The applicant will be required to leave space for a dry sorbent injection system in case it is needed.  However, the low sulfur content of sugarcane and sorghum bagasse, the inherent scrubbing capabilities of the bagasse ash, and the long averaging period will likely make this emission limit achievable without add-on controls.  The Department will also set a 1-hour limit of 0.078 lb/MMBtu, which is consistent with the ambient modeling performed for the project, to assure that the 1-hour ambient standard for SO2 will not be exceeded.

  - PM, PM10, and PM2.5 Emissions

    - Discussion

Particulate matter is a mix of substances in the solid or liquid state in the atmosphere, excluding liquid water, of microscopic or sub-microscopic size, but larger than molecular dimensions.  The size fraction of particulate matter with aerodynamic diameter less than 10 micrometers is called PM10, while the size fraction of particulate matter with aerodynamic diameter less than 2.5 micrometers is called PM2.5.  Chemical speciation of PM2.5 in the atmosphere has shown that it is composed of many different substances, and this composition varies spatially and temporally.  Common chemical constituents of PM2.5 include carbonaceous compounds, sulfate ions, nitrate ions, ammonium ions, crustal components, and sea salt.

Chemically speciated measurements of ambient PM2.5 composition are not very common.  Speciated fine PM measurements are made at the Chassahowitzka National Wildlife Refuge, which is approximately 150 miles northwest of Clewiston.  This site is part of the IMPROVE monitoring network.  While data from this site may not be entirely representative of PM composition near Clewiston, it does give a qualitative sense for PM composition in much of peninsular Florida.  Average PM2.5 composition at the Chassahowitzka site from 2001 through 2014 is shown in Figure 8 (Average PM2.5 concentration for this period is 7.8 micrograms per cubic meter).

Figure 8.  Average PM2.5 Composition at Chassahowitzka IMPROVE Site, 2001-2014.

Some processes directly emit particles, in a form such as soot.  These directly emitted particles are called filterable PM, since a stack test method employing a filter (such as EPA Method 5) would measure these particles.  Some particulate matter is formed very soon after exiting the stack, upon reaching ambient temperature: this is referred to as condensable PM, since it is formed from rapid condensation upon reaching atmospheric temperatures.  Condensable PM can be thought of as the result of a physical process (i.e. condensation), as opposed to a chemical process (i.e. chemical reactions).  Together, filterable and condensable PM are called primary PM.  Primary PM, therefore, is PM that is in the aerosol phase when it is emitted, or very shortly thereafter.

In contrast to primary PM, secondary PM forms in the atmosphere from chemical reactions between precursor gases.  An example of this is the reaction between atmospheric sulfur dioxide and ammonia to form ammonium sulfate.  Similarly, VOCs can be oxidized in the atmosphere and form organic aerosol.

For BACT purposes, “PM” includes only filterable PM, while PM10 and PM2.5 include both filterable PM (under the appropriate size cut-off) and condensable PM.  At the time of the previous BACT determination for this facility, the Department had not yet adopted PM2.5 as a PSD pollutant, and the Department was not yet considering condensable PM as part of PM10 or PM2.5.  Therefore the previous BACT determination included only filterable PM and filterable PM10.

Under NESHAP Subpart DDDDD, the boiler will be subject to a limit on (filterable) PM of 0.026 lb/MMBtu.  NSPS Subpart Db imposes a limit on (filterable) PM of 0.030 lb/MMBtu.

    - Applicant’s Proposal

For PM and PM10, the applicant has requested a reaffirmation of the previously issued BACT determination.  This includes the use of a wet sand separator (a type of cyclone) and electrostatic precipitator.  The applicant considered a fabric filter baghouse to be technically infeasible for the project, given concerns that hot embers from a bagasse-fired hybrid suspension grate boiler could pose a fire risk.  Further, the applicant considers a highly efficient ESP to be equivalent in effectiveness to a baghouse.  This limit is 0.015 lb/MMBtu for filterable PM, to be demonstrated by initial and annual Method 5 stack test.  Because Method 5 does not employ any size cut, the use of Method 5 implicitly makes filterable PM a proxy for filterable PM10.  While this PM10 limit does not include condensable PM, condensable PM will be considered as part of the PM2.5 limit.

The applicant proposes a limit on PM2.5 (filterable + condensable) of 0.022 lb/MMBtu.  Compliance would be demonstrated by initial and annual stack test.  The applicant also notes that there exists minimal information on condensable PM emissions from bagasse-fired boilers and requests that this limit be raised if initial testing shows that it cannot be met.  In order to limit condensable (and secondary) PM, the applicant has also proposed reducing the current limit for ammonia slip from the SNCR system from 30 ppmvd @ 7% O2 to 25 ppmvd @ 7% O2.

    - Department’s Review

The applicant’s proposed limit for filterable PM is less than the applicable standards from Subparts Db and DDDDD.  The proposed limit is in line with other recently issued BACT limits for PM, including the Sierra Pacific project in California (2014, 0.020 lb/MMBtu), the North Springfield biomass project in Vermont (2013, 0.019 lb/MMBtu), and the Beaver Wood Energy Fair Haven project in Vermont (2012, 0.019 lb/MMBtu).  These project have utilized a mix of ESP technology and baghouse technology.  The Department also notes that the U.S. Sugar Boiler No. 9 project (2016) utilized an ESP as BACT controls for PM2.5.  The Department will reaffirm the BACT determination for filterable PM and PM10, at 0.015 lb/MMBtu, to be demonstrated by annual stack test for filterable PM.

Only a handful of BACT determinations for PM2.5 (filterable + condensable) have been issued for biomass boilers.  The Department issued a limit of 0.0268 lb/MMBtu for U.S. Sugar Boiler No. 9.  The Abengoa Energy project in Kansas received a limit of 0.030 lb/MMBtu, including 0.013 lb/MMBtu filterable PM2.5 and 0.017 condensable PM.  The applicant’s proposed limit of 0.022 lb/MMBtu is more stringent than either of these previously issued limits, and the Department will adopt this proposed limit for PM2.5.  The Department does recognize the limited amount of data regarding condensable PM emissions from biomass-fueled boilers.  If initial testing indicates that the standard cannot be achieved, the Department will revisit this BACT limit, after one year of additional quarterly testing for PM2.5.  In this scenario, the BACT limit would be set at the highest of these five initial tests, plus an additional margin of 10% to account for variability in feedstock, operations, etc.

  - GHG Emissions

    - Discussion

Three greenhouse gases are expected to be emitted from the boiler in this project:  carbon dioxide (CO2), methane (CH4), and nitrous oxide (N2O).

Carbon dioxide is the primary product of combustion of carbon-based fuels in air.  The exothermic reaction between fuels and molecular oxygen in air results in the breaking of carbon-carbon bonds or carbon-hydrogen bonds in fuels, the release of energy in the form of heat, and the formation of CO2 and water.

Negligible amounts of CH4 and N2O are expected from this project.  The complete combustion of fuel to CO2 is the desired outcome in the boiler, so formation of CH4 is expected to be minimal.  A very small amount of N2O can be produced as a combustion byproduct.  At the high temperatures associated with combustion, atmospheric N2 and oxygen O2 react to form, among other byproducts, N2O.

Greenhouse gases are categorized and compared on an “equivalency” basis according to their “global warming potential” (GWP).  The GWP of a substance is calculated by determining the ratio of the amount of warming due to the emission of a unit mass of the substance, integrated over a chosen time period, to the amount of warming due to the emission of a unit mass of CO2, integrated over the same time period.  The most commonly used time period for GWP calculations is 100 years.  The US EPA uses GWP values of unity for CO2, 25 for CH4, and 298 for N2O.  Multiplying emissions of each of these three gases by its respective GWP, and summing the result, yields a CO2-equivalent (CO2e) greenhouse gas emissions estimate.

    - Controls for GHGs

Carbon Capture and Sequestration (CCS):  CCS entails capturing the CO2 from flue gas, transporting it to an appropriate location for storage, and sequestering it underground.  This CO2 is usually used for processes such as enhanced oil recovery, in which the CO2 aids in the production of fossil fuels from underground.  Deep saline formations, which are large, porous rock formations, also present a potential opportunity for underground CO2 storage.

The separation and capture of CO2 from the effluent stream can be performed using several different technologies, such as absorption, adsorption, low-temperature distillation, gas separation membranes, or mineralization and biomineralization.  The transport of CO2 from the facility to its ultimate storage site is usually accomplished via pipeline, at a pressure of over 1,000 pounds per square inch.  CO2 can also be transported in insulated tanks at low temperature via seagoing vessels, rail, or truck.  Potential locations for long-term underground storage of CO2 include depleted oil and gas reservoirs, un-mineable coal seams, and underground saline formations.

CCS has been deployed at a very small number of commercial-scale facilities.

Efficient Boiler Technology:  Various boiler types are capable of combusting biomass to create steam.  These include fluidized bed combustion, suspension combustion, stoker combustion, and pile combustion.  The applicant has selected a hybrid suspension grate boiler for this project.  This type of boiler is especially appropriate for moist biomass fuel, such as bagasse.

In this case, the use of a hybrid suspension-grate boiler is a key design choice made by the applicant for this project.  To include other boiler types in a BACT analysis would constitute a redefinition of the source.  Therefore, other boiler technologies will not be considered in defining BACT.

Low-Carbon Fuel:  The use of biomass is a key design parameter for this project – bagasse is a readily available byproduct from the harvesting of sugar cane or sorghum.  Natural gas, the lowest-emitting fossil fuel, will be used as an auxiliary fuel for startups and shutdowns.  However, to consider other fuels in defining BACT for this project would constitute a redefinition of the source.

Additionally, while the Department takes no position on the carbon neutrality of biomass fuels, the applicant notes that bodies such as the Intergovernmental Panel on Climate Change and agencies such as the US EPA consider biomass fuels to be at least partially, if not completely, carbon neutral.  The carbon neutrality of the fuel depends on many factors such as the chosen time horizon for analysis and the sustainability of the practices used to grow and harvest the crop.  The bagasse to be fired in this boiler will be grown on existing crop land that will not involve the removal of trees, and the sugar cane and sorghum will generally re-grow at roughly the same rate at which it is processed, on a season-by-season basis.  However, a full discussion of the carbon neutrality of bagasse fuels is beyond the necessary scope of a BACT review for this project.

Energy Efficiency Options:  There are a number of options for the design, operation, and maintenance of a boiler that serve to maximize efficiency, which in turn minimize GHG emissions.  The design thermal efficiency of the planned boiler is 68.0%, which is higher than those of U.S. Sugar Boilers No. 8 and 9.

Combined Heat and Power (CHP):  A CHP system utilizes the steam generated in a boiler to provide heat to industrial processes and to generate electricity.  Steam generated by the proposed boiler will be used for both of these purposes.  Steam generated by the boiler will first go to the electric turbine generator to generate electricity.  Lower pressure steam from the turbine generator will then be used for heat in the ethanol production process.

    - Applicable NSPS

NSPS Subpart TTTT includes limits on greenhouse gas emissions from new electric generating units.  To be subject to a limit under this subpart, a unit must (1) have a base load rating greater than 250 MMBtu/hr on fossil fuel, and (2) serve a generator or generators capable of selling greater than 25 megawatts (MW) of electricity to a utility power distribution system (40 CFR 60.5509(a)).  Condition (1) is not met, since the unit will have a capacity of 249 MMBtu/hr on natural gas.  Furthermore, condition (2) is not met, since the unit will not serve a generator capable of selling more than 25 MW of power to the grid.  Therefore, there is no applicable GHG NSPS for this unit.

    - Applicant’s Proposal

In determining a proposed GHG BACT, the applicant next eliminated options it considered to be technically infeasible.  The applicant considered CCS to be technically infeasible for this project for several reasons.

- The first argument focused on the capture of CO2 from flue gas.  There have been just a handful of power plant CCS demonstration projects that have utilized CO2 capture.  These projects have utilized coal as their primary fuel.

- The applicant noted that the compression of CO2 to sufficient pressures for transport (approximately 2000 pounds per square inch) generates a large amount of heat, which necessitates additional demand for cooling water, or cooling through electrical means.  Either method has significant environmental impacts.

- The transportation infrastructure required to move compressed CO2 from the project site to an appropriate place for storage does not yet exist.  Presumably, this would mean that many miles of pipeline would have to be constructed to transport the compressed CO2.  This would have significant economic and environmental consequences.

- Additionally, the applicant noted the need for a long-term storage site.  Currently, there are no demonstrated permanent CO2 sequestration locations in Florida, nor are there already any CO2 pipelines in place in the state.  A 2015 report from the US Geological Survey indicated that while there is potential for carbon sequestration in a few formations in the southern part of Florida, no studies have yet demonstrated industrial-scale usage or suitability of these formations for carbon sequestration.

The applicant has proposed the use of biomass fuel with natural gas as a startup fuel, along with a highly efficient boiler design, as constituting BACT for this project.  The applicant has requested a GHG BACT limit of 0.42 lb CO2 per lb steam, on a 12-month rolling basis, including all periods of operation.  A calculation based on the carbon content of bagasse suggests an ideal emissions rate of 0.40 lb CO2 per lb steam; the applicant’s requested limit includes an additional 5% to account for non-ideal operation, such as startup and shutdown.

    - Department’s Review

The Department agrees that CCS is not technically feasible for this project.  Only a handful of projects have successfully captured CO2 from power (or steam) generation.  The Mississippi Power Kemper plant, designed with CCS for enhanced oil recovery (EOR) in mind, is still in the late construction phase and is intentionally located near oil fields to make EOR more feasible.  Similarly, the SaskPower Boundary Dam Carbon Capture Project in southern Saskatchewan is located near Saskatchewan oil fields to facilitate EOR.  CO2 not used for EOR at the SaskPower project will be stored in a nearby (less than 2 miles from the plant) brine-filled sandstone formation.  The Petra Nova project in Texas utilizes CO2 captured from a coal-fired power plant for EOR in nearby oilfields.  This confluence of local opportunities for EOR and amenable geology is clearly not the case for the proposed Highlands EnviroFuels facility.  The lack of information regarding candidate sites for sequestration, the lack of infrastructure for transporting compressed CO2, and the very high costs cause CCS to be excluded from BACT for this project.

The Department also agrees that the use of bagasse and natural gas, together with the use of an energy efficient boiler design, constitute components of GHG BACT for this project.  The Department will set a GHG BACT limit of 0.42 lb CO2 per lb steam, on a 12-month rolling basis, including all periods of operation.  Emissions of other GHGs, such as methane and nitrous oxide, are expected to be negligible.

- BACT Review for COOLING TOWERS (EU 003)

  - Discussion

Up to three cooling towers will be used for machine cooling, cooling the condensing set in the power block, and process cooling.  The design parameters for the cooling towers are:  one cell with a stack height of 35 feet, a combined circulating water flow rate of 34,000 gallons per minute (gpm), a temperature of 77 °F and a design drift rate of 0.001%.

Cooling towers emit PM, PM10, and PM2.5 based on the total dissolved solids (TDS) loading in the recirculating water.  According to the applicant, the plant will use fresh water with a concentration TDS of only 500 ppmw.  The applicant estimated PM/PM10/PM2.5 emissions at 0.37/0.19/0.19 TPY.

If not properly maintained and operated, heat exchangers in the ethanol process and machines may leak thereby contaminating the water of the associated cooling tower with VOC.  The VOC will subsequently be stripped from the water stream by the air flow thus emitting the VOC to the atmosphere.  HEF did not estimate VOC or organic HAP from the cooling tower presumably due to expected good operation and maintenance.

  - Applicant’s proposal

The applicant proposes to reaffirm the original BACT determination for this project.  This includes a drift rate of 0.001% together with a recordkeeping requirement to demonstrate that the TDS of the incoming cooling makeup water is maintained at 500 ppmw or less on an annual basis.  The Department also required expansion of the leak detection and repair (LDAR) plan required for the facility under NSPS Subpart VVa to include the machine cooling and process cooling towers.  This will prevent the intrusion of organic liquids into the cooling water streams in heat exchangers.

  - Department’s Determination

In view of the very low TDS value, the requested drift rate is acceptable at 0.001% together with a permit requirement recordkeeping requirement that can demonstrate that TDS of the incoming cooling makeup water is maintained less than or equal to 500 ppmw on an annual basis, the Department accepts the applicant’s BACT proposal for the cooling towers.

As required by NSPS Subpart VVa, the applicant submitted a preliminary Leak Detection and Repair (LDAR) Program plan.  The Department will require expansion of the LDAR Program plan required for the facility pursuant to NSPA Subpart VVa to include the machine cooling and process cooling towers.  The applicant will be required to collect a sample of cooling water from each tower on a weekly basis and analyze it for VOC.  This will enable the early detection of leaking heat exchangers, thereby minimizing VOC emissions (including organic HAP) and odors.   The applicant is required to submit a final LDAR Program plan that includes the cooling tower to the Compliance Authority 90 days before the HEF facility becomes operational.

- BACT Review for ETHANOL PRODUCTION PROCESS (EU 004)

  - VOC Emissions

    - Discussion

The ethanol production process will result in the emissions of ethanol (C2H5OH) and other VOC such as acetic acid, lactic acid, and methanol (a HAP).  These emissions will occur from the fermentation, distillation, and dehydration steps, as the ethanol is separated from the fermentation products.  Properly designed scrubbers and thermal oxidizers (TO) can effectively control VOC and HAP emissions from ethanol production processes.

Wet scrubbers (water as solvent) can achieve good VOC reduction objectives when used on ethanol plants.  Ethanol (C2H5OH), which comprises the bulk of the VOC emissions, is completely miscible in water.  A properly designed scrubber could achieve a level of removal 99% or greater.  Organic acids and strongly polarized molecules such as acetic acid (CH3COOH) and methanol (CH3OH – a HAP) can also be removed in a properly designed scrubber due to their strong interaction with water.  A wet scrubber using water as a solvent can therefore be designed to accomplish excellent removal of VOC, especially from the distillation/dehydration steps.

Non-polar VOC such as ethyl acetate (C4H8O2) and HAP such as acetaldehyde (C2H4O) and acrolein (C3H4O) are not as efficiently removed as C2H5OH when using a wet scrubber that uses only water as a solvent.  Reagents such as sodium bisulfite (NaHSO3 - a food preservative) can be added to the scrubber water that will react with aldehydes to form an “adduct” that precipitates, thus allowing removal of at least the key HAP.

While a TO can be used to treat emissions from the fermentation and distillation/dehydration scrubbers, these are typically used to control emissions from the drying of solid residue such as Dried Distillers Grains with Solubles (DDGS), which is a byproduct of the more traditional grain-to-ethanol production process.

    - Applicant’s Proposal

The Department’s original BACT determination included the use of two wet scrubbers to control VOC (and HAP) emissions from the ethanol production process.  The scrubbing liquor would include a sodium bisulfite reagent to enhance VOC and HAP capture of aldehydes, particularly acetaldehyde and acrolein.  Each scrubber would have a design capture efficiency for VOC and HAP of 98%.  The limits on VOC emissions were 19.01 lb/hr for the fermentation scrubber stack and 2.78 lb/hr for the distillation/dehydration scrubber stack.  The applicant has proposed that the Department re-affirm this previous BACT determination.

    - Department’s Determination

There have been no fundamental changes in VOC controls in the period since the original BACT determination.  The Department agrees that a thermal oxidizer would be not be cost effective for this unit, considering the high capture efficiency of the proposed scrubber system with sodium bisulfite reagent and the destruction of ethanol product that would occur in a thermal oxidizer.  The Department accepts the wet scrubbers described by the applicant as BACT for this emissions unit with the following emission limits:  VOC emissions through the fermentation scrubber stack shall not exceed 19.01 lb/hr, and VOC emissions through the distillation/dehydration scrubber vent shall not exceed 2.78 lb/hr.  As was noted in the original BACT determination, the vendor will need to insure that the appropriate scrubber liquids or additives are used to remove C4H8O2 (the key VOC other than ethanol) in order to comply with the VOC emission limit.

Initial and annual stack tests for these two VOC limits will be required.  In addition, the Department establishes the following requirements:

- The applicant will have to comply with the Department’s objectionable odor regulation Rule 
62-296.320(2), F.A.C., which states:  “No person shall cause, suffer, allow or permit the discharge of air pollutants which cause or contribute to an objectionable odor”.  While the applicant may install wet scrubbers, the Department notes that the applicant would have to apply for a permit to install additional control equipment or inject reagents into the scrubbers to address objectionable odor problems.

  - GHG Emissions

    - Discussion

CO2 is a natural product of the fermentation process.  A molecule of sucrose (C12H22O11), extracted from the sugarcane (or sorghum), is converted in microorganisms such as yeast to two molecules of glucose (C6H12O6).  The microorganisms then convert the glucose to ethanol and carbon dioxide:

C6H12O6→2 C2H5OH+2 CO2	Eq. 14

(Other sugars may also ferment similarly, though they would not necessarily produce ethanol and carbon dioxide in equimolar amounts, as in Eq. 14.)

This CO2 is completely biogenic in nature – all the carbon released as CO2 comes from the sugars in the sugarcane or sorghum, which had previously been atmospheric CO2.  See Section 7.5, above, for a full discussion on greenhouse gases.  Carbon capture and storage, as described in Section 7.5.2, could potentially be employed for the exhaust gases from the fermentation stack.  However, the same barriers that make it uneconomical for the boiler also prevent it from being cost effective for the fermentation process.

    - Applicant’s Proposal

The applicant calculates that annual emissions of CO2 from the fermentation process will be 122,096 tons, while annual ethanol production will be 30 million gallons.  This yields a production-based emissions rate of 8.14 lb CO2 per gallon of ethanol produced.  The applicant also notes that this is an uncertain number, impacted by biological processes which can be difficult to control.  The applicant has requested a limit of 8.14 lb CO2 per gallon of ethanol produced, to be tested only by an initial test.  The emissions factor determined in this initial test would then be used to estimate future CO2 emissions, based on the amount of ethanol produced.  Because of the lack of available data from similar facilities, and because of the difficulties with biological processes, the facility has also requested that this limit be adjusted after initial startup if it proves unattainable.

    - Department’s Determination

If the fermentation reaction follows Eq. 14 exactly, and if ethanol is recovered perfectly, one mole of CO2 is produced for each mole of ethanol produced.  Assuming a density of 6.59 lb/gal for the final ethanol product, and a molar mass of 46.1 lb per lb-mole, one gallon of ethanol equals 0.143 lb-moles of ethanol.  This means that 6.29 pounds of CO2 (0.143 lb-moles of CO2) are generated per gallon of ethanol.  If Eq. 14 is the assumed ethanol production pathway, then 6.29 lb CO2 per gallon of ethanol would represent the lowest possible emissions of CO2 per unit of ethanol produced.  Considering the inevitable production of some unwanted fermentation products such as fusel oils and the inconsistencies associated with biological processes, establishing a limit somewhat greater than 6.29 lb CO2 per gallon of ethanol is entirely reasonable.  The applicant’s requested limit is 29% greater than this theoretical limit.

The Department notes that the Abengoa project in Kansas received a BACT limit for the fermentation process of 5.89 lb CO2e per gallon of anhydrous ethanol produced.  However, the Abengoa project included a different slate of feed stock (corn stover, wheat straw, switchgrass, etc.), and presumably, different fermentation technology and chemistry as a result.  For the Abengoa project, the facility proposed as the main method of compliance with this limit (and the State of Kansas accepted) the monitoring of process efficiency, as indicated by a CO2 CEMS, as well as the use of LDAR to minimize evaporative product losses.  Considering the potential for a highly variable emissions profile due to biological processes, a CO2 CEMS is necessary to accurately measure CO2 emissions over a long time period.

For this process, BACT is essentially an efficient process that minimizes the amount CO2 emitted per unit of ethanol produced.  The applicant’s requested emission limit of 8.14 lb CO2 per gallon of ethanol produced is reasonable, and the Department will set this as the limit for this process.  In order to assure continuous monitoring of the efficiency of the process, and to account for the variability in emissions due to biological processes, compliance will be demonstrated with a CEMS for CO2, on a 12-month rolling basis, rolled monthly.  The use of LDAR for the minimization of product losses will also be considered a component of BACT, since optimizing product recovery helps to minimize the emissions per unit of product.

The Department notes that this facility will employ a batch fermentation process.  During a batch process, CO2 production ramps up at the beginning of a fermentation, then peaks or plateaus, then decreases as fermentation slows.  A traditional stack test cannot capture this type of temporal pattern, further indicating at a CEMS is a more appropriate option for monitoring.

Initial compliance with this limit will be demonstrated during a special 30-day initial compliance period.  If the limit cannot be achieved during this initial compliance demonstration, then the Department will re-evaluate the BACT limit based on emissions and production data from the first year of operation of the facility.  In this scenario, the BACT limit would be set equal to the average emissions rate (pounds CO2 per gallon of ethanol produced) for the first 12 months of operation, plus an additional 10% to account for the inherent variability in biological processes.

- BACT Review for STORAGE TANKS (EU 005)

  - Discussion

The only pollutant of concern related to the proposed storage tanks is VOC.  There will be five tanks storing volatile organic liquids (VOL): one small (2,300 gallons) tank for corrosion inhibitor, and four larger tanks (between 100,000 and 1,000,000 gallons) for fuel ethanol, 200-proof ethanol, off-specification ethanol, and denaturant/gasoline.  These four tanks will be subject to NSPS Subpart Kb, and they will be fitted with internal floating roofs, or will have a pressure relief device/vent condenser to control VOC to an equivalent level.  The original BACT determination was the use of internal floating roofs on the Subpart Kb tanks.  Tanks containing VOC but not subject to Subpart Kb must use pressure relief valves with vapor condensers.

  - Applicant’s Proposal

The applicant has proposed the reaffirmation of the previous BACT determination.

  - Department’s Determination

The Department agrees that its original determination still constitutes BACT for the storage tanks.  Pollutant controls from tanks have not changed appreciably since the original BACT determination.  If the permittee decides to use pressure relief valves in lieu of internal floating roofs, it must provide proof of the valves’ equivalency as defined in the NSPS to the Compliance Authority before construction of the blending and storage VOL tanks commences.

- BACT Review for TRUCK RACK LOADOUT AND FLARE (EU 006)

  - Discussion

The denatured ethanol product (ethanol blended with gasoline) will be loaded onto tanker trucks at a maximum rate of 600 gallons per minute using submerged fill.  The maximum throughput product rate is 36,000,000 gal/yr of ethanol, blended with gasoline.  During this filling process, vapors that were already present in the trucks’ tanks are displaced by the incoming ethanol and gasoline, leading to emissions of VOC.  This operation is subject to the standards for transfer racks in NESHAP Subpart FFFF, for miscellaneous organic chemical manufacturing.  Subpart FFFF requires the control of vapor emissions from loading rack operations through several possible options, including a flare, a non-flare control device with a destruction efficiency of 98%, a mechanism to vent emissions to a fuel gas system, or a vapor balancing system to route collected vapors back to the storage tank.  The BACT option must be at least as stringent as the Subpart FFFF requirements.

The Department’s previous BACT determination included the use of a flare, with a rated capacity of 9.8 MMBtu/hr and a design control efficiency of 98%, for the destruction of collected vapors.  This is also one of the Subpart FFFF control options.

  - Applicant’s Proposal

The applicant has proposed the reaffirmation of the previous BACT determination.

  - Department’s Determination

The applicant agrees that a capture system with flare constitutes BACT for the emissions unit.  This control option is one of the NESHAP options, so it is clearly at least as stringent as the NESHAP requirement.  The flare is an appropriate BACT control for this process.

- BACT Review for MISCELLANEOUS DRY MATERIAL STORAGE SILOS (EU 007)

  - Discussion

These silos include one limestone, hydrated lime or trona storage silo for the DSIS (if needed); one lime storage silo for the water treatment system; if used in SNCR system, one urea storage silo; and one fly ash storage silo.  The silos will emit small amounts of PM, PM10, and PM2.5 with the applicant estimating the total to be 0.85 TPY of each.

  - Applicant’s Proposal

The Department’s original BACT determination was to control PM/PM10/PM2.5 emissions from the miscellaneous dry material storage silos by standard type bin vent filters.  These are passive control devices that do not have a fan.  When the silos are pneumatically loaded from trucks, the conveying air must exit the silo through the bin vent filter.  These filters will control dust emissions in the exhaust gas to a concentration of 0.01 grains per dry standard cubic foot (gr./dscf).  These storage silos will each have a standard type bin vent filter to control dust emissions.  The applicant has proposed reaffirmation of this as BACT.

  - Department’s Determination

The Department concurs with the applicant’s proposal for BACT.  The Department also establishes that VE from each bin vent filter during material loading shall not exceed 5% opacity as demonstrated by initial and annual compliance tests.  A VE emission reading of 5% opacity or less may be used to establish compliance with the 0.01 gr./dscf standard.  A visible emission reading greater than 5% opacity will require the permittee to perform a PM emissions stack test on the bin vent filter within 60 days to show compliance with the PM limit.  Because essentially all of this PM is expected to be in the filterable form, only a test for filterable PM (Method 5) would be required in this scenario.

- BACT Review for EMERGENCY ENGINES (EU 008)

  - Discussion

The applicant has proposed the installation of one emergency generator rated at 2,000 kilowatts to provide backup electrical power in the event of a power outage.  A 600-horsepower diesel fire pump engine will be installed to provide fire water if necessary.  The engines will be operated only in emergencies, or for testing purposes – non-emergency use may not exceed 100 hours per year.  These engines will be subject to NSPS Subpart IIII, which limits emissions of CO, non-methane hydrocarbons (NMHC) + NOX, PM, and SO2.

  - Applicant’s Proposal

The Department’s original BACT determination was for the engines to comply with NSPS Subpart IIII.  Note that the limit on NMHC + NOX is effectively a limit on both VOC and NOX emissions.  The applicant has proposed a reaffirmation of this original BACT determination.

  - Department’s Determination

The limits in Subpart IIII, for compression ignition reciprocating internal combustion engines, are sufficiently stringent to be BACT for these emergency engines.  For greenhouse gases, efficiently operating engines are effectively the only way to limit emissions from emergency equipment.  For this reason, the installation of engines certified to meet the requirements of Subpart IIII will also constitute BACT for GHGs.

- BACT Review for FUGITIVE EQUIPMENT LEAKS (EU 009)

  - Discussion

Uncontrolled leaks from equipment such as from pumps, compressors, relief devices, flanges, valves, etc. can be significant sources of VOC and HAP emissions.  This equipment is part of several of the emission units associated with this project.  Because the HEF project is a SOCMI facility, it is subject to NSPS Subpart VVa - Equipment Leaks in the Synthetic Organic Chemical Manufacturing Industry (for projects that commence construction or modifications after November 7, 2006).  Subpart VVa has specific requirement for controlling such leaks from pumps, compressors, relief devices, flanges, valves, etc.  One requirement is the development of a Leak Detection and Repair (LDAR) program to insure compliance with VVa and any other requirements to control equipment leaks.  The VOC emissions from the following other emission units at the proposed HEF facility also fall under EU-012:

- EU-003:  Cooling Towers;

- EU-004:  Ethanol Production Process;

- EU-005:  Storage Tanks; and

- EU-006:  Truck Rack Product Loadout and Flare.

For equipment handling significant amounts of methane, LDAR would also be an important strategy for the control of GHG emissions.  However, the HEF facility will handle primarily solid feedstocks and liquid products, not including methane.

  - Applicant’s Proposal

The Department’s original BACT determination included the use of a LDAR program and compliance with Subpart VVa as BACT for this emissions unit.  The applicant has request a reaffirmation of this previous determination.

  - Department’s Determination

Subpart VVa is a comprehensive requirement.  Together with the LDAR program, Subpart VVa will complement the BACT determinations for each process emission unit that is a source of VOC and possibly odor.  The Department accepts the applicant’s proposal as BACT and will include a requirement to submit the details of a site-specific LDAR program pursuant to Subpart VVa no later than 90 days before the HEF becomes operational.  In addition, equipment such as pumps, compressors, pressure relief devices, sampling connection systems, open-ended valves, line valves and flanges or other connectors in VOC service and any devices or systems subject to NSPS, Subpart VVa and the associated emissions unit must be identified with a list submitted to the Compliance Authority no later than 90 days before the HEF facility becomes operational.  Finally, per Subpart VVa, HEF must demonstrate compliance with NSPS, Subpart VVa no later than 180 days after the initial startup of the HEF facility.

- ODOR CONSIDERATIONS

  - Discussion

In previous sections, reference was made to Rule 62-296.320(2), F.A.C., which states:  “no person shall cause, suffer, allow or permit the discharge of air pollutants which cause or contribute to an objectionable odor”.  However, even with control measures, conventional grain ethanol plants are often associated with odors.  The most important odor source in a conventional grain ethanol plant is from the residual grain material after fermentation and separation of the ethanol.  The potential for odor from an ethanol plant utilizing sweet sorghum as its feedstock is probably less than a corn feedstock based facility.  Still odor is a concern and must be addressed.

  - Applicant’s Proposal

The applicant proposes the following measures to control VOC and odors at the HEF facility:

- Just-in-time delivery of ethanol process feedstock biomass;

- Wet scrubbers to control water-soluble VOC from hydrolysis, fermentation and distillation steps;

- Floating roofs on product storage tanks;

- A Flare to control emissions from product load out;

- Maintaining only small storage piles of supplemental (wood chips, yard waste and harvest residue) to minimize odors;

- Prompt repair of any leaking components (such as heat exchangers) within the cooling towers to minimize contamination of the water by and subsequent stripping of VOC to the atmosphere; and

- As per NSPS 40 CFR 60, Subpart VVa, HEF will implement a LDAR program to minimize VOC emissions from process equipment leaks.  This will address a significant portion of the odor potential.

  - Department’s Review

The Department agrees that the VOC control measures proposed by the applicant at HEF will reduce the generation potential for objectionable odors.  However it is important to reiterate that objectionable odors are actually prohibited.  The relevant rule states:

“No person shall cause, suffer, allow or permit the discharge of air pollutants which cause or contribute to an objectionable odor.  An objectionable odor is defined in Rule 62-210.200(Definitions), F.A.C., as any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance.”

The Department will require that HEF shall submit an odor control plan (OCP) early in the design process that describes procedures to be implemented if objectionable odors occur.  The OCP must be submitted to the Compliance Authority no later than 90 days prior to HEF commencing operation.

- BIOMASS BOILER HEAT INPUT MONITORING

Monitoring of heat input is difficult when using biomass as fuel.  Sugarcane and sweet sorghum bagasse can have high moisture contents (50%) and boiler energy will be expended to evaporate that moisture thus reducing the boiler efficiency.

To accurately calculate heat input, the Department will include in the permit a requirement to conduct a boiler thermal efficiency test in accordance with American Society of Mechanical Engineers (ASME) methods (refer to Appendix ASME of the draft permit).  The boiler heat input rate calculations must then be performed using ASME methods or those provided in 40 CFR 75, Appendix F.  (Refer to Appendix F of the draft permit.)

- air quality analysis

As a part of this review, Rules 62-212.400(7) and 62-212.400(5), F.A.C., require the applicant to perform a current air quality analysis and a source impact analysis and for each PSD applicable pollutant.

The original PSD air construction permit application for this project was approved in September 2011. On March 17, 2017, the applicant applied for an extension of the original permit. During the review process, it was determined that the original permit application did not include estimates of condensable PM as is now required. Therefore, a new PSD application was required for the increase in future potential emissions of PM, PM10, and PM2.5 above the PSD-applicability thresholds. No other estimated project emissions have changed. The new PSD permit application, submitted May 19, 2017, analyzes the project’s estimated future potential emissions of PM, PM10, and PM2.5.  These emission rates are based on the worst-case operating scenario for each pollutant, which exceed the applicable PSD significant emission rates (SER) and are subject to review.

For NO2, SO2, and CO, the Department accepts the ambient analysis as described in the original technical evaluation for this project, from 2011.  This analysis showed no exceedances of any ambient air quality standards or available PSD increments.  However, since the original evaluation, the National Ambient Air Quality Standard (NAAQS) for ozone has been decreased; the evaluation below now accounts for the current NAAQS for ozone.

  - Current Air Quality Analysis

    - State Level

The State of Florida has generally good ambient air quality and is currently in attainment of all NAAQS in the vicinity of this project.  As can be seen in Figure 9, Florida’s air monitor design values are well within attainment of the NAAQS for PM10 and PM2.5.  In addition, air pollutant emissions have seen a significant decrease in the past fifteen years (Figure 10).  Statewide actual annual emissions from stationary sources of PM have decreased 66% since 2000.  These emission decreases have occurred in spite of the increase in the population of Florida of over four million, or nearly 27%, through the same period. A variety of national rules that are currently being implemented are expected to maintain these lower levels or even reduce them further in the foreseeable future.

Figure 9. Florida ambient air monitoring network design values for 2013-2015 for PM10 and PM2.5.  PM10 design values are based on expected exceedances.

Figure 10. Actual annual emissions of PM in Florida from 2000 to 2015.

    - County Level

Highlands County, 2016 population of 100,917, is a rural area, especially near the project site.  The nearest city to the project site is Lake Placid, located 10 km N with a population of approximately 3,000.  The largest cities in the county, Sebring and Avon Park, are located over 30 km N of the project site with populations of approximately 10,000 each.  Table 4 includes emissions of PM from stationary sources in Highlands County in 2006 and 2015.  PM emissions in the county have decreased significantly, even more than the trend in statewide stationary source emissions.

Table 4 - Actual annual emissions of pm by stationary sources in highlands county, florida in 2005 and 2015.

| Pollutant | 2005 Actual Emissions (TPY) | 2015 Actual Emissions (TPY) | Percent Change |
| --- | --- | --- | --- |
| PM | 58.0 | 4.8 | -92% |

    - Nearby Sources

Highlands County contains very few significant stationary sources of air pollutants.  The existing sources within Highlands County are generally very small and outside of population centers, providing for clean ambient air.  Table 5 provides some perspective on the relative size of the project and nearby sources by comparing its maximum potential future emissions of PM with the actual 2015 emissions from the five largest PM sources within 50 km, all of which are over 25 km away from the project site (Figure 11).

Table 5 - ACTUAL 2015 EMISSIONS OF PM FROM THE LARGEST STATIONARY SOURCES NEAR THE PROJECT SITE, COMPARED TO THE MAXIMUM FUTURE POTENTIAL EMISSIONS

| Owner | Facility Name | County | 2015 PM Emissions (TPY) |
| --- | --- | --- | --- |
| Highland EnviroFuels, LLC | This Project | Highlands | 52.2 |
| Turf Care Supply Corp. | TCSC Sebring Plant | Highlands | 3.20 |
| Florida Gas Transmission Company | Compressor Station No. 29 | Highlands | 0.85 |
| Duke Energy Florida, Inc. | Avon Park | Highlands | 0.43 |
| Okeechobee Asphalt & Ready-Mix Concrete | Okeechobee Asphalt/Asphalt Plant | Okeechobee | 0.31 |
| Highlands County Dept. of Solid Waste | Highlands County Dept. of Solid Waste | Highlands | 0.21 |

Figure 11. Reference map for the Highlands Ethanol and Cogen Plant project including the largest sources of air pollutants within 50 km.

    - Monitors

Florida has a robust ambient air monitoring network operated by the Department and its partners (local air pollution control programs).  The network monitors concentrations of each of the criteria pollutants and includes monitors in Florida counties containing 92% of the population.  The representative monitor chosen to evaluate the existing air quality in the area is described in Table 6 and is used to satisfy the preconstruction monitoring requirements for PSD review contained in Rule 62-212.400(7), F.A.C.  This monitor is the nearest monitor that is located in a similar setting to the project site.  Other nearby PM10 and PM2.5 monitors are either on the coast of Florida or are in or near the large urban area of Tampa, and so are not considered representative for the area.  The chosen monitor also provides conservative estimates, because it is located in the city of Lakeland, which is more urbanized than the rural area of the project site.  Design values at this monitor are well below the applicable NAAQS.

Table 6 - CRITERIA POLLUTANT DESIGN VALUES FOR FLORIDA DEP AMBIENT AIR MONITOR CHOSEN TO CONSERVATIVELY CHARACTERTIZE THE PROJECT AREA AS PART OF THE PRECONSTRUCTION MONITORING REQUIREMENT OF PSD REVIEW.

| Pollutant | Location (Site Number) | Averaging Period | Ambient Concentration |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Compliance Period | Value | Standard | Unitsa |
| PM10 | Lakeland, FL | 24-hour | 2015 | 40b | 150c | µg/m3 |
|  | (105-6006) |  |  |  |  |  |
| PM2.5 | Lakeland, FL | 24-hour | 2013 – 2015 | 14 | 35d | µg/m3 |
|  | (105-6006) | Annual | 2013 – 2015 | 6.5 | 12.0e | µg/m3 |
| - Units are in: micrograms per cubic meter (µg/m3) - Exceedance based standard – Second highest 2015 concentration given for comparison. - Not to be exceeded more than once per year on average over a three-year period. - Three-year average of the annual 98th percentile, daily 24-hour average concentrations. - Three-year average of the arithmetic annual means. |  |  |  |  |  |  |

  - Source Impact Analysis

A source impact analysis is required by Rule 62-212.400(5), F.A.C. to demonstrate that allowable emission increases from the proposed project will not cause or contribute to a violation of any NAAQS or PSD increment as defined in 40 CFR Part 50 and 40 CFR 52.21(c) respectively.  This analysis is performed using approved air quality models and analysis techniques as described in Appendix W (Guideline on Air Quality Models) of 40 CFR 51.

    - Dispersion Modeling Approach

Dispersion modeling for the source impact analysis typically occurs in six steps:

- Class II SIL Analysis: Initial modeling is performed to determine if the maximum predicted concentrations due to the new source(s) alone are likely to cause a significant impact on ambient air quality.  Modeling is performed using five years of actual meteorological data and the highest resultant concentrations are compared to the EPA suggested SILs for each pollutant that is subject to PSD review.  For each pollutant that is less than the SIL, steps two and three are skipped.  For all others, refined NAAQS and Class II increment analyses are required.

- NAAQS Analysis: Cumulative source modeling is performed for each pollutant and averaging time that exceeded the Class II SIL.  This analysis includes modeled emissions from all nearby sources that are considered to have a significant impact and a non-modeled background concentration intended to represent all other sources of pollutants.  The resulting concentrations are evaluated on a receptor-by-receptor basis for comparison to each NAAQS using the following methods:

- PM2.5 24-Hour Average: 5-year average of the yearly 8th-high 24-hour average concentration

- PM2.5 Annual Average: 5-year average of the annual mean

- PM10 24-Hour Average: 6th-high 24-hour concentration over five years

- Class II Increment Analysis: Cumulative source modeling is performed with nearby PSD increment consuming or expanding sources.  For annual averaging periods, the highest five-year annual average is compared to the increment.  For all other short-term averaging periods, the 2nd-highest concentration from each of five years is compared.

- Class I SIL Analysis: A Class I analysis is typically required if a source is within 200 km of a Federal Class I area. Almost all of Florida is within this distance of at least one Class I area and therefore an analysis is always required.  This analysis is identical to the Class II SIL analysis except that the SILs are smaller and only evaluated within the boundaries of the Class I area.

- Class I Increment Analysis: For those pollutants that exceed the applicable Class I SIL, an increment analysis is required.  Again this analysis mirrors the Class II increment analysis except with smaller increments that are only evaluated within the Class I area.

- Class I AQRV Visibility and Deposition Analysis: A visibility and deposition analysis is required for any Class I area that does not pass a specific screening criteria.  This analysis is typically performed with CALPUFF.

    - Models

The AERMOD (AMS (American Meteorological Society)/EPA Regulatory Model) modeling system is a near-field, Gaussian, steady-state plume dispersion model that simulates pollutant dispersion methods based on planetary boundary layer turbulence structure and scaling concepts, including the treatment of both surface and elevated sources, and both simple and complex terrain.  The system is comprised of the AERMET meteorological processor, the AERMAP terrain processor, and the actual AERMOD model.  AERMOD was commissioned by EPA for regulatory use and was developed by AERMIC (AMS/EPA Regulatory Model Improvement Committee) from 1991 to 2005 when EPA officially promulgated it as the preferred regulatory model.  Between 2005 and 2016 the program has undergone 12 major updates. It is the recommended model for assessing air quality impacts up to 50 km from the source.

    - Class II SIL Analysis

The general modeling approach for the SIL, NAAQS, and PSD increment analyses followed current EPA and DEP modeling guidance.  The applicant used a series of specific model features recommended by EPA that are referred to as the regulatory options and the latest version of each model component available at the time of the analysis.  It should be noted that ambient concentrations of modeled pollutants in the area near the project site are significantly below the applicable NAAQS for each and therefore use of SILs in this case satisfies Section 165(a)(3) of the CAA.  The applicant has chosen to use more recent SIL values for PM2.5 developed by EPA, which EPA believes is sufficient to conclude whether the proposed project will cause or contribute to any violation of the PM2.5 NAAQS.

      - Meteorological Data

The AERMET v.16216 meteorological input used with the AERMOD v.16216R model consisted of a concurrent 5-year period of hourly surface-weather observations from the National Weather Service (NWS) Automated Surface Observing System (ASOS) station at Punta Gorda Airport (PGD) and upper air sounding (RAOB) data from Tampa International Airport (TBW).  This data was compiled by DEP for the period 2012 – 2016 and included land cover and land use parameters derived from the 1992 National Land Cover Database (NLCD) by AERSURFACE v.13016 and 1-minute ASOS wind data extracted by AERMINUTE v.11059 with a minimum wind speed threshold of 0.5 meters per second (m/s).  The ASOS station at PGD is located approximately 72 km WSW of the project site and is the closest primary weather station.  Table 7 summarizes the annual average land use parameters for the project site and the ASOS location.  These parameters were derived seasonally and for twelve 30-degree wind direction sectors.  Given the similarity of the land surrounding both sites, the ASOS data are considered to be representative of the project site.

Table 7 - ANNUAL AVERAGE LAND USE PARAMETER COMPARISON BETWEEN THE PGD ASOS STATION AND THE PROJECT SITE.

| Location | Albedo | Bowen Ratio | Surface Roughness |
| --- | --- | --- | --- |
| PGD ASOS Station | 0.16 | 0.45 | 0.057 |
| Highlands Project Site | 0.16 | 0.47 | 0.188 |

      - Building Downwash

Building downwash effects were simulated for 11 future structures at the facility.  For each stack, direction-specific building heights and maximum projected widths were calculated by the Building Profile Input Program (BPIP v.04274) incorporating the Plume Rise Model Enhancement (PRIME) algorithm developed by the Electric Power Research Institute (EPRI).  This wind direction-specific information was then output to AERMOD which simulates aerodynamic downwash based on stack and building locations and heights.

      - Receptors and Terrain

A combination of fence line, near-field, and far-field receptors was chosen for predicting maximum concentrations in the vicinity of the project for comparison to the Class II SILs.  Receptor locations used in the modeling analysis were based on Universal Transverse Mercator (UTM) coordinates from Zone 17 North, North American Datum 1983 (NAD83).  The modeling domain was set as a 14 km X 14 km grid centered at UTM 17N east and north coordinates of 466,380 and 3,008,958 meters, respectively.  A discrete Cartesian grid of 4,669 receptors was located at the following intervals and distances:

- 50 m spacing along the property boundary and fence line;

- 100 m spacing from the fence line to 2,000 m from the domain origin;

- 250 m spacing from 2,000 m to 7,000 m from the domain origin.

This receptor placement is considered to be sufficient to resolve the areas of highest concentration in Florida’s flat terrain.

Base elevations were extracted from the US Geological Survey’s (USGS) 1-second National Elevation Dataset (NED) by AERMOD’s terrain processor AERMAP v.11103 for all receptors and sources.

      - Onsite Modeled Sources

The SIL analysis evaluates whether the potential emissions from the new project alone are capable of significantly contributing to a modeled NAAQS exceedance.  Table 8 summarizes the emission factors for each onsite modeled source.  Worst-case scenario conditions were assumed for all sources.

The boiler unit is the largest source of PM in the project.  The boiler is intended to run on 100% bagasse fuel as the normal operating mode.  However, the boiler will also be permitted to run on bagasse and up to 10% wood fuel, or bagasse and up to 30% natural gas fuel.  The maximum short-term emission rate across all potential fuel combinations was calculated to determine the maximum short-term emission rate to use in the modeling.  The worst-case emissions scenario for the boiler unit is running on 100% bagasse fuel.

PM emissions from the cooling tower are based on a drift rate of 0.001 percent and total dissolved solids concentration of 500 ppm, reflecting typical values for freshwater in the vicinity of the site.  PM emissions for the materials storage silos are based on maximum estimated material loading times and rates for each silo.  PM emissions for the truck/rail loading rack flare are based on AP-42 emission factors for industrial flares.

The worst-case emissions scenario for fugitive PM emissions is the use and handling of bagasse fuel and 10% wood fuel.  Fugitive PM emissions were estimated for sources of material handling, including conveyer belts and storage piles; wind erosion of storage piles; and truck traffic on paved roads related to deliveries, load outs, and storage pile maintenance.  Fugitive PM emissions were estimated using EPA’s AP-42 emission factors.

Table 8 - Onsite Modeled Sources

| Source | Type | PM10 |  | PM2.5 |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Annual (TPY) | 24-hour (lb/hr) | Annual (TPY) | 24-hour (lb/hr) | Area source size (ft2) |
| Bagasse boiler | Point | 49.76 | 11.92 | 40.09 | 9.51 |  |
| Cooling tower | Point | 0.19 | 0.043 | 0.19 | 0.043 |  |
| Flare | Point | 0.052 | 0.034 | 0.052 | 0.034 |  |
| Ash silo | Point | 0.847 | 0.21 | 0.847 | 0.21 |  |
| Lime silo 1 | Point | 0.002 | 0.21 | 0.002 | 0.21 |  |
| Lime silo 2 | Point | 0.00042 | 0.21 | 0.00042 | 0.21 |  |
| Biomass materials handling | Area | 0.047 | 0.051 | 0.0071 | 0.0077 | 32,500 |
| Biomass pile wind erosion | Area | 0.11 | 0.29 | 0.11 | 0.29 | 100,000 |
| Biomass pile vehicular maintenance | Area | 1.39 | 0.45 | 0.14 | 0.046 | 100,000 |
| Biomass truck traffic | Line | 0.29 | 0.067 | 0.072 | 0.017 |  |
| Other truck traffic | Line | 0.011 | 0.0027 | 0.0028 | 6.67E-04 |  |

      - Results

The results of the SIL modeling summarized in Table 9 indicate that refined cumulative source modeling is required for 24-hour and annual average PM10 and PM2.5 impacts to demonstrate compliance with the NAAQS.

Table 9 - MAXIMUM PREDICTED AIR QUALITY IMPACTS FOR THE PROJECT, COMPARED TO THE CLASS II SILS.

| Pollutant | Averaging Time | Max Impact (μg/m3) | SIL (μg/m3) | Percent of SIL | Significant Impact? |
| --- | --- | --- | --- | --- | --- |
| PM2.5 | Annual 24-Hour | 0.51 7.1 | 0.2 1.2 | 255% 592% | Yes Yes |
| PM10 | Annual | 1.7 | 1 | 170% | Yes |
|  | 24-Hour | 13.7 | 5 | 274% | Yes |

    - Cumulative Dispersion Modeling

Cumulative source modeling that evaluates whether the combined air quality impacts from all nearby significant sources will comply with the NAAQS and increment for each pollutant is performed for each pollutant that exceeds the SIL.  In order to assess cumulative impacts, the potential emission from the most significant nearby sources are added to the modeling platform developed for the SIL analysis.  A monitored background concentration intended to represent all non-modeled anthropogenic and natural pollutant sources is added to the results which are then compared to the NAAQS and increment.

      - Significant Impact Area

Receptor placement and the choice of which sources to explicitly model are based on the establishment of a significant impact area (SIA).  The SIA is the area in which the proposed project has the potential to significantly contribute to a NAAQS exceedance, i.e. a circular area with a radius equal to the distance from the source to the most distant receptor with a modeled SIL violation.  The radius of the SIA for the SIL analysis for this project was estimated to be 2.5 km.  The analysis evaluated receptors within the SIA.

      - Background Source Choices

Background source emission data were obtained from the DEP ARMS database, DEP permit files, and recent PSD permit reviews.  EPA recommends that the list of explicitly modeled sources should remain small and that professional judgment should be used in the decision process.  In order to evaluate sources in the screening area that could significantly interact with the project, the applicant evaluated facilities within 50 km of the project site using the North Carolina screening technique (also known as the “20D approach”). Based on this technique, facilities whose annual emissions (i.e., TPY) are less than the threshold quantity, Q, are eliminated from the modeling analysis since they are not likely to significantly interact with the project. Q is equal to 20 × (D - SIA), where D is the distance in km from the facility to the Project site. Based on the results of the facility screening, no additional background sources were identified for inclusion in the NAAQS and PSD Class II increment analyses.

      - Background Development and Monitors

The background concentration is based on monitoring data and is designed to take into account all existing natural or anthropogenic sources that are not explicitly modeled.  There are a variety of ways to develop a background concentration that differ in complexity and conservatism.  For this project, the least complex, most conservative method was utilized.  The background concentrations added to the model results were simply the design values for the nearest PM10 and PM2.5 monitor (see Table 6).

      - Results

The results of the NAAQS analysis that are summarized in Table 10 indicate that the project is not expected to cause or significantly contribute to an exceedance of the NAAQS.

Table 10 - CUMULATIVE MODELING RESULTS FOR THE PROJECT COMPARED TO THE NAAQS.

| Pollutant and Averaging Time | Maximum Concentration (μg/m3) |  |  | NAAQS (µg/m3) | Percent of NAAQS |
| --- | --- | --- | --- | --- | --- |
|  | Sources | Background | Total |  |  |
| PM2.5 Annual | 0.5 | 6.5 | 7.0 | 12 | 58% |
| PM2.5 24-hour | 4.7 | 14.0 | 18.7 | 35 | 25% |
| PM10 24-hour | 11.2 | 40.0 | 51.2 | 150 | 34% |

      - Class II Increment Analysis

PSD increment analyses are necessary for the 24-hour and annual average PM2.5 and PM10 impacts for this project. The PSD increment represents the limit above an established baseline concentration that new sources may increase the local ambient ground level concentrations of a pollutant (without exceeding the NAAQS). PSD increment modeling is similar to NAAQS modeling in that it is a cumulative analysis that takes into account the impact from nearby increment consuming and expanding sources, except that a background concentration is not added. An increment consuming source is any source that has increased actual emissions since the established baseline date for a pollutant while increment expanding sources are any sources with a decrease in actual emissions. The baseline date for PM2.5 and PM10 is October 20, 2010. There are no increment-affecting sources near the project site. Five years were modeled individually using AERMOD, including all the same modeling parameters from the SIL analysis and the highest annual average and highest, second-high 24-hour average concentrations were then compared to the increments. The results shown in Table 11 indicate that no exceedance of an allowable PSD Class II increment is expected for this project.

Table 11 - CUMULATIVE MODELING RESULTS FOR THE PROJECT COMPARED TO THE CLASS II PSD INCREMENTS.

| Pollutant and Averaging Time | Maximum Concentration (µg/m3) | PSD Increment (µg/m3) | Percent of Increment |
| --- | --- | --- | --- |
| PM2.5 Annual | 0.6 | 4 | 15% |
| PM2.5 24-hour | 6.8 | 9 | 76% |
| PM10 Annual | 1.7 | 17 | 10% |
| PM10 24-hour | 11.5 | 30 | 38% |

    - Class I Analysis

All areas not explicitly designated as Class I in 40 CFR 81 Subpart D (such as national parks and wilderness areas) are considered Class II areas.  While the NAAQS apply to all areas equally, more stringent SILs and increments exist for Class I areas.  A Class I analysis is required for any project that may affect a Federal Class I area.  The Class I areas closest to the project site are Everglades National Park (ENP), 147 km to the southeast and Chassahowitzka National Wilderness Area (CNWA), 188 km to the northwest (Figure 12).  There are no other Class I areas within 350 km of the site.

Figure 12. Map of Federal Class I areas near the project site.

      - Class I SIL analysis

A screening analysis was performed using AERMOD to evaluate the annual and 24-hour PM2.5 and PM10 SILs.  AERMOD was run using a ring of receptors located 50 km from the project site and space at 1 degree intervals.  The results in Table 12 show that the maximum impacts are below all SILs; therefore, a cumulative Class I increment analysis is not required.

Table 12 - MAXIMUM PREDICTED AIR QUALITY IMPACTS 50 KM FROM THE PROJECT SITE COMPARED TO THE CLASS I SIL.

| Pollutant | Averaging Time | Max Impact (μg/m3) | SIL (μg/m3) | Percent of SIL | Significant Impact? |
| --- | --- | --- | --- | --- | --- |
| PM2.5 | Annual | 0.0037 | 0.05 | 7.4% | No |
|  | 24-Hour | 0.037 | 0.27 | 13.7% | No |
| PM10 | Annual | 0.0055 | 0.2 | 2.8% | No |
|  | 24-Hour | 0.07 | 0.3 | 23.3% | No |

    - Ozone Analysis

The Department is updating the ozone analysis in this evaluation to account for the current NAAQS for ozone, which decreased since the original evaluation.  Projects with VOC or NOX potential emissions increases of 40 TPY or greater are required to perform a source impact analysis for ozone. The applicant estimated maximum annual potential NOX and VOC emissions from the project to be 194.2 TPY and 136.6 TPY, respectively, and is therefore required to provide an analysis for ozone; however, ozone site-specific modeling is not typically completed for single source permitting because of its complexity involving computationally intensive models such as the Community Model for Air Quality (CMAQ) and the Weather Research and Forecasting Model (WRF).

Ozone is a secondarily formed pollutant that is known to be caused by the regional emissions of VOC and NOX in combination with certain meteorological conditions (temperature, humidity, solar insolation, etc.). Ambient ozone levels in Highlands County, as inferred from a monitor located approximately 2 km south of the project site (60 ppb), are well within attainment of the recently promulgated 70 ppb 2015 ozone NAAQS. As shown in Figure 13, actual emissions of the ozone precursors NOX and VOC have declined dramatically over the past ten years despite significant increases in population. These reductions are far greater than the increase in NOX and VOC emissions from this project. Ambient levels of ozone have also decreased over the last 15 years (Figure 14) due to improvements in motor vehicle emissions rates and the implementation of national rules such as the Clean Air Interstate Rule (CAIR), and continued reductions in both average motor vehicle fleet emissions and stationary source emissions are expected to further improve ozone air quality.

For these reasons, DEP has reasonable assurance that the project will not significantly contribute to or cause any violation of the ozone NAAQS.

Figure 13.  Annual emissions of NOX and VOC from stationary sources (actual) and mobile sources (estimated from MOVES2014a) in Florida from 2000 to 2015.

Figure 14. Florida monitored ambient ozone concentration trend 2001-2016.

  - Additional Impacts Analysis

The applicant is required by Rule 62-212.400(8), F.A.C. to provide an analysis of the project’s potential impacts on visibility, soils, vegetation, and wildlife due to the proposed project or any general commercial residential, or industrial growth associated with the project.

    - Growth

The 12-18 month construction phase of this project will require approximately 500 to 1,000 workers during that time, with many workers commuting to the site. Once construction is complete, about 60 permanent personnel will remain. This is a small fraction of the population in the area and no air quality impacts are expected from the small increase in vehicular traffic.  Operation of the facility is not expected to result in any commercial or industrial growth in the area because existing commercial and industrial infrastructure is more than sufficient to meet the needs of the facility.

    - Soils, Vegetation, and Wildlife

Emissions of pollutants have the potential to negatively affect soils, vegetation and wildlife near sources.  The project’s maximum predicted air quality impacts are less than the NAAQS which were established to protect both public health and welfare.  In addition, secondary NAAQS have been set to protect against visibility impairment and damage to animals, crops, vegetation, and buildings.  All ambient air quality impacts from the project have been predicted to remain well below the applicable secondary NAAQS and therefore the impact on soils, vegetation, and wildlife is expected to be negligible.

    - Class I AQRV

The Federal Land Manager (FLM) for every Class I area that may be affected by a source is charged with protecting all air quality related values (AQRV), including visibility and deposition, in that area.  An AQRV analysis is generally required for all PSD projects and the applicant completed such an analysis for this project.

An initial screening analysis was performed following FLAG 2010 guidance to determine if there could be any significant impacts in Class I areas.  The analysis calculates the Q/D ratio, where Q is potential project emissions in TPY of SO2, NO2, particulate matter, and sulfuric acid mist, and D is the distance in kilometers to the Class I area.  For sources with a Q/D ratio of 10 or less, no further AQRV analysis is required.  To be conservative, the AQRV screening analysis for the project takes into account the NOX, SO2, and sulfuric acid mist (SAM) emissions from the original application in addition to the updated PM10 emissions from the new application.  As seen in Table 13, Class I AQRV impact analyses are not required for this project.

Table 13 - AQRV Analysis Screening Results

| Potential Emissions Increase based on Maximum Allowable Emissions (TPY) |  |  |  |  | Class I Area | Minimum Distance in km (D) | FLAG Screening Ratio Q/D | AQRV Analysis Required? |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| NOx | SO2 | SAM | PM10 | Total (Q) |  |  |  |  |
| 552.3 | 309.2 | 15.2 | 54.4 | 931.1 | Chassahowitzka | 188 | 4.9 | No |
|  |  |  |  |  | Everglades | 147 | 6.3 | No |

  - Conclusion

Based on the results presented in the air quality impact analysis, the Department has reasonable assurance that the increased pollutant emissions associated with the project will not cause or significantly contribute to any violation of a NAAQS or PSD increment; in addition, the Department finds that there will be no adverse impact on soils, vegetation, wildlife, or AQRVs in Class I areas.

- Preliminary Determination

The Department makes a preliminary determination that the proposed project will comply with all applicable state and federal air pollution regulations as conditioned by the Draft Permit.  This determination is based on a technical review of the complete application, reasonable assurances provided by the applicant, and the conditions specified in the Draft Permit.  John Dawson is the project engineer responsible for reviewing the application and drafting the permit changes.  Ashley Kung is the meteorologist responsible for reviewing and approving the ambient air quality analyses.  Additional details of this analysis may be obtained by contacting the project engineer at the Department’s Office of Permitting and Compliance at Mail Station #5505, 2600 Blair Stone Road, Tallahassee, Florida  32399-2400 at 850-717-9085 or by email John.Dawson@dep.state.fl.us.

Application available in Oculus.  (Choose “PUBLIC OCULUS LOGIN.”)

The Technical Evaluation and Preliminary Determination is included in the original Draft Permit package.  The original Final Permit is also available on the Department’s website.

Request for Additional Information and applicant’s response available in Oculus.  (Choose “PUBLIC OCULUS LOGIN.”)

Technical Evaluation and Preliminary Determination for Permit No. 0530380-010-AC/PSD-FL-090G

Seinfeld, J.H, and S.N. Pandis, Atmospheric Chemistry and Physics:  From Air Pollution to Climate Change, Second Edition, Wiley, 2006, p. 22.

Interagency Monitoring of Protected Visual Environments

http://www.ipcc.ch/meetings/session25/doc4a4b/vol4.pdf

https://yosemite.epa.gov/sab/sabproduct.nsf/0/3235DAC747C16FE985257DA90053F252/$File/Framework-for-Assessing-Biogenic-CO2-Emissions+(Nov+2014).pdf

Roberts‐Ashby, T.L., Brennan, S.T., Merrill, M.D., Blondes, M.S., Freeman, P.A., Cahan, S.M., DeVera, C.A., and Lohr, C.D.,

2015, Geologic framework for the national assessment of carbon dioxide storage resources—South Florida Basin, chap. L

of Warwick, P.D., and Corum, M.D., eds., Geologic framework for the national assessment of carbon dioxide storage resources: U.S. Geological Survey Open‐File Report 2012-1024-L.  Available at http://pubs.usgs.gov/of/2012/1024/l/ofr20121024l.pdf.

The Technical Evaluation and Preliminary Determination is included in the original Draft Permit package.

U.S. EPA’s Draft “Guidance on Significant Impact Levels for Ozone and Fine Particles in the Prevention of Significant Deterioration Permitting Program,” August 18, 2016.