- PERMITTEE

Ronald Nazaro

Terminal Manager

Motiva Enterprises, LLC

6500 West Commerce St.

Tampa, FL 33616

- Permitting Authority

Environmental Protection Commission of Hillsborough County

3629 Queen Palm Dr.

##### Tampa, Florida 33619

- PROJECT

Air Permit No. 0570197-024-AC

Minor Air Construction Permit

Motiva Enterprises, LLC

This permit authorizes the construction of a fourth loading lane on the truck loading rack.  In addition, this permit removes the facility-wide VOC emissions limitation from the permit conditions.  The fourth loading lane, which is expected to have four gasoline loading arms and one diesel loading arm, will be constructed in order to allow the facility to load more trucks at one time.  However, Motiva is not requesting an increase in the annual throughput of the loading rack.  The throughput will continue to be limited to 695,053,000 gallons of petroleum products per any twelve consecutive month period.

- NOTICE AND PUBLICATION

The EPCHC distributed a draft minor air construction permit package on May 11, 2016.  The applicant published the Public Notice in the Tampa Bay Times on May 14, 2016.  The EPCHC received the proof of publication on May 19, 2016.  No requests for administrative hearings or requests for extensions of time to file a petition for administrative hearing were received.

COMMENTS

No comments on the Draft Permit were received from the public or the applicant.

- CONCLUSION

The final action of the Department is to issue the permit with the minor changes, corrections and clarifications as drafted.

Permittee

| Motiva Enterprises, LLC 6500 West Commerce St. Tampa, FL 33616 Authorized Representative: Ronald Nazaro, Terminal Manager | Air Permit No. 0570197-024-AC Permit Expires: December 1, 2017 Air Construction Permit Addition a Fourth Truck Loading Lane on the Truck Loading Rack |
| --- | --- |

Project

This air construction permit authorizes the construction of a fourth truck loading lane on the truck loading rack.  In addition, this permit removes the facility-wide VOC emissions limitation from the permit conditions.  The proposed work will be conducted at the existing facility, which is a bulk gasoline terminal categorized under Standard Industrial Classification No. 5171 – Petroleum Bulk Stations and Terminals.  The existing facility is located in Hillsborough County at 6500 West Commerce St., Tampa, FL 33616.  The UTM coordinates of the existing facility are Zone 17, 348.03 km East, and 3082.41 km North.

This permit is organized into the following sections:  Section 1 (General Information); Section 2 (Administrative Requirements); Section 3 (Emissions Unit Specific Conditions); and Section 4 (Appendices).  Because of the technical nature of the project, the permit contains numerous acronyms and abbreviations, which are defined in Appendix A of Section 4 of this permit.

Statement of Basis

This air pollution construction permit is issued under the provisions of:  Chapter 403 of the Florida Statutes (F.S.) and Chapters 62-4, 62-204, 62-210, 62-212, 62-296 and 62-297 of the Florida Administrative Code (F.A.C.).  The permittee is authorized to conduct the proposed work in accordance with the conditions of this permit.  This project is subject to the general preconstruction review requirements in Rule 62-212.300, F.A.C. and is not subject to the preconstruction review requirements for major stationary sources in Rule 62-212.400, F.A.C. for the Prevention of Significant Deterioration (PSD) of Air Quality.

Executed in Tampa, Florida.

ENVIRONMENTAL PROTECTION

COMMISSION OF HILLSBOROUGH COUNTY

_________________________________

Janet L. Dougherty

Executive Director

CERTIFICATE OF SERVICE

The undersigned duly designated deputy agency clerk hereby certifies that this Notice of Final Permit (including the Final Permit and Final Determination) was sent by electronic mail, or a link to these documents made available electronically on a publicly accessible server, with received receipt requested, or was sent via mail, before the close of business on the date indicated below to the following persons.

Ronald Nazaro – Motiva Enterprises, LLC ron.nazaro@motivaent.com

Michael Waller, P.E. – Ashworth Leininger Group mwaller@algcorp.com

Thomas Jackson - Motiva Enterprises, LLC thomas.jackson@motivaent.com

# FILING AND ACKNOWLEDGMENT FILED, on this date, pursuant to Section 120.52(7), Florida Statutes, with the designated agency clerk, receipt of which is hereby acknowledged.

___________________________  _____________

Clerk	Date

Facility Description

Motiva’s Bulk Gasoline Terminal consists of 1) twenty petroleum liquid storage tanks for storage and handling of gasoline, ethanol, ethanol-gasoline blends, jet kerosene, diesel, other distillate products, and additives; and 2) a truck loading rack with three existing loading lanes. VOC emissions from the truck loading rack are primarily controlled by a John Zink VRU.  The backup control device is a John Zink Company VCU, Model # ZCT-2-8-35-2-316-X.  Emissions may also be controlled by a Portable VCU.

The existing facility consists of the following emission units.

| EU No. | ## Brief Description |
| --- | --- |
| Regulated Emissions Units |  |
| 002 | Loading Rack with Vapor Recovery Unit (VRU), Vapor Combustion Unit (VCU), and Portable VCU |
| 008 | Gasoline Storage Tanks: #3, #7, #8, #9, #10, #11, #12 |
| 009 | Distillate Storage Tanks: #2, #15 |
| 010 | Contact Water Tanks: #18, #23, #28, Oil/Water Separator |
| 011 | Miscellaneous Tanks, Additive: #13, #19, #20, #21, #22, # 24, #25 |
| 012 | Diesel Fuel Emergency Generator |

PROPOSED PROJECT

This permit authorizes the construction of a fourth loading lane on the truck loading rack.  In addition, this permit removes the facility-wide VOC emissions limitation from the permit conditions, as described below.  There are no changes to the throughput limit or to the facility’s VOC potential emissions.

The fourth loading lane, which is expected to have four gasoline loading arms and one diesel loading arm, will be constructed in order to allow the facility to load more trucks at one time.  However, Motiva is not requesting an increase in the annual throughput of the loading rack.  The throughput will continue to be limited to 695,053,000 gallons of petroleum products per any twelve consecutive month period.

In addition, this permit removes the facility-wide VOC PTE limit from the permit conditions.  The existing Title V Permit No. 0570197-023-AV includes a specific condition that lists the facility-wide VOC PTE of 154.4 TPY.  This specific condition was originally established in Permit No. 0570197-021-AC to summarize the potential emissions of the facility.  The condition was not included in the permit for the purpose of ensuring the facility remained below the VOC PSD source threshold of 250 TPY. Since the potential emissions limitation was established in a construction permit, a construction permit is required to remove the limitation, which is being done by this permit.

This project will modify the following emissions unit.

| EU No. | ## Brief Description |
| --- | --- |
| Regulated Emissions Units |  |
| 002 | Loading Rack with Vapor Recovery Unit (VRU), Vapor Combustion Unit (VCU), and Portable VCU |

Facility Regulatory Classification

- The facility is not a major source of hazardous air pollutants (HAP).

- The facility does not operate units subject to the acid rain provisions of the Clean Air Act (CAA).

- The facility is a Title V major source of air pollution in accordance with Chapter 62-213, F.A.C.

- The facility is not a major stationary source in accordance with Rule 62-212.400(PSD), F.A.C.

References Permit Nos.: 0570197-009-AC, 0570197-014-AC, 0570197-019-AC, 0570197-021-AC

Replace Permit No.:  NA

- Permitting Authority:  The permitting authority for this project is the Environmental Protection Commission of Hillsborough County. The mailing address is 3629 Queen Palm Dr., Tampa, Florida 33619.  All documents related to applications for permits to operate an emissions unit shall be submitted to the Environmental Protection Commission of Hillsborough County.

- Compliance Authority:  All documents related to compliance activities such as reports, tests, and notifications shall be submitted to the Environmental Protection Commission of Hillsborough County at:  3629 Queen Palm Dr., Tampa, Florida 33619.

- Appendices:  The following Appendices are attached as a part of this permit:  Appendix A (Citation Formats and Glossary of Common Terms); Appendix B (General Conditions); Appendix C (Common Conditions); and Appendix D (Common Testing Requirements).

- As requested by the permittee, in order to limit the potential to emit for both criteria and Hazardous Air Pollutants (HAP), the following potential emission limitations shall apply for any 12 consecutive month period:  [Rules 62-210.200 and 62-4.070(3), F.A.C., Permit No. 0570197-021-AC]

- The hazardous air pollutant (HAP), as defined in Rule 62-210.200, F.A.C., emissions shall be less than 10 tons in any 12 consecutive month period for any individual HAP, and less than 25 tons in any 12 consecutive month period for any combination of HAPs.

- The permittee shall not handle gasoline oxygenated using MTBE.

- Applicable Regulations, Forms and Application Procedures:  Unless otherwise specified in this permit, the construction and operation of the subject emissions units shall be in accordance with the capacities and specifications stated in the application.  The facility is subject to all applicable provisions of: Chapter 403, F.S.; and Chapters 62-4, 62-204, 62-210, 62-212, 62-213, 62-296 and 62-297, F.A.C.  Issuance of this permit does not relieve the permittee from compliance with any applicable federal, state, or local permitting or regulations.

- New or Additional Conditions:  For good cause shown and after notice and an administrative hearing, if requested, the EPCHC may require the permittee to conform to new or additional conditions.  The EPCHC shall allow the permittee a reasonable time to conform to the new or additional conditions, and on application of the permittee, the EPCHC may grant additional time.  [Rule 62-4.080, F.A.C.]

- Modifications:  The permittee shall notify the Compliance Authority upon commencement of construction.  No new emissions unit shall be constructed and no existing emissions unit shall be modified without obtaining an air construction permit from the EPCHC.  Such permit shall be obtained prior to beginning construction or modification.  [Rules 62-210.300(1) and 62-212.300(1)(a), F.A.C.]

- Not federally Enforceable.  Objectionable Odor Prohibited.  No person shall cause, suffer, allow or permit the discharge of air pollutants, which cause or contribute to an objectionable odor.  An “objectionable odor” means any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance.  [Rule 62-296.320(2) and 62-210.200(Definitions), F.A.C.; and EPCHC Rule 1-3.22(3)]

- General Visible Emissions. No person shall cause, let, permit, suffer or allow to be discharged into the atmosphere the emissions of air pollutants from any activity equal to or greater than 20% opacity.  Emissions from the following types of activities in Hillsborough County are further subject to a general 5% opacity standard:  loading or unloading of materials to or from containers such as rail cars, trucks, ships, storage structures and stockpiles; permanent conveyor systems; storage of materials in structures such as silos or enclosed bins, which have a storage capacity of fifty cubic yards or more; crushing, grinding, sizing and screening operations; and, static drop transfer points.  These regulations do not impose a specific testing requirement.  [Rules 62-296.320(4)(b)1, F.A.C. and Rule 1-3.52, HCEPC. [Rule 62-296.320(4)(b)1. & 4., F.A.C.]

- Prevention of Accidental Releases (Section 112(r) of CAA).  If and when the facility becomes subject to 112(r), the permittee shall: [40 CFR 68]

- Submit its Risk Management Plan (RMP) to the Chemical Emergency Preparedness and Prevention Office (CEPPO) RMP Reporting Center.  Any Risk Management Plans, original submittals, revisions or updates to submittals, should be sent to:  RMP Reporting Center, Post Office Box 10162, Fairfax, VA  22038, Telephone:  (703) 227-7650.

- Submit to the permitting authority Title V certification forms or a compliance schedule in accordance with Rule 62-213.440(2), F.A.C.

- General Pollutant Emission Limiting Standards. Volatile Organic Compounds (VOC) Emissions or Organic Solvents (OS) Emissions.  The permittee shall allow no person to store, pump, handle, process, load, unload or use in any process or installation, volatile organic compounds (VOC) or organic solvents (OS) without applying known and existing vapor emission control devices or systems deemed necessary and ordered by the Department or its delegated agent, the Environmental Protection Commission of Hillsborough County. [Rule 62-296.320(1), F.A.C.]

- Maintaining tightly fitting covers, lids, etc., on all containers when they are not being handled, tapped, etc.

- Where possible and practical, procuring/fabricating a tightly fitting cover for any open trough, basin, etc., of VOC so that it can be covered when not in use.

- Immediately attending to all spills/waste as appropriate.

- Emissions of Unconfined Particulate Matter.  Pursuant to Rules 62-296.320(4)(c)1., 3. & 4., F.A.C., reasonable precautions to prevent emissions of unconfined particulate matter at this facility include the following requirements: [Rule 62-296.320(4)(c), F.A.C.]

- Maintenance of parking areas and yards.

- Removal of particulate matter from paved areas, building, and work areas under the control of the owner/operator.

- Reduce vehicular speed.  Post limits, if necessary.

- When the Environmental Protection Commission of Hillsborough County (EPC) after investigation, has good reason (such as complaints, increased visible emissions or questionable maintenance of control equipment) to believe that any applicable requirement or permit condition is being violated, it may require the owner or operator of the source to conduct compliance tests which identify the nature and quantity of pollutant emissions from the source and to provide a report on the results of said tests to the Environmental Protection Commission of Hillsborough County. [Rules 62-297.310(7)(b) and 62-4.070(3), F.A.C.]

- At least 15 days prior to the date on which each required emissions test is to begin, the owner or operator shall notify the EPC, unless shorter notice is agreed to by the EPC. The notification shall include the date, time, place of each such test, Facility ID Number, Emission Unit ID Number(s) and description(s), Emission Point Number(s) and description(s), test method(s), pollutant(s) to be tested, along with the name and telephone number of the person who will be responsible for conducting such test(s) for the owner or operator. If a scheduled emissions test needs to be re-scheduled, the owner or operator shall submit to the EPC a revised notification at least seven days prior to the re-scheduled emissions test date or arrange a re-scheduled test date with the EPC by mutual agreement.  [Rule 62-297.310(9), F.A.C.]

- Construction and Expiration:  The expiration date shown on the first page of this permit provides time to complete the physical construction activities authorized by this permit, complete any necessary compliance testing, and obtain an operation permit.  Notwithstanding this expiration date, all specific emissions limitations and operating requirements established by this permit shall remain in effect until the facility or emissions unit is permanently shut down.  For good cause, the permittee may request that that a permit be extended.  Pursuant to Rule 62-4.080(3), F.A.C., such a request shall be submitted to the Permitting Authority in writing before the permit expires.  [Rules 62-4.070(4), 62-4.080 & 62-210.300(1), F.A.C.]

- Electronic Annual Operating Report and Title V Annual Emissions Fees.  The information required by the Annual Operating Report for Air Pollutant Emitting Facility [Including Title V Source Emissions Fee Calculation] (DEP Form No. 62-210.900(5)) shall be submitted by April 1 of each year, for the previous calendar year, to the Department of Environmental Protection’s (DEP) Division of Air Resource Management.  Each Title V source shall submit the annual operating report using the DEP’s Electronic Annual Operating Report (EAOR) software, unless the Title V source claims a technical or financial hardship by submitting DEP Form No. 62-210.900(5) to the DEP Division of Air Resource Management instead of using the reporting software.  Emissions shall be computed in accordance with the provisions of subsection 62-210.370(2), F.A.C.  Each Title V source must pay between January 15 and April 1 of each year an annual emissions fee in an amount determined as set forth in subsection 62-213.205(1), F.A.C.  The annual fee shall only apply to those regulated pollutants, except carbon monoxide and greenhouse gases, for which an allowable numeric emission-limiting standard is specified in the source’s most recent construction permit or operation permit.  Upon completing the required EAOR entries, the EAOR Title V Fee Invoice can be printed by the source showing which of the reported emissions are subject to the fee and the total Title V Annual Emissions Fee that is due.  The submission of the annual Title V emissions fee payment is also due (postmarked) by April 1st of each year.  A copy of the system-generated EAOR Title V Annual Emissions Fee Invoice and the indicated total fee shall be submitted to:  Major Air Pollution Source Annual Emissions Fee, Post Office Box 3070, Tallahassee, Florida 32315-3070.  Additional information is available by accessing the Title V Annual Emissions Fee On-line Information Center at the following Internet web site:

http://www.dep.state.fl.us/air/emission/tvfee.htm.  [Rules 62-210.370(3), 62-210.900 & 62-213.205, F.A.C.; and, §403.0872(11), Florida Statutes (2013)]

{Permitting Note:  Resources to help you complete your AOR are available on the electronic AOR (EAOR) website at:  http://www.dep.state.fl.us/air/emission/eaor.  If you have questions or need assistance after reviewing the information posted on the EAOR website, please contact the Department by phone at (850) 717-9000 or email at eaor@dep.state.fl.us.}

{Permitting Note:  The Title V Annual Emissions Fee form (DEP Form No. 62-213.900(1)) has been repealed.  A separate Annual Emissions Fee form is no longer required to be submitted by March 1st each year.}

- Monitoring Reports.  The permittee shall submit reports of any required monitoring at least every six (6) months.  All instances of deviations from permit requirements must be clearly identified in such reports.  [Rule 62-213.440(1)(b)3.a., F.A.C.]

- All applicable rules of the Environmental Protection Commission of Hillsborough County including design discharge limitations specified in the application shall be adhered to.  The permit holder may also need to comply with county, municipal, federal, or other state regulations prior to construction.  [Rule 62-4.070(7), F.A.C.]

- The use of property, facilities, equipment, processes, products, or compounds, or the commission of paint overspraying or any other act, that causes or materially contributes to a public nuisance is prohibited.  [Hillsborough County Environmental Protection Act, Section 16, Chapter 84-446, Laws of Florida, as Amended.]

- If the permittee wishes to transfer this permit to another owner, an "Application for Transfer of Air Permit" (DEP Form 62-210.900(7)) shall be submitted, in duplicate, to the Environmental Protection Commission of Hillsborough County within 30 days after the sale or legal transfer of the permitted facility.  [Rule 62-4.120, F.A.C.]

- Annual Statement of Compliance.  The permittee shall submit an annual statement of compliance to the compliance authority at the address shown on the cover of this permit and to the US. EPA at the address shown below within 60 days after the end of each calendar year during which the Title V air operation permit was effective.  [Rules 62-213.440(3)(a)2. & 3. and (b), F.A.C.]

U.S. Environmental Protection Agency, Region 4

Atlanta Federal Center

61 Forsyth Street, SW

Atlanta, Georgia  30303

Attn:  Air Enforcement Branch

- Application for a Title V Operating Permit:  This permit authorizes construction of the permitted emissions unit(s) and initial operation to determine compliance with Department rules.  A Title V air operation permit is required for regular operation of the permitted emissions unit.  The permittee shall apply for a Title V air operation permit at least 90 days prior to expiration of this permit, but no later than 60 days after completion of compliance testing.  To apply for a Title V operation permit, the applicant shall submit the appropriate application form and such additional information as the Department may by law require.  The application shall be submitted to the Environmental Protection Commission of Hillsborough County.  [Rules 62-4.030 and 62-4.050, F.A.C.]

This section of the permit addresses the following emissions unit.

| EU ID No. 002 | Loading Rack with VRU, VCU, and Portable VCU |
| --- | --- |

Equipment

- Equipment:  The permittee is authorized to construct a fourth truck loading lane at the truck loading rack.  [Rule 62-4.070(3), F.A.C. and Permit Application Received April 21, 2016]

Performance Restrictions

- Permitted Capacity.  The maximum annual throughput of petroleum products shall not exceed 695,053,000 gallons per any twelve consecutive month period.  [Rules 62-4.160(2) and 62-210.200(PTE), F.A.C.; and Permit No. 0570197-014-AC]

- Methods of Operation.  All vapors displaced during product loading into the tanker trucks shall be routed to the VRU, the VCU, or the Portable VCU.  The VRU shall operate as the primary control device and the VCU and Portable VCU should be used as a backup units as necessary.  The vapor collection system, the VRU, the VCU, and the Portable VCU shall be maintained in good working order.  All loading and vapor lines equipped with fittings shall be vapor tight.  The permittee shall ensure that a means is provided to prevent liquid waste from the loading device to exceed the quantity specified for the self sealing coupler or adapter according to API regulation RP 1004 (or equivalent) upon the loading device being disconnected or when it is not in use. [Rule 62-213.410 and 62-296.510(4), F.A.C., 40 CFR 60.502(a), and Permit Nos. 0570197-014-AC, -019-AC, and -021-AC]

- Hours of Operation.  The hours of operation for this emission unit are not restricted.  [Rule 62-210.200(PTE), F.A.C., and Permit No. 0570197-014-AC]

##### Emissions Standards

- The maximum allowable VOC emissions from the loading rack shall not exceed 10 milligrams per liter of gasoline loaded into tanker trucks.  [Rules 62-212.300 and 62-296.510(2), F.A.C., 40 CFR 60.502(b) and (c), and Permit No. 0570197-009-AC]

- The maximum potential VOC emissions for the truck loading rack shall not exceed 66.7 tons per any twelve consecutive month period.  [Rule 62-4.070(3), F.A.C. and Permit No. 0570197-009-AC]

- The permittee shall comply with the following requirements of 40 CFR Subpart XX - Standards of Performance for Bulk Gasoline Terminals:  [40 CFR 60.500 and Rule 62-204.800, F.A.C.]

- Each vapor collection system shall be designed to prevent any total organic compounds vapors collected at one loading rack from passing to another loading rack. [40 CFR 60.502(d)]

- Loading of liquid product into gasoline tank trucks shall be limited to vapor-tight gasoline tank trucks using the following procedures:  [40 CFR 60.502(e) and Rule 62-4.070(3), F.A.C.]

- The permittee shall obtain the vapor tightness documentation described in 40 CFR 60.505(b) (Specific Condition No. A.18) for each gasoline tank truck which is to be loaded at the affected facility.

- The permittee shall require the tank identification number to be recorded as each gasoline tank truck is loaded at the affected facility.

- The permittee shall cross-check each tank identification number obtained in paragraph (2) above with the file of tank vapor tightness documentation within 2 weeks after the corresponding tank is loaded.

- The permittee shall notify the owner or operator of each nonvapor-tight gasoline tank truck loaded at the affected facility within 1 week of the documentation cross-check in paragraph (3) above.

- The permittee shall take steps assuring that the nonvapor-tight gasoline tank truck will not be reloaded at the affected facility until vapor tightness documentation for that tank is obtained.

- In order to comply with paragraphs 3. and 5. above, the permittee is allowed to use a terminal automation system to cross-check and lock out trucks with expired vapor tightness documentation.

- The permittee shall act to assure that the loadings of gasoline tank trucks are made only into tanks equipped with vapor collection equipment that is compatible with facility's vapor collection system.

[40 CFR 60.502(f)]

- The permittee shall act to assure that the facility’s and tank truck’s vapor collection systems are connected during each loading of a gasoline tank truck.  Examples of actions to accomplish this include training drivers in hookup procedures and posting visible reminder signs at the loading rack.  [40 CFR 60.502(g)]

- The vapor collection and liquid loading equipment shall be designed and operated to prevent gauge pressure in the delivery tank from exceeding 4500 pascal (450 mm of water) during product loading when measured by the procedure specified in 40 CFR 60.503(d) (Specific Condition No. A.13).   The pressure shall be monitored and recorded daily.  If the pressure exceeds 4500 pascal (450 mm of water) then it shall be considered an exceedance.  In the event of an exceedance, the facility shall immediately shut down the VRU and divert the collected vapors to the VCU or Portable VCU, or cease loading product.  Notify the Environmental Protection Commission of Hillsborough County within 24 hours of the problem.   The unit shall not be operated until the problem is corrected and a written explanation and the corrective actions implemented shall be submitted in the semi-annual monitoring report required in Specific Condition No. A.9.  [40 CFR 60.502(h) and Rule 62-4.070(3), F.A.C.]

- No pressure vacuum vent in the bulk petroleum products terminal’s vapor collection system shall begin to open at a system pressure less than 4500 pascal (450 mm of water).  [40 CFR 60.502(i)]

- Each calendar month, the vapor collection system, the vapor processing system, and each loading rack handling gasoline shall be inspected during the loading of gasoline tank trucks for total organic compounds liquid or vapor leaks.  For purpose of this paragraph, detection methods incorporating sight, sound, or smell are acceptable.  Each detection of a leak shall be recorded and the source of the leak repaired within 15 calendar days after it is detected.  [40 CFR 60.502(j)]

- In addition to the requirements of Specific Condition No. A.7., the following limitations shall apply to the Portable VCU:  [Rule 62-4.070(3), F.A.C.]

  - The Portable VCU shall be equipped with a device to monitor the presence of a pilot flame.

  - If the pilot flame presence is not detected, all vapors shall be automatically routed to the VRU or VCU, as long as it is fully functional, or the loading operation shall be automatically shutdown.

- Excess Emissions.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown, or malfunction shall be prohibited.  No trucks shall be hooked up for filling once the equipment or process failure is recognized.  Truck loading shall restart only after the malfunction is completely resolved. The permittee shall notify the Environmental Protection Commission of Hillsborough County within twenty-four (24) hours of any malfunction, reporting the problem and the duration of excess emissions.  The permittee shall include all excess emissions over the past six (6) months in the semi-annual monitoring report, as required by Specific Condition No. FW17, and submit the reports to the Environmental Protection Commission of Hillsborough County. [Rules 62-210.700 and 62-213.440(1)(b)3.b., F.A.C.]

Test Methods and Procedures

- Test Methods and Required Compliance Tests.  Test the loading rack for VOC emissions as follows within 60 days of completion of construction of the fourth loading lane.  All four loading lanes shall be in operation during each test. [Rule 62-4.070(3), F.A.C.]

  - Test the loading rack while the VRU is in operation.

  - Test the loading rack while the VCU is in operation.  If the Portable VCU is needed to be in operation in conjunction with the VCU, then both VCUs are required to be tested.

- Compliance with Specific Condition Nos. A.5., A.6., A.7., and A.10 shall be determined using EPA Methods 2, 2A, 2B, 2C, or 2D as appropriate, 21, 25A or 25B, and 27 as contained in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-297, F.A.C. as listed below.  Two copies of the test data shall be submitted to the Air Management Division of the Environmental Protection Commission of Hillsborough County office within 45 days of such testing. Testing shall be conducted while loading a typical mix of products.  Failure to submit the gasoline throughput rate and the pressure drop and temperature across the Vapor Processing Unit or operating at conditions during testing which do not reflect actual operating conditions may invalidate the data.  [Rules 62-4.070(3), 62-296.510(4), 62-297.310 and 62-297.440, F.A.C.; 40 CFR 63 – Subpart BBBBBB (Table 3) and 40 CFR 63.8; and Permit No. 0570197-021-AC]

- Pre-Testing Requirements.  Immediately before the performance test required to determine compliance with 40 CFR 60.502(b), (c), and (h) (Specific Condition Nos. A.5., and A.7.), the permittee shall use EPA Method 21 to monitor for leakage of vapor from all potential sources in the terminal's vapor collection system equipment while a gasoline tank truck is being loaded. The permittee shall repair all leaks with readings of 10,000 ppm (as methane) or greater before conducting the performance test.  [40 CFR 60.503(b) and Rule 62-296.510(4), F.A.C.]

- Testing Requirements.  The permittee shall determine compliance with the standards in 40 CFR 60.502(b), (c) (Specific Condition Nos. A.5. and A.6.) and Rule 62-297.440, F.A.C. as follows:

- The performance test shall be at least 6 hours long during which at least 302,800 liters (80,000 gallons) of gasoline is loaded.  If this is not possible, the test may be continued the same day until 302,800 liters of gasoline is loaded or the test may be resumed the next day with another complete 6-hour period.  In the latter case, the 302,800-liter criterion need not be met.  However, as much as possible, testing should be conducted during the 6-hour period in which the highest throughput normally occurs. [40 CFR 60.503(c)(1) and Rule 62-297.440(2)(b), F.A.C.]

- The emission rate (E) of total organic compounds shall be computed using the following equation:

[40 CFR 60.503(c)(3)]

n

E = K     (Vesi Cei)/(L 106)

i=1

where:

E    =	 emission rate of total organic compounds, mg/liter of gasoline loaded.

Vesi =	volume of air-vapor mixture exhausted at each interval "i", scm

Cei  =	concentration of total organic compounds at each interval "i", ppm

L    =	total volume of gasoline loaded, liters

n    =	number of testing intervals

i    =	emission testing interval of 5 minutes

K    =	density of calibration gas, 1.83 x 106 for propane and 2.41 x 106 for butane, mg/scm

- The performance test for the vapor collection system shall be conducted in intervals of 5 minutes.  For each interval "i", readings from each measurement shall be recorded, and the volume exhausted (Vesi) and the corresponding average total organic compound concentration (Cei) shall be determined.  The sampling system response time shall be considered in determining the average total organic compounds concentration corresponding to the volume exhausted.  [40 CFR 60.503(c)(4)]

- The following methods shall be used to determine the volume (Vesi) air-vapor mixture exhausted at each interval: [40 CFR 60.503(c)(5)]

- Method 2B shall be used for the VCU and the Portable VCU.

- Method 2A shall be used for the VRU.

- Method 25A or 25B shall be used for determining the total organic compounds concentration (Cei) at each interval. The calibration gas shall be either propane or butane. The permittee may exclude the methane and ethane content in the exhaust vent by any method (e.g., Method 18) approved by the Administrator. [40 CFR 60.503(c)(6)]

- To determine the volume (L) of gasoline dispensed during the test period at all loading racks whose vapor emissions are controlled by the processing system being tested, terminal records or readings from gasoline dispensing meters at each loading rack shall be used.  [40 CFR 60.503(c)(7)]

- The permittee shall determine compliance with the standard in 40 CFR 60.502(h) (Specific Condition No.  A.7.E.) as follows:   [40 CFR 60.503(d)(1)&(2)]

- A pressure measurement device (liquid manometer, magnehelic gauge or equivalent instrument), capable of measuring 500 mm of water gauge pressure with ± 2.5 mm of water precision, shall be calibrated and installed on the terminal’s vapor collection system at a  pressure tap located as close as possible to the connection with the gasoline tank truck.

- During the performance test as required in Specific Condition No. A.12, the pressure shall be recorded every 5 minutes while a gasoline truck is being loaded; the highest instantaneous pressure that occurs during each loading shall also be recorded.  Every loading position must be tested at least once during the performance test.

- Test Methods: Required tests shall be performed in accordance with the following reference methods.

| Method | Description of Method and Comments |
| --- | --- |
| 1 | Sample and Velocity Traverses for Stationary Sources |
| 1a | Sample and Velocity Traverses for Stationary Sources With Small Stacks or Ducts |
| 2 | Determination of Stack Gas Velocity and Volumetric Flow Rate (Type S Pitot Tube) |
| 2A | Direct measurement of gas volume through pipes and small ducts |
| 2B | Determination of exhaust gas volume flow rate from gasoline vapor incinerators |
| 2C | Determination of gas velocity and volumetric flow rate in small stacks or ducts (standard pitot tube) |
| 2D | Measurement of gas volume flow rates in small pipes and ducts |
| 21 | Determination of volatile organic compound leaks |
| 25A | Method for Determining Gaseous Organic Concentrations (Flame Ionization) |
| 25B | Determination of total gaseous organic concentration using a nondispersive infrared analyzer |
| 27 | Determination of vapor tightness of gasoline delivery tank using pressure-vacuum test |

The above methods are described in Appendix A of 40 CFR 60 and are adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the EPCHC.  [Rules 62-204.800, F.A.C.; and Appendix A of 40 CFR 60]

Monitoring Requirements

- CAM Plan.  This emissions unit is subject to the Compliance Assurance Monitoring (CAM) requirements specified in Permit No. 0570197-023-AV.  Failure to adhere to the monitoring requirements specified does not necessarily indicate an exceedance of a specific emissions limitation; however, it may constitute good reason to require compliance testing pursuant to Rule 62-297.310(7)(b), F.A.C. [40 CFR 64; and Rules 62-204.800 and 62-213.440(1)(b)1.a., F.A.C.]

- Monitoring Requirements.  In order to demonstrate compliance with 40 CFR 63 – Subpart BBBBBB, the permittee shall install, operate, and maintain a continuous emission monitoring system (CEMS) on the outlet of the VRU.  The CEMS shall be operated in accordance with the manufacturer’s specifications and be used to demonstrate compliance with the VOC emission limitation from Specific Condition No. A.5. by developing an equivalent hydrocarbon concentration to be monitored following each stack test performed on the VRU.  The vapor processing system shall be operated in a manner not to exceed this equivalent hydrocarbon concentration.  The monitored operating parameter shall be re-established and reported with each annual VOC compliance stack test report.  The CEMS shall be operated and maintained in accordance with 40 CFR 63 – Subpart A, as applicable, based on 40 CFR 63 – Subpart BBBBBB.   [Rule 62-4.070(3), F.A.C.; 40 CFR 63.8 and 40 CFR 63.11092; and Permit No. 0570197-021-AC]

- The loading rack and control system (EU 002) are subject to the NESHAP for Gasoline Distribution Bulk Terminals, Bulk Plants, Pipeline Facilities and Gasoline Dispensing Facilities, 40 CFR 63, Subpart BBBBBB (Gasoline Distribution Bulk Terminals, Bulk Plants, Pipeline Facilities and Gasoline Dispensing Facilities).  The permittee shall comply with all applicable requirements from that rule. [Rule 62-4.070(3), F.A.C., 40 CFR 63.11081, and Permit No. 0570197-021-AC]

- The permittee shall comply with 40 CFR Part 63, Subpart A - General Provisions. [Rule 62-204.800(10)(d), F.A.C. and Permit No. 0570197-021-AC]

Records and Reports

- Records of the monitored data from the CEMS shall be collected and compiled in a data acquisition system and made available to the EPC, state, and federal air pollution agencies upon request.  The records shall be maintained for a minimum of 5 years.  [Rules 62-4.070(3) and 62-213.440(1)(b)2., F.A.C.; 40 CFR 63 – Subpart BBBBBB (Table 3) and 40 CFR 63.10; and Permit No. 0570197-021-AC]

- The tank truck vapor tightness documentation required in 40 CFR 60.502(e)(1) (Specific Condition No. A.7.) shall be kept on file in a permanent form available for inspection.  The documentation file for each gasoline tank truck shall be updated at least once per year to reflect current test results as determined by EPA Method 27.  This documentation shall include, as a minimum, the following information:  [40 CFR 60.505(a)&(b)]

- Test Title:  Gasoline Delivery Tank Pressure Test - EPA reference Method 27.

- Tank owner and address.

- Tank identification number.

- Test location.

- Date of test.

- Tester name and signature.

- Witnessing inspector, if any:  Name, signature and affiliation.

- Test Results:  Actual pressure change in 5 minutes, mm of water (average for 2 runs)

- A record of each monthly leak inspection required under 40 CFR 60.502(j) (Specific Condition No. A.7.) shall be kept on file at the terminal for at least 5 years. Inspection records shall include, as a minimum, the following information:  [40 CFR 60.505(c) and Rule 62-213.440, F.A.C.]

- Date of inspection.

- Findings (may indicate no leaks discovered; or location, nature, and severity of each leak).

- Leak determination method.

- Corrective action (date each leak repaired; reasons for repair interval in excess of 15 days)

- Inspector name and signature.

- The permittee shall keep documentation of all notifications required by 40 CFR 60.502(e)(4) (Specific Condition No. A.7.) on file at the facility for at least five (5) years.  [40 CFR 60.505(d) and Rule 62-213.440, F.A.C.]

- The permittee shall keep records of all replacements or additions of components performed on an existing vapor processing system for at least five years.  [40 CFR 60.505(f) and Rule 62-213.440, F.A.C.]

- The permittee shall maintain a monthly recordkeeping system as follows in order to ensure compliance with Specific Condition Nos. A.2 and A.6., and maintain the records for a minimum of 5 years.  The records shall be made available upon request to the Environmental Protection Commission of Hillsborough County, state, or federal air pollution agency for inspection.  The records shall include, but not limited to, the following:  [Rules 62-4.070(3) and 62-213.440(1)(b)2., F.A.C.; and Permit Nos. 0570197-009-AC, 014-AC, and 021-AC]

- Month, Year

- Products Loaded

- Product Throughput (gallons)

- Most recent twelve month rolling totals for item C) above

- Twelve month rolling total of VOC and HAP emissions

- The hours of operation of the VCU

- The hours of operation of each Portable VCU that is brought onsite.

- The make and model number of each Portable VCU brought onsite.

- Rolling twelve month total of F) and G)