TECHNICAL EVALUATION

&

PRELIMINARY DETERMINATION

APPLICANT

Cutrale Citrus Juices USA, Inc.

11 Cloud Street

Leesburg, Florida 34748

Cutrale Citrus Juices USA, Inc. - Leesburg

Facility ID No. 0690002

PROJECT

Project No. 0690002-019-AC

Application for Air Construction Permit for Title V Facility

Revisions to Best Management Practices for Carbon Monoxide (CO)

COUNTY

Lake County, Florida

PERMITTING AUTHORITY

Florida Department of Environmental Protection

Permitting and Waste Cleanup Program

Central District Office

Orlando, Florida 32803-3767

February 6, 2018

- General Project INFORMATION

Air Pollution Regulations

Projects at stationary sources with the potential to emit air pollution are subject to the applicable environmental laws specified in Section 403 of the Florida Statutes (F.S.).  The statutes authorize the Department of Environmental Protection (Department) to establish regulations regarding air quality as part of the Florida Administrative Code (F.A.C.), which includes the following applicable chapters:  62-4 (Permits); 62-204 (Air Pollution Control – General Provisions); 62-210 (Stationary Sources – General Requirements); 62-212 (Stationary Sources – Preconstruction Review); 62-213 (Operation Permits for Major Sources of Air Pollution); 62-296 (Stationary Sources - Emission Standards); and 62-297 (Stationary Sources – Emissions Monitoring).  Specifically, air construction permits are required pursuant to Chapters 62-4, 62-210 and 62-212, F.A.C.

In addition, the U. S. Environmental Protection Agency (EPA) establishes air quality regulations in Title 40 of the Code of Federal Regulations (CFR).  Part 60 specifies New Source Performance Standards (NSPS) for numerous industrial categories.  Part 61 specifies National Emission Standards for Hazardous Air Pollutants (NESHAP) based on specific pollutants.  Part 63 specifies NESHAP based on the Maximum Achievable Control Technology (MACT) for numerous industrial categories.  The Department adopts these federal regulations in Rule 62-204.800, F.A.C.

Glossary of Common Terms

Because of the technical nature of the project, the permit contains numerous acronyms and abbreviations, which are defined in Appendix A of this permit.

Facility Description and Location

Cutrale Citrus Juices USA, Inc. - Leesburg is a citrus processing plant categorized under Standard Industrial Classification No. 2037. The existing facility is located in Lake County at 11 Cloud Street, Leesburg, Florida.  The UTM coordinates are Zone 17, 415.5 kilometers (km) East, and 3187.3 km North.  This site is in an area that is in attainment (or designated as unclassifiable) for all air pollutants subject to Ambient Air Quality Standards (AAQS).

Facility Regulatory Categories

- The existing facility is a prevention of significant deterioration (PSD) major source of air pollutants in accordance with Rule 62-212.400, F.A.C.; therefore, the facility is a major stationary source in accordance with Rule 62-212.400(PSD), F.A.C.

- The facility is not a major source of hazardous air pollutants (HAP).

- The facility does not operate units subject to the acid rain provisions of the Clean Air Act (CAA).

- The facility is a Title V major source of air pollution in accordance with Chapter 62-213, F.A.C.  The facility is classified as a Title V facility for Carbon Monoxide (CO), Volatile Organic Compounds (VOC), and Nitrogen Oxides (NOx).

PROPOSED PROJECT

This project revises conditions authorized in Construction Permit No. 0690002-012-AC (PSD FL 366) for the facility’s peel dryer, combustion turbine, and process boilers.  Specifically, the Best Management Practices for Carbon Monoxide are revised and simplified to correspond to units burning natural gas only.  An incorrect reference to the burning of No. 2 fuel oil for Boiler #4 was removed from the Statement of Basis also.  The only equipment allowed to burn No. 2 fuel oil at the facility are the emergency generators.

- Processing Schedule

December 19, 2017	Received the application for a minor source air pollution construction permit.

December 27, 2017 	Received additional information; Application complete.

- PSD Applicability

The project is located in Lake County which is in an area that is currently in attainment with the AAQS or is otherwise designated as unclassifiable.  The facility is a PSD major source; however, the proposed project will not increase emissions for any PSD pollutant; therefore, this project is not subject to a PSD preconstruction review.

3.	Department review

- List of Emissions Units

| EU No. | ## Brief Description |
| --- | --- |
| Regulated Emissions Units |  |
| 005 | Citrus Peel Dryer |
| 006 | Pellet Cooling Reel |
| 004 | Process Steam Boiler #4 |
| 008 | Relocatable Boiler |
| 009 | New Cogeneration System Turbine & Existing Steam Generator |
| 010 | Feed Mill Emergency Generator |
| 011 | Cogeneration System Emergency Generator |

- Summary of Emissions

This project only revises/simplifies the Best Management Practices for Carbon Monoxide for the facility’s peel dryer (EU No. 005), Process Steam Boiler No. 4 and Relocatable Boiler (EU Nos. 004 & 008), and New Cogeneration System Turbine & Existing Steam Generator (EU No 009).  Potential and Allowable emissions will not be affected because of this project.

As provided by the applicant, emissions from the facility operations are expected to remain below the following values:

| Pollutant | Potential Emissions Tons per Year (tpy) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | EU 004 – Boiler No. 4 | EU 005- Citrus Peel Dryer | EU 006- Pellet Cooling Reel | EU 008 – Relocatable Boiler | EU 009 – New Cogeneration System Turbine & Existing Steam Generator | EU 010 – Feed Mill Emergency Generator | EU 011 – Cogeneration System Emergency Generator | Total Facility-Wide Potential Emissions (tpy) |
| CO | 28.14 | 1438.57 | - | 34.63 | 58.55 | 0.48 | 0.90 | 1561.3 |
| NOx | 33.49 | 54.11 | - | 13.19 | 68.19 | 0.55 | 4.15 | 173.7 |
| PM | 2.55 | 65.70 | 21.90 | 3.13 | 5.07 | 0.03 | 0.29 | 98.7 |
| SO2 | 0.20 | 0.23 | - | 0.25 | 16.73 | 0.06 | 0.10 | 17.6 |
| VOC | 1.84 | 774.10 | 78.55 | 2.27 | 2.94 | 0.55 | 0.33 | 860.6 |
| Total HAPs | 0.63 | 0.73 | - | 0.78 | 1.09 | 2.22E-03 | 3.56E-03 | 3.2 |
| Individual HAPs | 0.60 | 0.70 | - | 0.78 | 0.97 | 6.92E-04 | 1.11E-03 | 3.0 |

- State Requirements and Federal Regulations

This project is subject to the preconstruction review requirements of Chapter 403, Florida Statutes and Chapters 62-204 through 62-297, Florida Administrative Code (F.A.C.), as indicated below.

| Subject to: | Y/N | Comments |
| --- | --- | --- |
| Rule 62-210.300, F.A.C. – Permits Required | Y | subject to general permitting requirements |
| Rule 62-212.400, F.A.C. - Prevention of Significant Deterioration | N | facility is a PSD major source but this project does not trigger PSD review |
| Rule 62-296.320(4), F.A.C. - General Particulate Emission Limiting Standards | Y | operations could be a source of unconfined particulate matter emissions |
| Rules 62-296.320(1) and (2), F.A.C. - General Pollutant Emission Limiting Standards (VOCs and Odor) | Y | The facility is a source of VOC |
| Rule 62-296.401-418, F.A.C. - Stationary Source Emission Standards | N | EU Nos. 004, 008 & 009 are subject to 62-296.406, F.A.C. |
| Rule 62-296.500, F.A.C. - Reasonably Available Control Technology (VOC) | N | Lake County is not an air quality maintenance area for ozone |
| Rule 62-296.700, F.A.C. - Reasonably Available Control Technology (PM) | N | there is no applicable source category |
| Rule 62-204.800, F.A.C. - Standards of Performance for New Stationary Sources (NSPS) | N | EU No. 004 and 008 are subject to 40 CFR 60, Subpart Dc. EU No. 009 is subject to 40 CFR 60, Subpart KKKK |
| Rule 62-204.800, F.A.C. National Emission Standard for Hazardous Air Pollutants (NESHAPS – 40 CFR 61) | N | there is no applicable source category |
| Rule 62-204.800, F.A.C. National Emission Standard for Hazardous Air Pollutants for Source Categories a.k.a. MACT (NESHAPS –40 CFR 63) | N | there is no applicable source category |
| Chapter 62-213, F.A.C. - Operation Permits for Major Sources of Air Pollution | Y | facility is a Title V source |
| Rule 62-297.310, F.A.C. - General Compliance Test Requirements, F.A.C. | N | The boilers, peel dryer and combustion turbine have VE and PM testing requirements; however, this project only changes specific conditions in previous construction permit and therefore does not require any additional compliance testing. |

- Preliminary Determination

The Department makes a preliminary determination that the proposed project will comply with all applicable state and federal air pollution regulations as conditioned by the draft permit.  This determination is based on a technical review of the complete application, reasonable assurances provided by the applicant, and the conditions specified in the draft permit.  No air quality modeling analysis is required because the project does not result in a significant increase in emissions.  Mr. Jeff Rustin, P.E., is the project engineer responsible for reviewing the application and drafting the permit.  Additional details of this analysis may be obtained by contacting the project engineer at the Department’s Central District Office, 3319 Maguire Boulevard, Suite 232, Orlando, FL 32803-3767, phone (407) 897-2930, or by email jeff.rustin@dep.state.fl.us.