### TECHNICAL EVALUATION

&

PRELIMINARY DETERMINATION

#### APPLICANT

Shady Hills Energy Center, LLC

901 Main Avenue

Norwalk, Connecticut 06851

ARMS Facility ID No. 1010524

#### PROJECT

# Draft Permit No. PSD-FL-444

# Project No. 1010524-001-AC

Shady Hills Combined Cycle Facility

#### COUNTY

Pasco County, Florida

PERMITTING AUTHORITY

Florida Department of Environmental Protection

Division of Air Resource Management

Office of Permitting and Compliance

2600 Blair Stone Road, MS#5505

Tallahassee, Florida  32399-2400

May 29, 2018

- General Project INFORMATION

  - SHGS Facility Description and Location

The Shady Hills Generating Station (SHGS) is owned and operated by Shady Hills Power Company, LLC.  The SHGS consists of three, dual-fuel, nominal 170-megawatt (MW) General Electric (GE 7FA) combustion turbine-electric generators operating in simple-cycle peaking and intermittent-duty mode, one 10 million British thermal units per hour (MMBtu/hour) natural gas-fired process heater, one 1,341 horsepower (hp) diesel-fired emergency generator, one 222 hp diesel-fired fire pump engine, and one 2.8-million-gallon fuel oil storage tank.  The facility was also previously authorized to install two additional simple cycle combustion turbines, identified as emissions unit Nos. 005 and 006, through Permit No. 1010373-007-AC.  However, emissions unit Nos. 005 and 006 are no longer planned for construction.  The SHGS is authorized to operate under Title V Air Operating Permit No. 1010373-018-AV.  A natural gas Florida Gas Transmission (FGT) lateral to the plant provides natural gas to the existing electrical generating units that are connected to a 230-kV transmission facility.

The facility is categorized under Standard Industrial Classification Code No. 4911.  The existing Shady Hills Generating Station is in Pasco County at 14240 Merchant Energy Way, Shady Hills, Florida.  The UTM coordinates of the existing facility are Zone 17, 347.2 kilometers (km) East, and 3,138.8 km North.  This site is in an area that is in attainment (or designated as unclassifiable) for all air pollutants subject to Ambient Air Quality Standards (AAQS).

Figure 1 shows the location of Pasco County, while the location of the SHGS is shown Figure 2.

Pasco County

Figure 1.  Location of Pasco County, Florida. 	Figure 2.  Location of SHGS (Facility ID. 1010373).

  - Primary Regulatory Categories

- The facility is not a major source of hazardous air pollutants (HAP).

- The facility operates units subject to the acid rain provisions of the Clean Air Act (CAA).

- The facility is a Title V major source of air pollution in accordance with Chapter 62-213, Florida Administrative Code (F.A.C.)

- The facility is a major stationary source in accordance with Rule 62-212.400, F.A.C. for the Prevention of Significant Deterioration (PSD) of Air Quality.

- The facility operates units subject the New Source Performance Standards (NSPS) of Title 40 Code of Federal Regulations (CFR) Part 60.

- The facility operates units subject the National Emission Standards for Hazardous Air Pollutants (NESHAP) 40 CFR Part 63.

  - Project Description

Shady Hills Energy Center, LLC (SHEC) submitted an application for an air construction permit subject to the preconstruction review requirements of the PSD of Air Quality pursuant to Rule 62-212.400, F.A.C.  The purpose of this project is to construct a new 1-on-1 combined cycle plant, which will be known as the Shady Hills Combined Cycle Facility (SHCCF).  The new combined cycle combustion turbine and associated equipment will be constructed on a 14-acre parcel east of the existing SHGS power island, as outlined in red in Figure 3 below.

Figure 3.  Aerial View of the Certified Site Boundary for the Shady Hills Combined Cycle Facility.

- The following new emissions units (see Table 1) will be added by this project.

Table 1 - NEW EMISSIONS UNITS ADDED BY THIS PROJECT.

| - EU No. | - SHCCF Emission Unit Descriptions |
| --- | --- |
| - 001 | - GE 7HA.02 Combustion Turbine and HRSG with duct firing |
| - 002 | - Auxiliary Boiler |
| - 003 | - One Nominal 1,500 kW Emergency Diesel Generator |
| - 004 | - One Nominal 347-hp Emergency Fire Pump Engine |
| - 005 | - Mechanical Draft Cooling Tower |
| - 006 | - Two Circuit Breakers |

The generating capacity of a combined cycle plant is affected by ambient temperatures, which generally causes the overall fuel consumption to increase at lower ambient temperatures.  The proposed combustion turbine generator (CTG) and steam turbine generator will have a net capacity of approximately 573 MW (winter rating) operating at an ambient air temperature of 59°F with evaporative cooling and duct firing.  The heat recovery steam generator (HRSG) will have duct firing with a heat input rate of approximately 210 MMBtu/hour.  The CTG will use only natural gas as fuel.  Natural gas will be transported to the SHCCF by the existing pipeline connection to the FGT lateral.  The Project will be connected to a new natural gas metering yard.  The proposed auxiliary boiler will be used during start up and shutdown and when steam is not available from the HRSG.  An electric natural gas heater (not an emission point) will be used during operation to heat natural gas.

  - Processing Schedule

2/16/2018	Department received the application for an air pollution construction permit.

5/11/2018	Department issued draft permit package.

5/21/2018	Applicant requested new facility identification number for ease of separation.

5/29/2018	Department reissued draft permit package with the new facility identification number.

- Applicable Regulations

  - State Regulations

Projects at stationary sources with the potential to emit air pollution are subject to the applicable environmental laws specified in Section 403 of the Florida Statutes (F.S.).  The statutes authorize the Department of Environmental Protection (Department) to establish air quality regulations as part of the Florida Administrative Code (F.A.C.), which includes the applicable chapters contained in Table 2.

Table 2.  Applicable Rules from the F.A.C.

| Chapter | - Description |
| --- | --- |
| 62-4 | Permits |
| 62-17 | Electrical Power Plant Siting |
| 62-204 | Air Pollution Control – General Provisions |
| 62-210 | Stationary Sources of Air Pollution – General Requirements |
| 62-212 | Stationary Sources – Preconstruction Review |
| 62-213 | Operation Permits for Major Sources (Title V) of Air Pollution |
| 62-214 | Acid Rain Program Requirements |
| 62-296 | Stationary Sources – Emission Standards |
| 62-297 | Stationary Sources – Emissions Monitoring |

  - Federal Regulations

- The Environmental Protection Agency (EPA) establishes air quality regulations in Title 40 of the Code of Federal Regulations (CFR).  Part 60 identifies New Source Performance Standards (NSPS) for a variety of industrial activities.  Part 61 specifies National Emissions Standards for Hazardous Air Pollutant (NESHAP) based on specific pollutants.  Part 63 specifies NESHAP provisions based on the Maximum Achievable Control Technology (MACT) for given source categories.  Federal regulations are adopted in Rule 62-204.800, F.A.C.  Additional details of the applicable federal regulations are provided in Section 3 of this report.

- PSD Applicability Review

  - General PSD Applicability

The Department regulates major stationary sources in accordance with Florida’s PSD program pursuant to Rule 62-212.400, F.A.C.  PSD preconstruction review is required in areas that are currently in attainment with the state and federal ambient air quality standards (AAQS) or areas designated as “unclassifiable” for these regulated pollutants.  Commonly addressed PSD pollutants in the power industry include: carbon monoxide (CO), nitrogen oxides (NOX), particulate matter (PM), PM with a mean diameter of 10 microns or less (PM10), PM with a mean diameter of 2.5 microns or less (PM2.5), sulfur dioxide (SO2), volatile organic compounds (VOC), lead (Pb), fluorides (F), sulfuric acid mist (SAM), and mercury (Hg).

Additional PSD pollutants that are more common to certain other industries include: hydrogen sulfide (H2S), total reduced sulfur (TRS) including H2S, reduced sulfur compounds (RSC) including H2S, municipal waste combustor (MWC) organics measured as total tetra- through octa-chlorinated dibenzo-p-dioxins and dibenzofurans (dioxin/furan), MWC metals measured as PM; MWC acid gases measured as SO2 and hydrogen chloride (HCl), and MSW landfill emissions as non-methane organic compounds (NMOC).

As defined in Rule 62-210.200(189)(a)1, F.A.C., a stationary source is a “major stationary source” (major PSD source) if it emits or has the potential to emit (PTE):

- 250 tons per year (TPY) or more of any PSD pollutant; or

- 100 TPY or more of any PSD pollutant and the facility belongs to one of the 28 listed PSD major facility categories.

The list given in the citation includes the category of “fossil fuel-fired steam electric plants of more than 250 million British thermal units per hour heat input”.  The SHGS is a major stationary source because it meets this definition and will emit, or has the PTE, 100 TPY or more of any PSD pollutant.

PSD applicability for a “modification” to an existing major stationary source is based on thresholds known as the significant emission rates (SER) as defined in Rule 62-210.200(282), F.A.C.  Any “net emissions increase” as defined in Rule 62-210.200(210), F.A.C. of a PSD pollutant from the project that equals or exceeds the respective SER is considered “significant.”  SER also means any emissions rate or any net emissions increase of a PSD pollutant associated with a major stationary source or major modification which would construct within 10 km of a Class I area and have an impact on such area equal to or greater than 1 gram per cubic meter, 24-hour average.  Pursuant to Rule 62-210.200(121), F.A.C., the SHGS and SHCCF are considered to be one facility, therefore, the PSD analysis and HAP aggregation is collectively assessed for this project.  The SHCCF has been assigned a new facility identification number for ease of separation due to the possibility of new ownership in the near future.

Although a facility may be “major” (i.e. emits or has the PTE 100 or 250 TPY as applicable) for only one PSD pollutant, a project is subject to PSD review for any PSD pollutant that exceeds the corresponding SER given in Table 3.  As already noted, the SHGS is already a major stationary source.  Consequently, the SHCCF (project) is subject to the PSD SERs.

Table 3 - List of Significant Emissions Rates. a

| Pollutant | SER (TPY) | Pollutant | SER (TPY) |
| --- | --- | --- | --- |
| CO | 100 | NOX | 40 |
| PM/PM10/PM2.5 | 25/15/10 | Ozone (VOC) b | 40 |
| PM2.5 (NOX) | 40 | PM2.5 (SO2) | 40 |
| Ozone (NOX) b | 40 | SAM | 7 |
| SO2 | 40 | Pb | 0.6 |
| Hg | 0.1 | GHGs | 75,000 (CO2e) c |
| - Excluding fluoride and pollutants specific to the Pulp and Paper industry, MWCs, MSW landfills. - Ozone (O3) is regulated by its precursors (VOC and NOX). PSD for PM2.5 can be triggered by its precursors (NOX and SO2). - “CO2e” means carbon dioxide equivalents and refers to greenhouse gas (GHG) emissions. The calculation of GHG emissions is defined in 40 CFR 98, Subpart A, Table A-1. |  |  |  |

A source that triggers PSD review for a traditional PSD pollutant (listed above) also triggers a PSD review for GHG emissions if the source would emit or have the potential to emit 75,000 tons per year of GHGs on a CO2e basis.  Under this framework, a source cannot become subject to PSD review solely on the basis of GHG emissions.

  - PSD Applicability for the Project

The PTE for each new emissions unit associated with this project is summarized in Table 4.

Table 4 - PTE for individual emissions units (tpy).

| Pollutant | Emissions Unit |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | CT & HRSG a | Auxiliary Boiler | Emergency Generator | Fire Pump Engine | Cooling Tower | 2 Circuit Breakers |
| SO2 | 90.6 | 0.34 | 0.00580 | 0.00096 | - | - |
| PM | 59.3 | 0.42 | 0.181 | 0.029 | 16.06 | - |
| PM10 b | 59.3 | 0.42 | 0.181 | 0.029 | 3.17 | - |
| PM2.5 b | 59.3 | 0.42 | 0.181 | 0.029 | 0.010 | - |
| NOX | 116.8 | 3.00 | 5.80 | 0.57 | - | - |
| CO | 179.1 | 4.80 | 3.17 | 0.497 | - | - |
| VOC (as methane) | 30.7 | 0.30 | 0.907 | 0.143 | - | - |
| SAM | 15.2 | Neg. | Neg. | Neg. | - | - |
| GHGs (CO2e) | 1,877,683 | 7,019 | 606 | 100.8 | - | 62.4 |
| - The potential annual emissions resulting from this unit were estimated at baseload conditions with an ambient temperature of 59°F with evaporative cooling and 4,000 hours per year of duct firing. - The applicant considered all PM10 and PM2.5 emissions to be the same as PM emissions. Note: Neg. = negligible |  |  |  |  |  |  |

The project is in Pasco County, which is in an area that is currently in attainment with the AAQS or otherwise designated as unclassifiable.  The Project is also not located within an area of influence of a nonattainment area.  Therefore, nonattainment New Source Review (NSR) requirements are not applicable.  However, the project emits or has the potential to emit above the SER for at least one PSD pollutant.  Therefore, the project is subject to a PSD applicability review.  Table 5 identifies the total estimated emissions increases associated with the project based on the initial application.

Table 5 - Summary of the Applicant’s PSD Applicability Analysis.

| Pollutant | Annual Emissions, Tons/Year |  | Subject to PSD? |
| --- | --- | --- | --- |
|  | Project Potential Emissions | Significant Emission Rate |  |
| CO | 187.5 | 100 | Yes |
| NOX | 126.2 | 40 | Yes |
| PM | 76.0 | 25 | Yes |
| PM10 | 63.1 | 15 | Yes |
| PM2.5 | 59.9 | 10 | Yes |
| SO2 | 90.9 | 40 | Yes |
| VOC | 32.0 | 40 | No |
| GHG a | 1,885,409 | 75,000 | Yes |
| SAM | 15.2 | 7 | Yes |
| - Threshold applies only if PSD review triggered for regulated air pollutants other than GHG |  |  |  |

As shown in the Table 5, the project is subject to PSD preconstruction review for emissions of:  CO, NOX, PM/PM10/PM2.5, SO2, GHG and SAM.

- BACT Process

“Best Available Control Technology” or “BACT” is defined in Rule 62-210.200(32), F.A.C. as follows:

- An emission limitation, including a visible emissions standard, based on the maximum degree of reduction of each pollutant emitted which the Department, on a case by case basis, determines is achievable through application of production processes and available methods, systems and techniques (including fuel cleaning or treatment or innovative fuel combustion techniques) for control of each such pollutant, taking into account:

  - Energy, environmental and economic impacts, and other costs;

  - All scientific, engineering, and technical material and other information available to the Department; and

  - The emission limiting standards or BACT determinations of Florida and any other state.

- If the Department determines that technological or economic limitations on the application of measurement methodology to a particular part of an emissions unit or facility would make the imposition of an emission standard infeasible, a design, equipment, work practice, operational standard or combination thereof, may be prescribed instead to satisfy the requirement for eh application of BACT.  Such standard shall, to the degree possible, set forth the emissions reductions achievable by implementation of such design, equipment, work practice or operation.

- Each BACT determination shall include applicable test methods or shall provide for determining compliance with the standard(s) by means which achieve equivalent results.

- In no event shall application of best available control technology result in emissions of any pollutant which would exceed the emissions allowed by any applicable standard under 40 CFR Parts 60, 61, and 63.

EPA’s RACT/BACT/LAER Clearinghouse (RBLC), is also employed to provide a list of recent BACT determinations regarding similar projects within the last 10 years throughout the country for comparison.

- Department’s Project Review

As previously described, SHGS currently operates three simple cycle combustion turbines, identified as (EU 001- 003).  The initial startup date for EU 001 was December 1, 2001.  EU 002 and EU 003 are documented to have initial startup dates of January 2, 2002, and February 5, 2002, respectively.  The facility also includes a natural gas heater (EU 010), one emergency diesel generator (EU 011), and one emergency diesel fire pump (EU 012).  As currently permitted, the SHGS is not a major source of HAPs emissions.  The combined potential HAPs emissions from the proposed SHCCF and SHGS will remain under the “major source” threshold of 10 TPY for a single HAP (i.e., formaldehyde) and 25 TPY for all HAPs.

Regarding the PSD analysis, emission increases or decreases for a particular modification are contemporaneous if they occur between five years before the construction of that change and the date the increase from the change occurs.  However, none of the existing emission units will be affected by the construction of the SHCCF.  Therefore, there are no contemporaneous and creditable emission decreases in actual emissions, and the only increases in actual emissions would occur from the newly constructed units associated with the project.

  - GE 7HA.02 CTG (EU 001)

Combustion turbines are essentially composed of three major components: compressor, combustor, and power turbine.  A gas turbine essentially compresses air and fuel in the compressor module and then triggers an ignition within the combustor.  As a result, gases are expanded through the turbine and the turbine’s shaft continues to rotate and drive the compressor to continue operation.  The compressor module, combustor module and turbine module connected by one or more shafts are collectively called the CTG.  A HRSG may be added to convert the remaining heat energy of the exhaust gases into steam to drive a steam-electric turbine to produce additional electricity.  Gas turbines with heat recovery steam generators are commonly referred to as combined cycle units.  Furthermore, duct burners in the HRSG may be fired with natural gas to raise the useful heat energy of the gas turbine exhaust and produce additional steam-generated electricity.  Although the overall cycle of the unit is less efficient in this mode, duct firing is useful during periods of high-energy demand, i.e., peaking.

For this project, the applicant is proposing to install one nominal 385 MW GE 7HA.02 CTG and one HRSG with duct firing [approximately 210 MMBtu/hour], and one nominal 210 MW steam turbine generator (STG).  A process flow diagram of the new CTG/HRSG/STG configuration, operating at base load conditions with an ambient temperature of 59°F, is presented in Figure 4.

Figure 4.  A Process Flow Diagram of the New CTG/HRSG/STG Configuration.

Natural gas will be the only permitted fuel for the unit.  According to the manufacturer, the lowest operating load where compliance with emission levels are achieved is referred to as the minimum emission compliance load (MECL).  The MECL is approximately 25 percent for the GE 7HA.02 CTG but varies with ambient temperature.

EU 001 Applicable State Regulations

For this project, the following state regulations are applicable to EU 001:

- Rule 62-204.800, F.A.C. (Federal Regulations Adopted by Reference);

- Rule 62-212.400, F.A.C. (PSD Preconstruction Review and Best Available Control Technology (BACT));

- Rule 62-214.300, F.A.C. (Acid Rain Applicability); and

- Rule 62-297.310, F.A.C. (General Emissions Test Requirements).

EU 001 Applicable Federal Regulations

The following NSPS provisions are applicable to EU 001:

- NSPS, Subpart A (General Provisions);

- NSPS, Subpart KKKK (Standards of Performance for Stationary Combustion Turbines that Commenced Construction, Modification or Reconstruction After February 18, 2005); and

{Note:  Pursuant to NSPS, Subpart KKKK, the NOX emissions shall not exceed 15 parts per million by volume, dry (ppmvd) at 15% oxygen (O2) and 96 ppmvd at15% O2 for operating at less than 75% of peak load.  The emission standards of this NSPS also apply to the duct burners.  The NOX emission standards are on a 30-unit operating day rolling average basis}

- NSPS, Subpart TTTT (Standards of Performance for Greenhouse Gas for Electric Generating Units);

{Note:  Under NSPS, Subpart TTTT, baseload combustion turbines that combust more than 90% natural gas are subject to a standard of 1,000 lb CO2 per megawatt-hour (MWh), gross, on a 12-operating-month rolling average basis.  For gas-fired turbines under Subpart TTTT, and under the Acid Rain continuous monitoring provisions of 40 CFR 75, emissions of CO2 may be measured using a continuous emissions monitor, or through fuel use monitoring and emissions factors.}

    - BACT Review for EU 001

This project did not trigger PSD for VOC emissions.  Therefore, the BACT review for the CTG will only pertain to NOX, CO, PM/PM10/PM2.5, SO2 (including SAM) and GHG emissions.

      - NOX Emissions

The amount of NOX produced by a combustor increases with the value of the flame temperature in the combustor and the corresponding value of turbine inlet temperature.  Nearly all of the NOX is emitted as nitric oxide (NO), which is readily oxidized in the exhaust system or the atmosphere to the more stable NO2 molecule (nitrogen dioxide).  NOX forms from the dissociation of molecular nitrogen and oxygen into their atomic forms and subsequent recombination into seven different oxides of nitrogen.  Three primary mechanisms cause NOX emissions:

•	Thermal NOX forms in the high temperature area of the gas turbine combustor.  It increases exponentially with increases in flame temperature and linearly with increases in residence time.  Flame temperature is dependent upon the ratio of fuel burned in a flame to the amount of fuel that consumes all of the available oxygen.  Less NOX is formed during lean combustion (low fuel-to-air ratio) because the flame temperature is lower.

•	Prompt NOX is formed in the proximity of the flame front as intermediate combustion products.  The contribution of prompt NOX to overall NOx emissions is relatively small in combustors that operate near the stoichiometric air-to-fuel ratio.  However, new combustors that operate in lean premix mode generate far less thermal NOX, which makes prompt NOX a greater contributor to overall NOX emissions for these types of units.  Therefore, prompt NOx may provide a practical limit for NOX control by lean combustion.

•	Fuel NOX forms from the oxidation of nitrogen in the fuel.  This phenomenon is not important when combusting natural gas or distillate oil fuels, which contain negligible fuel-bound nitrogen (FBN).

Controlling NOX emissions is significantly important for various reasons, including its contribution to acid rain.

Identification of Control Technologies

The following technologies were identified as potentially applicable for the control of NOX from gas turbines.  A brief description of each technology is included with an estimated control efficiency.

Wet Injection (WI):  Water or steam is injected into the primary combustion zone to reduce the flame temperature, resulting in lower NOX emissions.  Water injected into this zone acts as a heat sink by absorbing the heat necessary to vaporize the water and raise the temperature of the vaporized water to the temperature of the exhaust gas stream.  Steam injection uses the same principle, excluding the heat required to vaporize the water.  Therefore, much more steam is required (on a mass basis) than water to achieve the same level of NOX control.  However, there is a physical limit to the amount of water or steam that may be injected before flame instability or cold spots in the combustion zone would cause adverse operating conditions for the combustion turbine.  Wet injection techniques are generally reserved for oil firing because advanced lean premix combustor designs can achieve much lower NOX emissions for gas firing without wet injection.  However, for oil firing, the advanced dual fuel combustor designs can tolerate large amounts of steam or water without causing flame instability and can typically achieve NOX emissions of less than 42 ppmvd when combined with wet injection techniques.  Therefore, wet injection remains a viable alternative when firing oil in modern dual fuel combustors.  Wet injection results in control efficiencies approaching 75% for oil firing.

Dry Low NOX (DLN) Combustion:  The excess air in lean combustion cools the flame and reduces the rate of thermal NOX formation.  Lean premixing of gaseous fuel and air prior to combustion can further reduce NOX emissions.  This is accomplished by minimizing localized fuel-rich pockets (and high temperatures) within the combustion zones.  This principle is incorporated into the General Electric DLN-2.6 can-annular combustor design depicted in Figure 5 below; this is a DLN design used in other models of GE turbines, but the general principle is the same for the 7HA.02 model.

Figure 5.  GE DLN-2.6 Fuel Nozzle Arrangement.

Each combustor includes six nozzles within which gaseous fuel and air have been fully pre-mixed.  There are 16 small fuel passages around the circumference of the combustor known as the quaternary fuel pegs.  The six nozzles are sequentially ignited as load increases in a manner that maintains lean pre-mixed combustion and flame stability.

Selective Catalytic Reduction (SCR):  This is an add-on control technology in which ammonia is injected into the exhaust gas stream in the presence of a catalyst bed to combine with NOX in a reduction reaction forming nitrogen and water.  Figure 6 below shows the general arrangement of the ammonia injection grid and SCR catalyst with respect to the heat recovery steam generator for a combined cycle unit.

Figure 6.  Key HRSG Components (10 is SCR).

The exhaust gas temperature must be maintained between 450°F and 850°F for this reaction to proceed satisfactorily.  For combined cycle gas turbines, the temperature is within the proper range and conventional catalysts such as vanadium or titanium oxide are acceptable.  However, the exhaust from simple cycle gas turbines can exceed 1000°F and require more expensive high temperature zeolite catalysts and possibly additional gas cooling to protect the catalyst.  Ammonia that escapes past the catalyst without reacting with NOX is called “ammonia slip”.  If the fuel contains significant amounts of sulfur, high levels of ammonia slip can lead to the formation of bisulfates and other particulate matter.  Ammonia slip will gradually increase over the life of the system due to degradation of the catalyst.  The catalyst is typically replaced every 5 to 7 years although vendors typically guarantee catalysts for about three years.  SCR is a commercially available, demonstrated control technology currently employed on numerous combined cycle combustion turbine projects permitted with very low NOX emissions (< 2.5/10 ppmvd for gas/oil firing).  There are a few “hot SCR” systems employed on smaller simple cycle units with slightly higher NOX emissions.  SCR results in control efficiencies of approaching 98%.

EMx (Formerly SCONOX):  This technology is a NOX and CO control system developed by Goal Line Environmental Technologies and is distributed through Alstom Power for large gas turbine projects.  Specialized potassium carbonate catalyst beds reduce NOX emissions using an oxidation-absorption-regeneration cycle.  The required operating temperature range is between 300°F and 700°F, which is within the typical range of exhaust gas from heat recovery steam generator in a combined cycle gas turbine.  SCONOxTM technology (at 2.0 ppmvd) has been used to define the Lowest Achievable Emission Rate (LAER) in non-attainment areas where cost is not a factor in establishing an emissions standard.  SCONOxTM systems also oxidize emissions of CO and VOC for additional emission reductions.  SCONOxTM can also achieve control efficiencies approaching 98% without the additional ammonia emissions associated with SCR.

XONONTM:  This is an emerging technology that partially burns fuel in a low-temperature pre-combustor and completes combustion in a catalytic combustor.  The result is partial combustion with a lower temperature (and less NOx formation) followed by flameless catalytic combustion to further inhibit NOX formation.  This technology has been demonstrated, but the design will be unique for each manufacturer and model of gas turbine.  It is anticipated that control efficiencies may approach 98%.

Selective Non-Catalytic Reduction (SNCR):  This technology works on the same principle as SCR, but in the absence of a catalyst.  Ammonia (or urea) is injected directly into a hot gas stream (1400° F to 2000° F), which promotes the conversion of NOX to nitrogen and water given sufficient residence time.  No applications have been identified wherein SNCR was applied to a gas turbine because the exhaust temperature of 1100° F is too low to support the NOX conversion mechanism.  However, with a large duct burner in the heat recovery steam generator, it is possible to reach the exhaust gas temperatures that would make SNCR feasible.

Thermal DeNOX:  Thermal DeNOX is a patented version of SNCR, using ammonia as the reducing agent.  Thermal DeNOX has been employed on boilers, furnaces, and incinerators, but not on combustion turbines.

NOXOUT:  Similar to SNCR, in the NOXOUT process, aqueous urea is injected into the flue gas stream, at high temperatures.  The reaction, in the presence of O2, converts urea, NO and O2 to N2, CO2 and water.  The commercial application of NOXOUT has been limited to boilers and municipal waste combustors, and it has not been demonstrated on combined cycle combustion turbines.

Non-Selective Catalytic Reduction (NSCR):  NSCR employs a three-way catalyst to reduce emissions of NOX and CO.  This technology is often employed on spark-ignition internal combustion engines, but is not commonly used on natural gas combustion cycle units.

Discussion of Technically Infeasible Control Options and Ranking of Remaining Options

As previously described, water injections remain as a viable control technology when firing oil in modern dual fuel combustors.  However, fuel oil will not be utilized in the CTG for this project, therefore, water injection is not considered technically feasible.  Other control technologies, such as EMx and XONONTM are also technically infeasible because they have not been commercially demonstrated on large combined cycle combustion turbines.  The NOXOUT system is limited mainly to boilers and has also not been commercially operated on any large combined cycle gas turbine units.  Similarly, there are no known applications of the Thermal DeNOx technology to combined cycle units and high capital, operating, and maintenance costs would be expected because of material requirements, a natural gas-fired exhaust heating system, and fuel consumption.

The temperature at the exhaust stack downstream of the HRSG is expected to range between approximately 160 and 220°F.  Therefore, the SNCR technology is not technically feasible for this application because the proposed CT will not approach the operating temperature window for SNCR.  Furthermore, the NSCR process will require low O2 content in the exhaust gas stream to be effective, which is not the case for combined cycle units which have high O2 levels (greater than 12 percent).  As a result, the NSCR technology is also not technically feasible for this unit.

Of these technologies, the applicant indicates that only an SCR and DLN combustors are considered to be technically feasible for the project.

Evaluation of Economic, Environmental, and Energy Impacts of Feasible Technologies

Properly tuned DLN combustors do not create negative environmental impacts since these systems are designed and operated to achieve the optimum balance between CO and NOX emissions.  The applicant also evaluated a reduction of approximately 1,500 TPY of NOX emissions with an SCR.  The SCR will require either anhydrous or aqueous ammonia, which can cause environmental consequences if not handled and stored properly.  However, the storage of anhydrous and aqueous ammonia (20% or greater) will trigger requirements imposed by OSHA and the Community Right-to-Know Act.  The applicant intends to use aqueous ammonia in a 19% or lower solution.  Ammonia slip concentrations (i.e., unreacted ammonia emitted from the stack) is typically 9 ppm or less but has the potential to increase depending on the ammonia feed rates.  Additionally, the used catalyst would be returned to the catalyst supplier for regeneration or disposed of in accordance with all applicable regulations.

The applicant estimated a total annualized cost of approximately $1.8 million and a total capital cost of about $4.2 million for the SCR.  The DLN combustors are part of the standard design of the 7HA.02 turbines to substantially reduce NOX emissions.  Therefore, the applicant estimated an incremental cost effectiveness of adding the SCR to the DLN combustors as $1,321-per ton of NOX removed, based on 8,760 hours of operation with 4,760 hours firing natural gas at baseload and 4,000 hours of duct firing.

Selection of BACT and Rationale

As stated in the definition of BACT, “in no event shall application of BACT result in emissions of any pollutant which would exceed the emissions allowed by any applicable standard under 40 CFR Parts 60, 61, and 63”.  An NSPS NOX standard of 15 ppmvd at 15% O2 applies and a 96 ppmvd at 15% O2 limit is provided for combustion turbines operating at less than 75% of peak load.   The NOX emissions standards under NSPS Subpart KKKK apply at all times; therefore, they can provide a useful Secondary BACT backstop during transient operating modes when Primary BACT limits might not be achievable.

The applicant proposes the following BACT determination for the control of NOX emissions for the proposed CTG:

•	NOX emissions will be controlled using DLN combustors and SCR;

•	NOX emissions shall be limited to 2.0 ppmvd at 15% O2 as BACT on a 24-hour block average basis;

•	During startups, shutdowns, SCR tuning, DLN tuning and malfunctions, the Secondary BACT limit, rather than the Primary BACT limits above, applies.  The Secondary BACT limit is equal to the NSPS Subpart KKKK limit.  Demonstrating compliance with the NSPS Subpart KKKK limit shall be sufficient for demonstrating compliance with the Secondary BACT limit during such transient modes of operation.

•	Duct firing shall be limited to 4,000 hours per year; and

- •	Compliance shown by a NOX continuous emissions monitoring system (CEMS).

- The RBLC was also referenced for previous BACT determinations to similar projects.  Table 6 provides a list of emissions standards, along with the selected control technologies, for limiting emissions of NOX.

Table 6 - RBLC BACT Determinations for NOX for Natural Gas-Fired Combustion Turbines.

| - RBLC ID | - Date | - Source Type | - Heat Input or MW Rating | - Pollutant Limit | - Averaging Period | - Control Method |
| --- | --- | --- | --- | --- | --- | --- |
| - FL-0356 | - 03/09/2016 | - 3-on-1 CCCT with HRSG | - 3,096 MMBtu/hour | - 2.0 ppmvd @ 15%O2 | - 24-hr block average CEMS | - DLN, SCR, WI |
| - FL-0363 a | - 12/04/2017 | - 2-on-1 CCCT with HRSG | - 1,200 MW |  |  |  |
| - GA-0138 | - 04/08/2010 | - 2-on-1 CCCT with HRSG | - 600 MW | - 2.5 ppmvd @ 15 O2 | - 3-hr rolling average CEMS | - DLN, SCR |
| - NJ-0085 | - 07/19/2016 | - 1-on-1 CCCT with HRSG | - 633 MW | - 2.0 ppmvd @ 15% O2 b | - 3-hr rolling average CEMS | - DLN, SCR |
| - TX-0709 | - 03/20/2015 | - 1-on-1 CCCT with HRSG | - 174 MW | - 2.0 ppmvd @ 15%O2 | - 24-hr rolling average CEMS | - SCR |
| - Abbreviations: Combined cycle combustion turbine (CCCT) - This project was not subject to PSD review for NOX, and the limit was imposed at the applicant’s request, i.e. the limit does not constitute BACT. However, the requested limit is consistent with BACT determinations for similar projects. - This limit constitutes the Lowest Achievable Emissions Rate (LAER). |  |  |  |  |  |  |

Considering all available information, the Department establishes a Primary NOX BACT standard of 2.0 ppmvd at 15% O2 on a 24-hour block average basis with compliance demonstrated by CEMS.  Consistent with other BACT determinations for natural gas firing, the SCR and DLN combustors will be required for installation.

The applicable NOX limitations contained in NSPS Subpart KKKK shall apply as Secondary BACT limits.  Conditions such as startup, shutdowns, and malfunctions, which are generally not subject to the Primary BACT limit, will be subject to a Secondary BACT limit, which is equivalent to the applicable NSPS Subpart KKKK emissions standards.  Demonstrating compliance with the NSPS Subpart KKKK limit for NOX will be sufficient for demonstrating compliance with the Secondary NOX BACT limit.

As requested, duct firing shall be limited to 4,000 hours per year.  The CTG will also be subject to work practices for startup and shutdown, which will minimize emissions of NOX and other pollutants.  Additionally, operators will be required to follow the manufacturer’s recommended procedures for startup and shutdown of the turbines, all operators will need to be trained in these procedures, and SHEC will have to maintain documentation of this training for all operators.

      - CO Emissions

As seen in Table 4, one of the primary pollutants being emitted from the combustion turbine is CO.  Emissions of CO are formed due to incomplete combustion of the natural gas.  Incomplete combustion occurs when there is insufficient residence time at high temperature or incomplete mixing to completely form carbon dioxide (CO2) and water (H2O).  Furthermore, the incomplete combustion of carbon-containing fuels such as natural gas is more likely to occur for gas turbines operating at low loads as compared to similar gas turbines operating at higher loads.

For many combustion processes, CO emissions are inversely proportional to NOX emissions.  However, the DLN combustor design for General Electric’s Frame 7HA gas turbines have also successfully reduced CO emissions concurrently with NOX emissions.  Emissions of CO can be further controlled through the careful tuning of combustion and through add-on technologies.

Identification of Control Technologies

Good Combustion Practices (GCP):  Evaporative cooling (also known as “fogging”) is the injection of fine water droplets into the gas turbine compressor inlet air, which reduces the gas temperature through evaporative cooling.  As described in the application, the gas turbine will employ evaporative cooling at 100 percent load and ambient temperatures of 59°F or higher.  The lower compressor inlet temperatures result in an increased mass flow rate through the gas turbine with a boost in shaft-driven electrical power production.  A full description of good combustion practices includes following the manufacture’s recommendations, the tuning of combustion, sufficient mixing of air and fuel, and dry controls using advanced combustor design to promote CO burnout.  The control system is adjusted to consider the effect of the water content due to high fogging which can cause the pulsation levels of the combustion system and CO emissions to increase.  Simulations in steady-state cycle confirmed that high fogging will cause a minor shift in the hot gas temperature if the dry formulas are applied without any consideration.  However, when using the adjusted turbine inlet temperature formulas, high fogging has a negligible influence on CO emissions under baseload operating conditions where the CO emissions are minimized.

Catalytic Oxidation Systems:  A catalytic oxidation system consists of a noble metal catalyst section incorporated into the gas turbine exhaust.  CO oxidation catalysts are especially useful for turbines that use wet injection, which can increase the concentrations of CO and unburned hydrocarbons in the exhaust.  The catalyst is regularly comprised of a precious metal such as platinum, palladium, or rhodium.  Other formulations are also used, such as metal oxides for emission streams containing chlorinated compounds.  The CO catalyst promotes the oxidation of CO and hydrocarbon compounds to CO2 and H2O as the emission stream passes through the catalyst bed.  The oxidation process takes place spontaneously, without the requirement for introducing reactants.  The performance of these oxidation catalyst systems on combustion turbines results in 90-plus percent control of CO and about 85 to 90 percent control of formaldehyde.  A catalytic oxidation system could be installed either before the HRSG or within the HRSG.  Installation within the HRSG would also reduce CO emissions from the duct burner.

EMX:  The EMX system is a process for control of CO, NOX, SO2 and PM emissions from natural gas fired combustion processes such as turbines, process heaters, and a variety of utility and industrial applications.  One benefit is that it does not require injection of ammonia or other chemicals and have demonstrated emission levels below 1 ppm.  However, this technology employs a catalyst that may be poisoned by even the very small amount of sulfur present in natural gas.  Finally, this technology has not been employed on large turbines, greater than approximately 80 MW.  The CTG for this project is roughly five times the size of the largest turbines on which this technology has been employed.  EMX is mechanically very complicated and requires on-site hydrogen production from natural gas.

Startup and Shutdown Work Practice Standards:  Emissions of CO can be rather high at low load operations, such as during periods of startup and shutdown.  At these low loads, CO emissions can briefly be on the order of hundreds of ppmvd.  The applicant has proposed work practice standards that will serve to reduce CO emissions associated with startups and shutdowns.  These include following the manufacturer-recommended procedures for startup and shutdown.

Discussion of Technically Infeasible Control Options and Ranking of Remaining Options

As, previously described, the EMx system has not been employed on large gas turbines.  Therefore, the EMx system is considered to not be technically feasible for the Project.  Work practice standards, combustion controls and oxidation catalyst systems are compatible technologies and are collectively considered as the top control option for CO when applied simultaneously.

Evaluation of Economic, Environmental, and Energy Impacts of Feasible Technologies

Combustion controls and work practice standards are customary for operating the unit, therefore, there will be no economic impacts.  The applicant evaluated the total capital cost of an oxidation catalyst to be approximately $881,000 per CTG/HRSG and a total annualized cost of approximately $717,000.  The applicant also evaluated the incremental cost effectiveness of adding an oxidation catalyst to be approximately $5,184 per ton of CO removed, based on 4,760 hours of operation at baseload and 4,000 hours at baseload with duct firing.  However, in assuming 90% control efficiency of CO, the Department evaluated the incremental cost effectiveness of adding an oxidation catalyst to be approximately $3,569 per ton of CO removed.

GCP along with the DLN combustors do not create negative environmental impacts since these systems are designed and operated to achieve the optimum balance between CO and NOX emissions.  However, the installation of an oxidation catalyst would theoretically reduce potential CO emissions while causing increased oxidation of SO2 to SAM with subsequent partial formation of ammonium sulfate as PM.  The applicant evaluated an emissions increase of up to 7.7 TPY of PM with a potential increase in SAM emissions of 11.5 TPY due to increased oxidation of SO2 to SAM.

In evaluating the energy impacts, the output of the combustion turbine would be reduced by the additional backpressure of an oxidation catalyst system.  The applicant evaluated a penalty that could amount to an estimated 3,539 MWh per year in potential lost generation which is equivalent to the monthly electrical supply of about 295 residential customers, assuming a monthly residential use of 1 MWh per month.  To replace this lost energy, an additional 21,942 British thermal units per year (Btu/yr) or about 22 million cubic feet per year (ft3/year) of natural gas would be required.

Selection of BACT and Rationale

The applicant proposes the following BACT determination for the control of CO emissions from the proposed CTG:

- CO emissions will be controlled using good combustion practices;

- CO emissions shall be limited to 4.3 ppmvd at 15% O2 at base load (≥90%);

- CO emissions shall be limited to 7.1 ppmvd at 15% O2 at non-base load (<90%);

- CO emissions shall be limited to 6.5 ppmvd at 15% O2 with duct firing;

- Work practice standards that limit CO emissions during startups and shutdowns apply; and

- Compliance shown by stack test.

As seen in Table 7, BACT determinations for CO were evaluated for similar combined-cycle projects that were established within the last ten years.  The GE 7HA.02 turbines have only recently been permitted in Florida.  However, 1-on-1 combined cycle configurations with duct burners were not found.  Given the lack of operating history of the 7HA.02 turbine, it is reasonable to allow some accommodation for this rather new turbine technology.

Table 7 - RBLC BACT Determinations for CO for Natural Gas-Fired Combustion Turbines.

| - RBLC ID | - Date | - Source Type | - Heat Input or MW Rating | - CO Limit | - Averaging Period | - Control Method |
| --- | --- | --- | --- | --- | --- | --- |
| - FL-0356 | - 03/09/2016 | - 3-on-1 CCCT with HRSG | - 3,096 MMBtu/hour | - 4.3 ppmvd @ 15%O2 b | Initial and annual stack tests (3 1-hr runs) | - GCP |
| - FL-0363 | - 12/04/2017 | - 2-on-1 CCCT with HRSG | - 1,200 MW | - 4.3 ppmvd @ 15%O2 b |  |  |
| - GA-0138 | - 04/08/2010 | - 2-on-1 CCCT with HRSG | - 600 MW | - 3.2 ppmvd @ 15%O2 a | - 3-hr rolling average CEMS | - Oxidation catalyst |
| - TX-0730 | - 04/01/2015 | - 2-on-1 CCCT with HRSG | - 1,100 MW | - 4.0 ppmvd @ 15%O2 a |  |  |
| - Limit is for combined cycle mode of operation with duct burner firing. - Limit is for turbine loads greater than or equal to 90%. |  |  |  |  |  |  |

Additionally, since no CEMS for CO is proposed, it will be rather difficult to assess CO emissions at low loads.  However, manufacturer product information shows that emissions limits for the 7HA.02 can be met down to turbine loads of 25%.  Additional non-base-load CO compliance tests will be required, and an additional work practice standard will be included in the permit, prohibiting the operation at a load lower than that load at which compliance with the non-base-load CO limit was achieved, other than during startups, shutdowns, SCR tuning, DLN tuning, and documented malfunctions.  Subsequent non-base-load CO tests will be required annually.  The Department determined the efficient combustion design and good operating practices to be representative of the Best Available Control Technology and accepts the applicant’s proposal to maintain consistency with other recently permitted combined cycle units in Florida.

      - PM/PM10/PM2.5 Emissions

PM emissions are defined as a complex mixture of fine solid particles and liquid droplets that are carried into the air and can be classified as either filterable or condensable.  PM emissions increase with incomplete fuel combustion along with higher concentrations of ash, sulfur, and trace elements in certain fuels.  Filterable PM is the portion of the total PM that exists in the stack in either the solid or liquid state and can be measured on a EPA Method 5 filter.  Condensable PM is composed of organic and inorganic compounds and is generally considered to be all less than 1.0 micrometers in aerodynamic diameter.  Condensable PM is that portion of the total PM that exists as a gas in the stack but condenses in the cooler ambient air to form particulate matter.  Condensable PM exists as a gas in the stack, so it passes through the Method 5 filter and is typically measured by analyzing the impingers, or "back half" of the sampling train.  The collection, recovery, and analysis of the impingers is described in EPA Method 202 of Appendix M, Part 51 of the Code of Federal Regulations.

Identification of Control Technologies

Clean Fuels:  PM emissions are negligible with natural gas firing and marginally significant with distillate oil firing because of the low ash content.  Natural gas is identified as the cleanest of the fossil fuels as seen in Table 8.

Table 8 - Fossil Fuel Emission Levels (Pounds/Billion Btu of Energy Input) a.

| Pollutant | Natural Gas | Oil | Coal |
| --- | --- | --- | --- |
| CO2 | 117,000 | 164,000 | 208,000 |
| CO | 40 | 33 | 208 |
| NOX | 92 | 448 | 457 |
| SO2 | 1 | 1,122 | 2,591 |
| PM | 7 | 84 | 2,744 |
| - Source: EIA- Natural Gas Issues and Trends 1998 |  |  |  |

GCP:  GCP can be utilized to ensure complete combustion to minimize PM emissions.  Combustion chamber designs can be optimized and to further improve the oxidation process to promote complete combustion.  Modern CTs have been improved to implement effective chamber designs.

Electrostatic Precipitator (ESP):  An ESP is an add-on control device that can be placed to lower PM concentrations by creating a direct-current voltage across a pair of electrodes.  PM is separated from the gas stream by high voltage electrodes that generate an electrical field to attract PM to collector walls.  Dry ESP walls are knocked or “rapped” to dislodge PM into a collection hopper.  Whereas a wet ESP removes particles from the collecting electrodes by washing the collection surface using liquid rather than mechanically rapping the collector plates.  A wet ESP is commonly used for gas streams which retain a high moisture content.  The efficiency of a wet or dry ESP depends on dust resistivity, gas composition, gas temperature, and particle size distribution.

Baghouses:  Baghouses are used to primarily remove PM/PM10/PM2.5, and PMHAP from processes with high PM loadings and/or flow rates.  A baghouse contains fabric filter bags to remove PM from the gas stream.  The gas passes through filter bags and deposits PM (filter cake) on the bags.  The PM is dislodged from the filter bags using mechanical shakers, pulse-jets, or reverse-air flow.  The PM collection efficiency of a baghouse has reached up to 99.9%.

Wet Scrubber:  Wet scrubbers primarily treat PM/PM10/PM2.5, and high-solubility gases, but offer incidental treatment of VOC.  The pollutants are removed primarily through the impaction, diffusion, interception and/or absorption of the pollutant onto droplets of liquid.  Venturi scrubbers are the most efficient for PM collection with efficiencies ranging from 70% to over 99%.

Discussion of Technically Infeasible Control Options and Ranking of Remaining Options

GCP and clean fuels have been commonly employed on large CTGs and are deemed to be technically feasible for this Project.  However, as seen in Table 9, add-on control devices such as baghouses, ESPs and wet scrubbers have not been utilized for combined cycle CTGs because of high volumes of airflow, fine particulate distribution, and inherently low uncontrolled PM emission rates.

Table 9 - RBLC BACT Determinations for PM/PM10/PM2.5 for Natural Gas-Fired Combustion Turbines.

| - RBLC ID | - Date | - Source Type | - Heat Input or MW Rating | - Pollutant Limit | - Averaging Period | - Control Method |
| --- | --- | --- | --- | --- | --- | --- |
| - FL-0356 | - 03/09/2016 | - 3-on-1 CCCT with HRSG | - 3,096 MMBtu/hour | - 2.0 gr S/100 scf | - -- | - GCP, clean fuels |
| - FL-0363 | - 12/04/2017 | - 2-on-1 CCCT with HRSG | - 1,200 MW |  |  |  |
| - GA-0138 | - 04/08/2010 | - 2-on-1 CCCT with HRSG | - 600 MW | - 0.5 gr S/100 scf | - -- | - Low sulfur fuel |
| - KY-0106 | - 09/30/2016 | - 3-on-1 and 2-on-1 CCCT with HRSG | - 1,700 MW | - 13.78 lb/hour a,b | - 24-hr average | - Low sulfur fuel (1 gr S/100 scf) |
| - LA-0313 | - 08/31/2016 | - 2-on-1 CCCT with HRSG | - 980 MW | - 0.008 lb/MMBtu | - 3-hour average | - GCP, clean fuels |
| - Limit is for combined cycle mode of operation with duct burner firing. - Limit is for PM10. |  |  |  |  |  |  |

Evaluation of Economic, Environmental, and Energy Impacts of Feasible Technologies

The applicant identified the use of GCP and clean fuels to result in the lowest economic, environmental and energy impacts in reducing emissions of PM.  The PM exhaust concentration of the proposed CTG/HRSG is estimated to be 0.002 grains/standard cubic feet (gr/scf) or less which is lower than the typical design outlet conditions for add-on controls used on fossil fuel steam generators that fire coal and oil.

Selection of BACT and Rationale

Due to the infeasibility of the remaining control options, GCP and clean fuels have been selected as the top control option for PM emissions.  The applicant has proposed the use of clean fuels and GCPs as BACT for PM, along with an emissions standard for opacity of 10% to ensure proper combustion and low emissions of PM.

The Department agrees that the combination of GCP and startup/shutdown work practice standards for this project constitute as BACT for PM.  To maintain consistency with previous BACT determinations, the following conditions are established as the draft BACT standards.

•	The combustion turbine shall fire natural gas as the only permitted fuel, which shall contain no more than 2.0 gr. sulfur/100 scf of natural gas.

•	Visible emissions shall not exceed 10% opacity based on a 6-minute average.  Visible emissions during startup, shutdowns, SCR tuning, DLN turning, and malfunctions shall not exceed 10% opacity, except for up to six 6-minute average periods during a calendar day, which shall not exceed 20% opacity.

      - SAM and SO2 Emissions

Emissions of SAM and SO2 are caused from the sulfur content contained in fuels.  The employed control technologies for combustion sources consist of fuel treatment and post-combustion add-on controls that rely on chemical reactions within the control device to reduce the concentration of SO2 in the flue gas.

Identification of Control Technologies

Flue Gas Desulfurization (FGD):  An FGD is an add-on control used for removing SO2 from the exhaust combustion flue gases of power plants that burn coal or oil.  FGD systems commonly employ alkaline sorbents such as lime or limestone to neutralize SAM and remove the SO2 from the flue gas.  Wet and dry scrubbers are potential FGD systems.  Wet scrubbers normally utilize limestone as the reagent which is slurried with water and sprayed into the flue gas stream in an absorber vessel.  The wet scrubbers create by-products such as calcium sulfite and/or calcium sulfate.  Unlike wet scrubbers, dry scrubbers utilize lime as the reagent and the by-products are in a dry-form to be captured downstream as PM.

Clean Fuels:  Sulfur compound emissions are minimized through the use of clean-burning fuels, such as natural gas.

Fuel Treatment:  Sulfur in oil can be removed through chemical desulfurization processes, but this is not a widely used commercial technology outside the petroleum industry.  Similarly, the desulfurization of natural gas is performed by the fuel supplier prior to distribution by pipeline.

GCP:  GCP can improve efficiency of conversion of fuel to electricity which would reduce the fuel consumption required and pollutant emissions per unit of electricity generated.

Discussion of Technically Infeasible Control Options and Ranking of Remaining Options

Fuel treatment is infeasible for this project since the sulfur content in pipeline quality natural gas is extremely low.  Furthermore, the installation of an FGD system would not be technically or economically feasible for the amount of SO2 and SAM being emitted from the combined cycle unit.  Therefore, clean fuels have been ranked as the top control method.

Evaluation of Economic, Environmental, and Energy Impacts of Feasible Technologies

The applicant has not identified any potential energy, environmental, or economic impacts that would preclude the use of natural gas.

Selection of BACT and Rationale

The sulfur content for pipeline natural gas is established by Federal Energy Regulatory Commission (FERC) through the approval of tariffs.  The maximum sulfur content tariff for FGT is 10 grains sulfur per 100 scf (FGT FERC NGA Gas Tariff, Fifth Revised Volume No. 1, General Terms and Conditions Section 2 Quality, August 2015).  However, the sulfur concentrations reported by FGT and individual plant samples have consistently been much less than 1 grain per 100 scf of gas.  Therefore, the applicant proposes a BACT work practice emission limit of 2 grains per 100 scf of gas for the CTG/HRSG with duct firing as a conservative basis, even though this sulfur content is not guaranteed by FGT.

The Department accepts the applicant’s proposal and shall establish a limitation of 2.0 grains of sulfur per 100 scf of gas.  Compliance with the fuel sulfur limit shall be demonstrated by keeping reports obtained from the vendor.  As seen in Table 10, the designated BACT determination is found to be consistent with recent determinations for combined cycle gas turbine projects for SO2 and SAM emissions.

Table 10 - RBLC BACT Determinations for SO2/SAM for Natural Gas-Fired Combustion Turbines.

| - RBLC ID | - Date | - Source Type | - Heat Input or MW Rating | - Pollutant Limit | - Averaging Period | - Control Method |
| --- | --- | --- | --- | --- | --- | --- |
| - FL-0356 | - 03/09/2016 | - 3-on-1 CCCT with HRSG | - 3,096 MMBtu/hour | - 2.0 gr S/100 scf c | - -- | - Low sulfur fuel |
| - FL-0363 | - 12/04/2017 | - 2-on-1 CCCT with HRSG | - 1,200 MW |  |  |  |
| - TX-0788 | - 03/24/2016 | - 2-on-1 CCCT with HRSG | - 220 MW | - 1 gr S/100 scf a,c | - Hourly basis | - GCP and low sulfur fuel |
| - KY-0106 | - 09/30/2016 | - 3-on-1 and 2-on-1 CCCT with HRSG | - 1,700 MW | - 1.17 lb/hour b | - 1-hour average | - Low sulfur fuel (1 gr S/100 scf) |
|  |  |  |  | - 7.82 lb/hour c |  |  |
| - TX-0730 | - 04/01/2015 | - 2-on-1 CCCT with HRSG | - 1,100 MW | - 2.0 gr S/100 scf b,c,d | - 1-hour average | - Efficient combustion, natural gas fuel |
| - There is also a limit for natural gas sulfur content of 0.25 grains sulfur per 100 scf, annual average. - This limit is for sulfuric acid mist, with duct burner firing. - This limit is for sulfur dioxide. - There is also a limit of 0.500 gr S/100 scf of natural gas, annual average. |  |  |  |  |  |  |

      - GHG Emissions

Three greenhouse gases are expected to be emitted from the gas turbine in this project:  carbon dioxide (CO2), methane (CH4), and nitrous oxide (N2O).

Carbon dioxide is the primary product of combustion of carbon-based fuels in air.  The exothermic reaction between fuels and molecular oxygen in air results in the breaking of carbon-carbon bonds or carbon-hydrogen bonds in fuels, the release of energy in the form of heat, and the formation of CO2 and water.  In the case of CH4, which is the main component of natural gas, the reaction is summarized as follows:

CH4+2O2→CO2+2H2O

Small amounts of CH4 are expected in the turbine stacks.  As the primary fuel for the turbines, any methane that remains after combustion represents a lost opportunity to generate electricity.  Methane emissions will be minimized for this reason.  However, very small amounts of CH4 emissions will likely occur.

A very small amount of N2O can be produced as a combustion byproduct.  At the high temperatures associated with combustion, atmospheric nitrogen (N2) and O2 react to form, among other byproducts, N2O.

Greenhouse gases are categorized and compared on an “equivalency” basis according to their “global warming potential” (GWP).  The GWP of a substance is calculated by determining the ratio of the amount of warming due to the emission of a unit mass of the substance, integrated over a chosen period of time, to the amount of warming due to the emission of a unit mass of CO2, integrated over the same time period.  The most commonly used period of time for GWP calculations is 100 years.  The US EPA uses GWP values of unity for CO2, 25 for CH4, and 298 for N2O.  Multiplying emissions of each of these three gases by its respective GWP, and summing the result, yields a CO2-equivalent (CO2e) greenhouse gas emissions estimate.  The maximum potential emissions of CO2e for the CTG/HRSG and duct burner were estimated to about 2 million TPY.

Identification of Control Technologies

Clean Fuels:  The use of low-emitting fuels is a common strategy for minimizing emissions of GHGs.  The use of natural gas results in CO2 emissions that are approximately 30% less than emissions from oil and 45% less than emissions from coal, per unit of heat input.  According to the US Energy Information Administration (EIA), natural gas results in significantly less CO2 than other fossil fuels (see Table 11).

Table 11 - CO2 emissions for various fossil fuels.

| Fuel | CO2 (lb / MMBtu) |
| --- | --- |
| Anthracite coal | 228.6 |
| Bituminous coal | 205.7 |
| Lignite coal | 215.4 |
| Subbituminous coal | 214.3 |
| Diesel fuel | 161.3 |
| Gasoline | 157.2 |
| Propane | 139.0 |
| Natural gas | 117.0 |

Energy Efficiency:  Energy efficiency entails optimizing the amount of electrical output produced per unit of heat input.  For a given unit of electrical output, greater efficiency reduces the amount of fuel used and the amount of CO2 emitted.  Energy efficiency has been included in essentially all BACT determinations for GHGs from combustion turbines.

Carbon Capture & Storage (CCS):  CCS entails capturing the CO2 from flue gas, transporting it to an appropriate location for storage, and sequestering it underground.  This CO2 is usually used for processes such as enhanced oil recovery, in which the CO2 aids in the production of fossil fuels from underground.  Deep saline formations, which are large, porous rock formations, also present a potential opportunity for underground CO2 storage.

The separation and capture of CO2 from the effluent stream can be performed using several different technologies, such as absorption, adsorption, low-temperature distillation, gas separation membranes, or mineralization and biomineralization.  The transport of CO2 from the facility to its ultimate storage site is accomplished via pipeline, most commonly at a pressure of over 1,000 pounds per square inch.  CO2 can also be transported in insulated tanks at low temperature via seagoing vessels, rail, or truck.  Potential locations for long-term underground storage of CO2 include depleted oil and gas reservoirs, un-mineable coal seams, and underground saline formations.

Oxidation Catalyst:  The use of catalytic oxidation technology is primarily used to reduce CO emissions, but it can also be used to reduce emissions of CH4.  Catalytic oxidation can convert CH4, with a GWP of 25, to CO2, with a GWP of one.  This technology would be most attractive to sources with high emissions rates of CH4.  Oxidation catalyst would yield a practically imperceptible reduction in GHG emissions, due to the very small amount of CH4 expected from this project.  Furthermore, the applicant estimates that the additional CO2 emissions arising from the backpressure that results from the use of oxidation catalyst would negate any reductions in CH4 emissions, in terms of CO2-equivalent GHG emissions.

Hybrid Technologies:  Various power generating facilities combine natural gas combined cycle (NGCC) units with solar thermal technology, with both the solar thermal heat and the CT exhaust heat feeding a single steam turbine.  The integration of steam derived from solar energy can significantly decrease the GHG emissions from a power plant per unit of electricity produced.  However, to consider such technologies when evaluating BACT for a fossil fuel-fired plant would constitute as a fundamental redefinition of the project, i.e., source, which is generally not allowed under the PSD program.

Discussion of Technically Infeasible Control Options and Ranking of Remaining Options

CCS is usually eliminated as a prospective control method due to it not being technically feasible.  However, EPA considers CCS as available even though it is not commercially available on a large scale.  Nevertheless, EPA recognizes CCS as an expensive technology, largely because of the costs associated with CO2 capture and compression as supported by EPA’s recent GHG NSPS for electric utility units.  In the Guidance, EPA states that “even if not eliminated in Step 2 of the BACT analysis, on the basis of the current costs of CCS, CCS would be eliminated from consideration in Step 4 of the BACT analysis, even in some cases where underground storage of the captured CO2 near the power plant is feasible”.  Consequently, for this project, CCS can be eliminated solely because it is not an economically feasible control technology based on the current status of CCS technology.

With regards to an Oxidation Catalyst, the applicant has estimated that the total amount of CO2e resulting from CH4 emissions is only 0.05% of total CO2e emissions and is about 900 tons CO2e.  The secondary emissions caused by the backpressure of an oxidation catalyst was estimated to be over 5,000 tons of CO2.  Therefore, the addition of an oxidation catalyst to the CTG/HRSG for GHG control is neither practicable nor feasible to reduce CH4.

The applicant has identified the “top” control option for the CTG/HRSG to be energy efficiency, along with the use natural gas which emits the lowest amount GHG of any fossil fuel.

Evaluation of Economic, Environmental, and Energy Impacts of Feasible Technologies

By selecting energy efficiency and clean fuels, the applicant did not identify any adverse economic, environmental, or energy impacts.  The proposed combined cycle units’ net heat rate and energy efficiency were compared to data obtained from the EIA.  Based on US EIA’s 2016 annual review of the electrical power industry, the reported average net heat rate for natural gas firing by the higher heating value (HHV) was 7,870 Btu/kWh net (43.4 percent efficiency) including all types of generation.  Of the generation types, the average tested heat rates when firing natural gas are:

- Steam turbine generator – 10,382 Btu/kWh net (HHV) (32.9 percent efficiency),

- Natural gas turbine – 11,214 Btu/kWh net (HHV) (30.4 percent efficiency),

- Internal combustion – 9,179 Btu/kWh net (HHV) (37.2 percent efficiency), and

- Combined cycle – 7,652 Btu/kWh net (HHV) (44.6 percent efficiency).

For comparison, the applicant calculated a “new and clean” net heat rate for the combined cycle unit to be 6,200 Btu/kWh net (HHV) (55.0 percent efficiency) at baseload conditions and 7,284 Btu/kWh(HHV) (47.0 percent efficiency) at the MECL, based on an ambient temperature of 77°F.

Selection of BACT and Rationale

The Department converted the unit’s net heat rate to an expected baseload CO2 emissions rate of approximately 737 lb CO2 per MWh:

6,200BtukWh×118.9 lb CO2106Btu×1000 kWhMWh=737.2lb CO2MWh

Note:  CO2 in lb/MMBtu, based on 40 CFR Part 75 Appendix G, Section 2.3 Table C-2, Subpart C, 40 CFR 98. Emission factors in kg/MMBtu for CH2 and N2O.

This would be the expected “new and clean” emissions rate for the CTG, operating at baseload conditions.  However, such efficiency would not be achieved at lower loads which is a necessary mode for turbine operation, even though combined cycle configurations are intended for baseload operations.  Therefore, there does need to be an accommodation for operation at loads less than 100%.

As proposed by the applicant, the Department will set a GHG BACT limit for periods of natural gas usage of 875 lb CO2 per MWh, gross, excluding periods of transient operations, such as startups, shutdowns, etc.  This limit is approximately 16% higher than the unit’s expected “new and clean” baseload emissions rate.  During transient modes of operation such as startups or shutdowns of the entire combined-cycle unit, startups or shutdowns, SCR tuning, DLN tuning, and malfunctions, the Department will adopt as a “Secondary BACT” the limits in NSPS Subpart TTTT.

Additionally, the Department recognizes that the climatic and environmental impacts of GHGs are generally analogous to a “cumulative” framework, rather than an “acute” one.  The Department plans to set the averaging period for GHG BACT for the CTG as a 12-month rolling average.  This averaging period is consistent with EPA’s NSPS Subpart TTTT limits, which are also on a 12-month rolling average basis.

The Department and the applicant identified several recent GHG BACT determinations for combined cycle units, issued within the last 10 years.  Table 12 represents the Department’s results in reviewing the RBLC.  The results ranged from 840 lb/MWh to 1,069 lb/MWh, however a few of these projects have been for less efficient turbine models than the 7HA.02.

Table 12 - RBLC BACT Determinations for GHG for Natural Gas-Fired Combustion Turbines.

| - RBLC ID | - Date | - Source Type | - Heat Input or MW Rating | - Pollutant Limit a | - Averaging Period | - Control Method |
| --- | --- | --- | --- | --- | --- | --- |
| - FL-0356 | - 03/09/2016 | - 3-on-1 CCCT with HRSG | - 3,096 MMBtu/hour | - 850 lb/MWH | - 12-month rolling average | - Clean fuels and energy efficiency |
| - FL-0363 | - 12/04/2017 | - 2-on-1 CCCT with HRSG | - 1,200 MW |  |  |  |
| - NJ-0082 | - 07/18/2014 | - 2-on-1 CCCT with HRSG | - 2,308 MMBtu/hour | - 947 lb/MWH | - 12-month consecutive period, rolled monthly | - Clean fuels and energy efficiency |
| - OH-0352 | - 06/18/2013 | - 2-on-1 CCCT with HRSG | - 5,470 MMBtu/hour | - 840 lb/MWH | - 12-month rolling average | - Clean fuels and energy efficiency |
| - KY-0106 | - 09/30/2016 | - 3-on-1 and 2-on-1 CCCT with HRSG | - 1,700 MW | - 1,069 lb/MWH | - -- | - Clean fuels (1 gr S/100 scf) |
| - TX-0730 | - 04/01/2015 | - 2-on-1 CCCT with HRSG | - 1,100 MW | - 879 lb/MWH b | - -- | - Clean fuels and energy efficiency |
| - GHG limits are given in carbon dioxide equivalent (CO2e). - Calculated from heat rate using EPA Part 75 procedures |  |  |  |  |  |  |

The Department recently proposed BACT limits for GE H-frame turbines for the Dania Beach Energy Center (DBEC) and Okeechobee Clean Energy Center (OCEC), which are operated by Florida Power & Light Company; these limits were 850 lb CO2e per MWh, net, for natural gas, and 1,210 lb CO2e per MWh, net, for ULSD fuel oil.  However, both combined cycle units did not include duct burning and the DBEC project was for a 2-on-1 CCCT and the OCEC project authorized a 3-on-1 CCCT.  Additionally, in 2015 a 2-on-1 combined-cycle facility using 7HA.02 turbines with duct burners was permitted in Texas: the GHG BACT limit for the Colorado Bend Energy Center is 879 lb/MWh, gross, excluding startup and shutdown.  According to the manufacturer’s data, the efficiency value varies by 0.2% between a 2-on-1 CCCT and a 1-on-1 CCCT (based on the lower heating value).  Therefore, the Department proposes a more stringent limitation of 875 lb/MWh, despite the slight variance in efficiency due to the configuration.  To account for the duct firing, the Department’s proposed GHG BACT limit is approximately 3% greater than the GHG BACT limits established for the OCEC and DBEC projects.

    - Summary of Emission Standards for EU No. 001

The emission limits for the combined cycle unit are summarized in Table 13.

Table 13 - Summary of Emission Limits for EU 001.

| Pollutant | Emission Standard a | Basis | Compliance Method b | Averaging Time |
| --- | --- | --- | --- | --- |
| NOX | 2.0 ppmvd @15% O2 | Primary BACT (Normal operating conditions) | CEMS | 24-hr block avg. |
|  | 15 ppmvd @15% O2 (for turbine loads ≥ 75%) | NSPS KKKK, Secondary BACT c |  | 30-operating-day rolling avg. d |
|  | 96 ppmvd @15% O2 (for turbine loads < 75%) |  |  |  |
| CO | 4.3 ppmvd @15% O2 (for turbine loads ≥ 90%) | BACT | Initial and annual stack tests | Three 1-hr runs |
|  | 7.1 ppmvd @15% O2 (for turbine loads < 90%) |  |  |  |
|  | 6.5 ppmvd @15% O2 (when duct firing) |  |  |  |
| PM/PM10/PM2.5 e | 2.0 gr. sulfur/100 SCF natural gas | BACT | Fuel Record Keeping | N/A |
|  | 10 percent opacity (Visible Emissions) |  | Annual Stack Test f | 6-minute block |
| SO2 and SAM | 2.0 gr. sulfur/100 SCF natural gas | BACT | Fuel Record Keeping | N/A |
| GHGs | 875 lb/MWh | Primary BACT | CEMS or fuel-use monitoring g (40 CFR 75) | 12-operating-month rolling avg.h |
|  | 1,000 lb/MWh | NSPS TTTT, Secondary BACT |  |  |
| - NOX and CO concentration emission standards are expressed in parts per million by volume, dry, corrected to 15 percent oxygen, abbreviated as ppmvd @15% O2. - CEMS means continuous emissions monitoring system. - Secondary BACT emission limits are alternative emission limits for specified modes of operation. Demonstrating compliance with the NOX limit in Table 1 of NSPS Subpart KKKK limit shall be sufficient for demonstrating compliance with the Secondary NOX BACT limit. - The composite NSPS KKKK NOX emission limit for periods during which multiple NOX emission standards apply shall be determined in accordance with 40 CFR 60.4380(b)(3). - The fuel sulfur specifications combined with the efficient combustion design and operation of the combustion turbines represent BACT for PM/PM10/PM2.5 and SO2 emissions. Compliance with the fuel specifications, CO standards, and visible emissions (opacity) limit shall serve as indicators of good combustion. - Compliance with the 10% opacity standard shall be demonstrated by conducting 30-minute tests in accordance with EPA Method 9 - Visual Determination of Opacity, at normal operating conditions. Visible emissions during startups, shutdowns, SCR tuning, DLN tuning, and malfunctions shall not exceed 10% opacity, except for up to six 6-minute average periods during a calendar day, which shall not exceed 20% opacity. - GHG monitoring shall be in accordance with 40 CFR 75, which includes options for continuous monitoring of fuel use combined with the use of emissions factors for GHGs, or the use of a continuous emissions monitor for CO2. Calculations of CO2e emissions shall use the 100-year global warming potential values listed in Table A-1 to Subpart A of 40 CFR 98 (2017) (i.e. 1 for CO2, 25 for CH4 and 298 for N2O). The GHG BACT limit applies to the combined cycle unit as an aggregate limit. The Primary GHG BACT limit applies during all operation, except the conditions enumerated in Alternate Standards and Excess Emissions. However, the Secondary GHG BACT limit applies for all operation, including the conditions enumerated in Alternate Standards and Excess Emissions. Compliance with the Secondary GHG BACT limit is demonstrated through compliance with NSPS Subpart TTTT. - The NSPS Subpart TTTT GHG standard applies during all periods of operation. |  |  |  |  |

Alternate Standards and Excess Emissions

The rule states that, “Considering operational variations in types of industrial equipment operations affected by this rule, the Department may adjust maximum and minimum factors to provide reasonable and practical regulatory controls consistent with the public interest.”  Therefore, the Department has the authority to account for these defined periods of operation in determining BACT standards based on the given characteristics of the specific project.  The Department establishes the following requirements for transient operating conditions for the gas turbine/HRSG system.

- Steam Turbine Cold Startup:  During a cold startup of the steam turbine, the Primary NOX and GHG BACT emission limits do not apply to the CTG/HRSG system, for no more than 6 hours during any 24-hour period.  A cold startup of the steam turbine is defined as startup of the 1-on-1 combined cycle system following a shutdown of the steam turbine lasting at least 72 hours.

{Permitting Note: During a cold startup of the steam turbine, the CTG/HRSG system is sequentially brought on line at low load to gradually increase the temperature of the steam turbine and prevent thermal metal fatigue or equipment materials differential expansion damage. Note that shutdowns and documented malfunctions are separately regulated in accordance with the requirements of this condition.}

- CT/HRSG System Cold Startup:  During a cold startup of the CTG/HRSG system, the Primary NOX and GHG BACT emission limits do not apply, for no more than 4 hours during any 24-hour period.  A cold startup of the CTG/HRSG system is defined as a startup of the 1-on-1 combined cycle system following a shutdown of the CTG/HRSG System lasting at least 72 hours.

- CT/HRSG System Warm Startup:  During a warm startup of the CTG/HRSG system, the Primary NOX and GHG BACT emission limits do not apply, for no more than 3 hours during any 24-hour period.  A warm startup of the CTG/HRSG system is defined as startup of the 1-on-1 combined cycle unit following a shutdown for a period exceeding 8 hours but less than 72 hours.

- CT/HRSG System Hot Startup: During a hot startup of the CTG/HRSG system, the Primary NOX and GHG BACT emission limits do not apply, for no more than 2 hours during any 24-hour period.  A hot startup of the CTG/HRSG system is defined as startup of the 1-on-1 combined cycle unit following a shutdown for a period less than or equal to 8 hours.

- Shutdown of Combined-Cycle Operation:  During the shutdown of combined cycle operation, the Primary NOX and GHG BACT emission limits do not apply to any CTG/HRSG system, for no more than 3 hours during any 24-hour period.

- CT/HRSG System Shutdown:  During the shutdown of the CTG/HRSG system, the Primary NOX and GHG BACT emissions limits do not apply to that CTG/HRSG system, for no more than 2 hours during any 24-hour period.

- SCR and DLN Tuning:  The Primary NOX and GHG BACT emission limits do not apply during either an SCR or a DLN tuning session and manufacturer required Full-Speed No-Load Tests (FSNL) trip tests, provided the tuning session is performed in accordance with the manufacturer's specifications or determined best practices.  Prior to performing any tuning session, the permittee shall provide the Compliance Authority with an advance notice that details the activity and proposed tuning schedule.  The notice may be by telephone, facsimile transmittal, or electronic mail.

- Documented Malfunction:  The Primary NOX and GHG BACT emission limits do not apply during a documented malfunction, for no more than 2 hours in any 24-hour period.  To qualify as a “documented malfunction,” the malfunction must be documented within one working day of detection by contacting the Compliance Authority by telephone, facsimile transmittal, or electronic mail.  The permittee shall report to the Department the nature, extent, and duration of the malfunction, and the actions taken to correct the problem.

- Separate Events:  Emissions during the startup, shutdown, SCR tuning, DLN tuning and documented malfunction events listed above are not subject to the Primary BACT standards for NOX or GHGs.  These are considered separate events, and each event may occur independently within any 24-hour period ("any 24-hour period" means a calendar day, midnight to midnight).  Data from the NOX and CO2 CEMS (or fuel use monitor) collected during the events described above will not be used to demonstrate compliance with the Primary BACT emission limits for NOX and GHGs.

- CEMS Data:  Data from the NOX and CO2 CEMS (or fuel use monitor if a CO2 CEMS is not used) collected during the operating conditions described above, during which the Primary NOX and GHG BACT limits do not apply, will be used to demonstrate compliance with the Secondary NOX and GHG BACT emission limits at all times.  All valid emissions data (including data collected during startups, shutdowns, malfunction, SCR tuning and DLN tuning) shall be used to report emissions for the Annual Operating Report.

- BACT Review for Other Sources of Air Emissions

This section contains the BACT analysis for the ancillary equipment, including any facility-wide fugitive emissions pertaining to NOX, CO, PM/PM10/PM2.5, SO2 (including SAM) or GHG.

  - Auxiliary Boiler (EU 002)

As mentioned in the project description, the applicant proposes to install a natural gas fired auxiliary boiler with a maximum heat input of 60 MMBtu/hour.  The auxiliary boiler will be used to provide steam and steam cleaning during construction and initial startup of the CTG/HRSG/STG combined cycle unit.  The auxiliary boiler will also provide steam to the combined cycle unit during cold, warm and hot startups and when the combined cycle unit is being shut down, as well as when steam is not available from the HRSG.  As seen in Table 4, the primary potential emissions are attributed to NOX, CO and GHG.

Identification of Control Technologies

In addition to the control technologies previously identified, the auxiliary boiler may also utilize a flue gas recirculation (FGR) system.  In an FGR system, a portion of the flue gas is recycled from the stack to the burner windbox.  Upon entering the windbox, the gas is mixed with combustion air prior to being fed to the burner.  The FGR system reduces NOX emissions by two mechanisms.  The recycled flue gas comprises combustion products which act as inert during combustion of the fuel/air mixture.  This additional mass is heated in the combustion zone, thereby lowering the peak flame temperature and reducing the amount of thermal NOX formed.  To a lesser extent, FGR also reduces NOX formation by lowering the oxygen concentration in the primary flame zone.  The amount of flue gas recirculated is a key operating parameter influencing NOX emission rates for these systems.  Flue gas recirculation is normally used in combination with specially designed low NOX burners capable of improved flame holding.  When used in combination, these techniques are capable of reducing uncontrolled NOX emissions by 60 to 90 percent.

Discussion of Technically Infeasible Control Options and Ranking of Remaining Options

The boiler will not be operated continuously or at the rated capacity making the addition of control equipment problematic and prohibitively expensive.  The addition of add-on controls such as fabric filters for PM control and FGD for SO2 removal would not result in meaningful emission reductions (less than 1 TPY combined).  CCS is also not feasible for the auxiliary boiler; therefore, the boiler shall utilize clean fuels and energy efficiency as the top control option for GHG.  The limited sulfur content in the natural gas shall also serve as the top control option for limiting emissions in SO2 and SAM.  In addition, the applicant has selected the use of LNBs to minimize emissions of NOX, while maintaining low CO emissions through GCP.

Evaluation of Economic, Environmental, and Energy Impacts of Feasible Technologies

The additional cost would make the add-on control technologies cost prohibitive.  Furthermore, the auxiliary boiler will be used to provide steam to the steam cycle during the startup sequences.

GHG emissions for natural gas firing is 116.9 lb CO2e/MMBtu compared to 163.6 lb CO2/MMBtu for distillate fuel oil firing based on Subpart C of 40 CFR Part 98, Mandatory Greenhouse Gas Reporting.  The emission factors include N2O and CH4 at the equivalent rates.  Therefore, firing natural gas will generate less GHGs than firing ULSD oil.

The applicant also identified that the addition of a SCR system for further NOX control would not be cost effective since the NOX reduction would be limited (less than 3 TPY) resulting in SCR being cost prohibitive.  In addition, operation of the auxiliary boiler would be limited to startup conditions of the CTG/HRSG limiting the amount of operation and greatly decreasing the cost effectiveness of SCR.

Selection of BACT and Rationale

The applicant has proposed for the auxiliary boiler to exclusively fire natural gas to minimize emissions of PM/PM10/PM2.5 and SO2 along with GCP.  The use of LNBs with a NOX emission limit of 0.05 lb/MMBtu is proposed as BACT.  In addition, the proposed auxiliary boiler will only fire natural gas, which is the cleanest GHG emitting fuel compared to other fossil fuels due to its low GHG emissions potential when combusted.  The applicant also proposes a maximum limit on the hours of operation of the auxiliary boiler of 2,000 hours per year.

The RBLC database was reviewed to compare previous BACT determinations for auxiliary boilers.  The results from the RBLC are presented in Table 14.

Table 14 - RBLC BACT Determinations for Natural-Gas Fired Auxiliary Boilers.

| - RBLC ID | - Date | - Heat Input | - Pollutant(s) | - Pollutant Limit | - Control Method |
| --- | --- | --- | --- | --- | --- |
| - FL-0356 | - 03/09/2016 | - 99.8 MMBtu/hour a | - NOX | - 0.05 lb/MMBtu | - DLN |
|  |  |  | - CO | - 0.08 lb/MMBtu | - GCP |
|  |  |  | - SO2, SAM, PM/PM10/PM2.5 | - 2.0 gr S/100 scf | - GCP and low sulfur fuel |
|  |  |  |  | - 10% opacity |  |
| - FL-0363 e | - 12/04/2017 |  | - NOX | - 0.05 lb/MMBtu | - DLN |
|  |  |  | - CO | - 0.08 lb/MMBtu | - GCP |
|  |  |  | - SO2, SAM, PM/PM10/PM2.5 | - 2.0 gr S/100 scf | - GCP and low sulfur fuel |
|  |  |  |  | - 10% opacity |  |
|  |  |  | - GHG | - -- | - Clean fuels and operation limitation |
| - MI-0412 | - 12/04/2013 | - 55 MMBtu/hour | - NOX | - 0.05 lb/MMBtu | - DLN and GCP |
|  |  |  | - CO | - 0.077 lb/MMBtu | - GCP |
|  |  |  | - VOC | - 0.008 lb/MMBtu |  |
|  |  |  | - PM10/PM2.5 | - 0.007 lb/MMBtu |  |
|  |  |  | - GHG b | - 28,514 tons/year | - GCP |
| - OH-0352 | - 06/18/2013 | - 99 MMBtu/hour a | - NOX | - 0.02 lb/MMBtu | - DLN and FGR |
|  |  |  |  | - 1.98 lb/hour |  |
|  |  |  | - CO | - 0.055 lb/MMBtu | - GCP and combustion optimization technology |
|  |  |  |  | - 5.45 lb/hour |  |
|  |  |  | - SAM | - 0.0001 lb/MMBtu | - Natural gas with 0.5 gr S/100 scf |
|  |  |  |  | - 0.011 lb/hour |  |
|  |  |  | - PM10/PM2.5 | - 0.008 lb/MMBtu | - Clean fuels, only natural gas |
|  |  |  |  | - 0.79 lb/hour |  |
|  |  |  |  | - 10% opacity, 6-minute average |  |
|  |  |  | - VOC | - 0.006 lb/MMBtu | - GCP and combustion optimization technology |
|  |  |  |  | - 0.59 lb/hour |  |
|  |  |  | - GHG b | - 11,761 tons/year | - GCP and Energy efficiency |
| - KY-0106 | - 09/30/2016 | - 2 boilers, 40 MMBtu/hour each c,d | - NOX | - 0.011 lb/MMBtu | - DLN |
|  |  |  | - CO | - 0.036 lb/MMBtu | - GCP |
|  |  |  | - SO2 | - 0.0028 lb/MMBtu | - Low sulfur fuel |
|  |  |  | - SAM | - 0.00064 lb/MMBtu |  |
| - KY-0106 | - 09/30/2016 | - 2 boilers, 40 MMBtu/hour each c,d | - PM/PM10/PM2.5 | - 0.005 lb/MMBtu | - GCP |
|  |  |  | - VOC | - 0.0015 lb/MMBtu |  |
|  |  |  | - GHG b | - 67 lb/MMBtu |  |
| - This boiler is limited to 2,000 hours of operation per rolling 12-months. - GHG limits are in terms of carbon dioxide equivalent (CO2e). - These boilers are limited to 4,600 hours of operation each per year. - Each limit is per boiler. - This project was not subject to PSD review for NOX, and the limit was imposed at the applicant’s request, i.e. the limit does not constitute BACT. However, the requested limit is consistent with BACT determinations for similar projects. |  |  |  |  |  |

The Department’s draft determination of BACT for CO for this unit includes the use of GCPs and LNBs, and a limit of 0.08 lb per MMBtu.  Operators will be required to follow the manufacturer’s recommended procedures for tuning and startup/shutdown operations of the boiler.  Compliance will be demonstrated through an initial stack test and subsequent stack tests before each Title V operation permit renewal.  To be consistent with previous BACT determinations, the Department accepts the proposed NOX limit of 0.05 lb/MMBtu.  During startups and shutdowns, the use of natural gas, GCPs, and LNBs provide a meaningful limitation on CO and NOX emissions.  Emissions of PM, SO2 and SAM shall be limited through the use of natural gas with a sulfur content of 2.0 gr S/100 scf natural gas.  The Department also imposes an operational restriction of 2,000 hours per year to minimize emissions of GHG.

As a new fossil fuel steam generator with less than 250 MMBtu/hour, the auxiliary boiler is also subject to Rule 62-296.406, F.A.C., which requires BACT for PM and SO2 and imposes an opacity standard of 20% except for one 6-minute period per 1-hour period during which opacity shall not exceed 27%.  Compliance with the opacity standard will be demonstrated through an annual test for visible emissions.  The auxiliary boiler shall also meet all of the applicable requirements of 40 CFR 60, Subpart Dc which applies to Small Industrial, Commercial, or Institutional Boilers.  Since the boiler will only fire natural gas, the emissions unit shall specifically comply with the reporting and recordkeeping requirements outlined in 40 CFR 60.48c.

  - Emergency Diesel Generator (EU 003) & Fire Pump (EU 004)

The SHCCF will be equipped with a diesel-fired 1,500 kW (kW-electric) emergency generator to support the plant.  The emergency generator will be used to provide electrical power during an emergency situation when electric power from the grid is interrupted or to ensure a safe shutdown of the CTG.  In addition, the emergency generator will be operated for maintenance checks and readiness testing.  A 347 brake-horsepower (BHP) diesel-fired fire pump engine will also be installed, which will be used to provide power to pump water for fire suppression or protection.  The applicant has specified that the emergency generator and fire pump will use ultra-low sulfur diesel (ULSD) fuel with a sulfur content not to exceed 0.0015% with both operated for only 1 to 2 hours per month for maintenance and reliability testing.

Identification of Control Technologies

Similar to the previous combustion sources, possible NOX controls include an SCR, lean NOX catalyst, NOX absorbers and an FGR system.  While CO emissions can be controlled through GCP and a diesel oxidation catalyst.  Energy efficiency and clean fuels can also be utilized to control GHGs, while emissions of PM can be controlled through the use of diesel particulate filters, catalyzed diesel particulate filters or a crankcase ventilation system.  The use of ULSD also reduces the formation of sulfur oxides and particulate sulfates from the diesel engine exhaust.

Discussion of Technically Infeasible Control Options and Ranking of Remaining Options

The installation of controls would not be cost effective given the amount of operation.  Therefore, the only feasible control methods that remain are GCP, clean fuels, and energy efficiency.

Evaluation of Economic, Environmental, and Energy Impacts of Feasible Technologies

The energy efficiency through the regulation of the amount of fuel used is considered to be the only technically feasible CO2 control option for the emergency diesel generator and fire pump engine.

Selection of BACT and Rationale

The applicant has proposed that the use of ULSD oil and GCP to minimize the emissions of PM, PM10, and PM2.5 and SO2, as BACT.  Energy efficiency through the regulation of fuel use to meet the function of the emergency units is the only remaining and feasible control technology and is selected as BACT for the GHG emissions.

The Department accepts the applicant’s proposal as a draft BACT determination and shall specify a fuel sulfur limit of 0.0015% for the ULSD oil.  As seen in Table 15, the selected control methods are consistent with previous BACT determinations for similar units.

Table 15 - RBLC BACT Determinations for Emergency Diesel Generator and Fire Pump Engines.

| - RBLC ID | - Date | - Source Type | - Pollutant | - Pollutant Limit | - Control Method |
| --- | --- | --- | --- | --- | --- |
| FL-0356b | 03/09/2016 | 3,300 kW Emergency Generator | - NMHC + NOX | - 6.4 g/kW-hr | GCP |
|  |  |  | - CO | - 3.5 g/kW-hr |  |
|  |  |  | - PM | - 0.20 g/kW-hr | - ULSD fuel |
|  |  |  | - SO2 | - 0.0015% S in fuel a |  |
|  |  | 422 HP Fire Pump Engine | - NMHC + NOX | - 4.0 g/kW-hr | GCP |
|  |  |  | - CO | - 3.5 g/kW-hr |  |
|  |  |  | - PM | - 0.20 g/kW-hr | - ULSD fuel |
|  |  |  | - SO2 | - 0.0015% S in fuel a |  |
| - FL-0363 b,d | - 12/04/2017 | 3,300 kW Emergency Generator | - NMHC + NOX | - 6.4 g/kW-hr | GCP |
|  |  |  | - CO | - 3.5 g/kW-hr |  |
|  |  |  | - PM | - 0.20 g/kW-hr | - ULSD fuel |
|  |  |  | - SO2 | - 0.0015% S in fuel a |  |
|  |  | 422 HP Fire Pump Engine | - NMHC + NOX | - 4.0 g/kW-hr | GCP |
|  |  |  | - CO | - 3.5 g/kW-hr |  |
|  |  |  | - PM | - 0.20 g/kW-hr | - ULSD fuel |
|  |  |  | - SO2 | - 0.0015% S in fuel a |  |
| - KY-0106 | - 09/30/2016 | 1,000 HP Emergency Engine | - NOX | - 6.4 g/kW-hr | - GCP and manufacturer’s instructions |
|  |  |  |  | - 10.6 lb/hour |  |
|  |  |  | - CO | - 3.5 g/kW-hr |  |
|  |  |  |  | - 5.8 lb/hour |  |
|  |  |  | - PM | - 0.20 g/kW-hr |  |
|  |  |  |  | - 0.33 lb/hour |  |
|  |  |  | - SO2 | - 0.023 lb/hour | - ULSD fuel |
|  |  |  | - SAM | - 0.005 lb/hour |  |
|  |  |  | - VOC | - 1.27 lb/hour | - GCP and manufacturer’s instructions |
|  |  |  | - GHG c | - 1,029 lb/hour |  |
| - Abbreviations: Non-methane Hydrocarbons (NMHC); g/kW-hr means grams per kilowatt-hour. - Equivalent to 15 parts per million of sulfur (on a per gallon basis). - These limits are pursuant to 40 CFR 60, Subpart IIII. - GHG limits are given in terms of carbon dioxide equivalent (CO2e) - This project was not subject to PSD review for NOX, and the limit was imposed at the applicant’s request, i.e. the limit does not constitute BACT. However, the requested limit is consistent with BACT determinations for similar projects. |  |  |  |  |  |

In addition to the BACT determination, the diesel engines will also meet the requirements of NSPS, Subpart IIII, and NESHAP, Subpart ZZZZ, by certifying the performance standards.  These units must be operated according to 40 CFR 60.4211(f) and will maximize efficiency while meeting the required emissions standards, pursuant to NSPS, Subpart IIII:

1,500 kW Emergency Generator

- NMHC + NOX:  6.4 g/kW-hr

- CO:  3.5 g/kW-hr

- PM:  0.20 g/kW-hr

347 BHP Diesel Fire Pump Engine

- NMHC + NOX:  4.0 g/kW-hr

- CO:  3.5 g/kW-hr

- PM:  0.20 g/kW-hr

  - Mechanical Draft Cooling Tower (EU 005)

Steam turbine condenser cooling will be provided by a cooling tower.  The cooling tower is anticipated to be a 6-cell tower design.  The cooling system uses a fan to move air through a re-circulated water system.  A very small amount of the circulating water may be entrained in the air stream and be carried out of the tower as “drift” droplets.  Because the drift droplets contain the same chemical impurities as the water circulating through the tower, the PM constituent of the drift droplets may be classified as an emission.  Therefore, this section contains the BACT analysis for the PM/PM10/PM2.5 emissions, collectively referred as PM emissions from the mechanical draft cooling tower for the Project.

Identification of Control Technologies

The magnitude of the drift loss is influenced by the number and size of droplets produced within the tower, which are determined by the tower fill design, tower design, the air and water patterns, and design of the drift eliminators.

Discussion of Technically Infeasible Control Options and Ranking of Remaining Options

Types of drift eliminator configurations include herringbone (blade-type), wave form, and cellular (or honeycomb) designs.  The cellular units are generally the most efficient.

Evaluation of Economic, Environmental, and Energy Impacts of Feasible Technologies

The applicant has not identified any energy or environmental impacts associated with drift eliminators and proposes a design drift rate of 0.001-percent as a feasible control option for PM.

Selection of BACT and Rationale

As described above, the applicant has proposed a design drift rate of 0.001 percent as the BACT work practice standard for PM emissions for the cooling tower.  However, after further discussion with the Department, the applicant has agreed to accept a more stringent design drift rate of 0.0005 percent.  As seen in Table 16, the selected draft BACT determination for PM is consistent with previous BACT determinations for cooling towers.

Table 16 - RBLC BACT Determinations for Cooling Towers.

| - RBLC ID | - Date | - Source Type | - Flow Rate | - Pollutant | - Pollutant Limit | - Control Method |
| --- | --- | --- | --- | --- | --- | --- |
| - FL-0356 | - 03/09/2016 | 30-cell mechanical draft cooling tower | - 465,815 gal/min | - PM | - Drift rate ≤ 0.0005% | - Mist/drift eliminators |
| - FL-0363 | - 12/04/2017 | 14-cell mechanical draft cooling tower | - 232,908 gal/min |  |  |  |
| - TX-0714 | - 12/19/2014 | - Mechanical draft cooling tower | - -- |  |  |  |
| - OH-0352 | - 06/18/2013 | - 16-cell mechanical draft wet cooling tower | - 322,000 gal/min | - PM10 | - 1.03 lb/hour a, drift rate ≤ 0.0005% |  |
|  |  |  |  | - PM2.5 | - 0.0034 lb/hour b, drift rate ≤ 0.0005% |  |
| - OH-0352 | - 06/18/2013 | - 16-cell mechanical draft wet cooling tower | - 322,000 gal/min | - Visible Emissions | - 10% opacity, 6-minute average |  |
| - KY-0106 | - 09/30/2016 | - 16-cell mechanical draft cooling tower | - 330,000 gal/min | - PM | - Drift rate ≤ 0.0005% |  |
| - Abbreviations: Gallons per minute (gal/min). - There is a second limit of 4.50 tons/year, per rolling 12 months. - There is a second limit of 0.0150 ton/year, per rolling 12 months. |  |  |  |  |  |  |

  - Circuit Breakers (EU 006)

The Project will also include circuit breakers in the power block, which contain a GHG known as sulfur hexafluoride (SF6).  SF6 is an electrical insulator and interrupter in equipment that transmits and distributes electricity.  SF6 has been broadly used in the U.S. due to its dielectric strength and arc-quenching characteristics and has replaced flammable insulating oils.

Identification of Control Technologies

As electrical equipment ages and reaches the end of its operational service life, replacement rather than equipment repair may provide the more attractive SF6 mitigation strategy.  Many equipment manufacturers now guarantee minimal to zero leak rates for new equipment.  Additionally, industry standards recommend that new equipment be built to low leakage limits.

Discussion of Technically Infeasible Control Options and Ranking of Remaining Options

Circuit breakers are required for connection of the electric power generated to the transmission and distribution system through the facilities located on the site.  The use of alternative dielectric fluids is not practical for high voltage applications.  Circuit breakers using SF6 with alarms and periodic inspection are technically feasible for the project.  Therefore, the applicant has selected two circuit breakers that will be designed to have low leakage rates as a feasible control option for GHG.  Circuit breakers using SF6 insulating gas are presently superior in their performance to alternative systems using dielectric oil, high pressure air blast, or vacuum circuit breakers.

Evaluation of Economic, Environmental, and Energy Impacts of Feasible Technologies

The circuit breakers associated with the Project are estimated to contain approximately 100 pounds of SF6 each.  The applicant estimated GHG emissions from the circuit breakers as follows, based on a design leak rate of 0.5 percent per year:

100 lb SF6 ×0.005leakageyear=0.5 lb SF6 per year

0.5 lb SF6year×22,800lb CO2e lb SF6*×1 ton2,000 lb=5.7 tons of CO2e  per year

* GWP factor sourced from Table A-1, 40 CFR 98.

Selection of BACT and Rationale

The Department accepts the use of modern enclosed circuit breakers with a leakage rate of no more than 0.5% as a draft BACT determination for GHG.  Each circuit breaker shall be thoroughly tested, equipped with leakage detection systems, and inspected periodically.  The permittee shall also monitor the circuit breakers remotely and continuously through the plant control system.  Preventive maintenance will be performed in accordance with manufacturer instructions, and the permittee will submit a circuit breaker monitoring plan to the Department after the equipment is selected and placed in service.

  - On-Site Natural Gas Supply

As part of the BACT review for GHG, the Department is assessing possible sources of natural gas leaks from new natural gas-fired power plants (NGPPs).  The new on-site natural gas supply connections, venting during maintenance, and venting during startup and shutdown represent a potential source of fugitive GHG emissions in the form of methane contained in the natural gas.

Identification of Control Technologies

Odor Detection.  Pursuant to 49 CFR 192.625(a), natural gas is required to have an odorant that can be detected so that at a concentration in ambient air of one-fifth of the lower explosive limit, the gas is readily detectable by a person with a normal sense of smell.  The lower explosive limit for methane, the main constituent in natural gas, is 5 percent by volume.  The concentration of natural gas in a leak that is required to be detectable by smell meeting the odorant requirement is 10,000 ppm.

CH4 Leak Detection & Repair (LDAR).  Detection and repair plans have been developed for CH4 leaks from oil refineries, natural gas pipelines, and landfills.  However, CH4 LDAR plans have not been utilized for power plants.  According to a recent study from Purdue University that was published in February of 2017, there is high uncertainty in estimates of CH4 emissions from NGPPs.  Average CH4 emission rates from NGPPs were evaluated to be 140 ± 70 kilograms per hour; which is larger than facility-reported estimates by factors of 21–120.  At NGPPs, the percentage of unburned CH4 emitted from stacks is on average around 0.01–0.14%, which was much lower than respective facility-scale losses of 0.10–0.42% from leaks.  Additionally, calculated throughput-based emission factors derived from the NGPP measurements made in this study were, on average, a factor of 4.4 (stacks) and 42 (facility-scale) larger than industry-used emission factors from the US EPA Greenhouse Gas Reporting Program.  The small number of studies of leak rates of methane from power plants leads to a large uncertainty in emission factors.

Discussion of Technically Infeasible Control Options and Ranking of Remaining Options

Unlike NGPPs, various chemical manufacturing facilities are required to complete a LDAR plan due to an applicable NESHAP or NSPS requirement.  The pertinent LDAR programs utilize EPA Method 21 to measure the concentration of VOC at a connector or valve to determine if the “leak detection concentration” is exceeded to warrant a repair.  The LDAR plans outlined in the NSPS provisions include a leak detection concentration of 10,000 ppm when measuring leaks, which is the same concentration that an odorant can be detected.  The applicant evaluated an average number of valves and connectors in the chemical manufacturing sites to be well over 10,000, in comparison to an estimated 230 valves and connectors for the Project.  EPA has indicated that a quarterly monitoring program would result in a control efficiency of approximately 67%.  Therefore, by assuming 67% control efficiency and utilizing the emission factors contained in 40 CFR Part 98, Subpart W, the applicant evaluated that implementing a LDAR plan would only result in a decrease of about 16 TPY of CO2e.

Evaluation of Economic, Environmental, and Energy Impacts of Feasible Technologies

SHEC has selected a best management practices program involving either LDAR or odorant detection procedures as feasible control technologies.  Since plant personnel routinely monitor plant operations through maintenance inspections, the observation of natural gas odorants would not require any additional cost.  While odorants are highly effective in the observation of leaks, it is unknown what the actual control effectiveness may be.

The implementation of a LDAR program would require either plant personnel or a contractor using calibrated instrumentation or a soap solution.  The applicant has deemed a LDAR plan to be time consuming as the detection would occur at the connector/valve where a leak may occur and there are an estimated 230 valves and connectors for the Project.  The applicant has noted that a considerable amount of documentation is required and an estimated cost for a quarterly LDAR program is approximated to exceed $30,000 per year.  By including the allowance cost of the current European Union price for CO2 as $14 per ton, the applicant computed a cost effectiveness for a quarterly LDAR program to be over $1,000 per ton of CO2e.

Selection of BACT and Rationale

The applicant has selected the odorant detection method as BACT for GHG emissions.  An odorant detection program meeting the following permit condition is proposed:

“Piping components used for the transmission of natural gas to the combustion turbine and duct burners of the HRSGs shall be inspected quarterly for potential leaks through odor detection and visible inspection.  Any leaks identified by odor must be evaluated and repaired as soon as practical.  Records of inspection, detected leaks, and repairs (including action taken and duration) shall be available upon request.”

The Department rejects the proposed BACT determination and notes that the emission factors contained in 40 CFR Part 98, Subpart W, are in reference to a study that was published in 1996 from well-site natural gas treatment processes.  Therefore, the Department would like to gather specific on-site data to better represent the natural gas leakage found in NGPPs.  Similar to the GHG BACT determination provided for the DBEC project, in lieu of specified LDAR requirements, the permittee will calculate a facility-specific methane loss rate from the gas entering the plant and the gas combustion rates of the permitted emissions units.  The permittee will be required to measure the following: (1) gas flow at the inlet to the SHCCF gas yard, (2) gas consumed by the SHCCF combustion turbine (EU No. 001), (3) gas consumed by the duct burner, and (4) gas consumed by the SHCCF auxiliary boiler (EU No. 002).  At the end of each calendar month, the permittee shall calculate the amount of methane difference for the month.  The amount of methane difference shall be calculated as the difference between the gas flow into the SHCCF (Item 1) and the gas consumed by the emissions units of the SHCCF (Items 2, 3, and 4).  Estimates of any natural gas required to be evacuated for safety reasons, based on engineer calculations, may be deducted from the monthly methane difference.  The permittee will be required to record and calculate these rates monthly and report annually to the Department.  The purpose of this alternate work practice standard is to confirm tight-fitting components consistent with a well-maintained system.

- Air Quality Analysis

As a part of this review, Rules 62-212.400(7) and 62-212.400(5), F.A.C., require the applicant to perform a current air quality analysis and a source impact analysis for each PSD applicable pollutant.  The emission rates in (see Table 5) are based on the worst-case operating scenario for each pollutant and indicate that SO2, NOX, CO, PM, PM10, and PM2.5 are subject to review.

  - Current Air Quality Analysis

    - State Level

The State of Florida has generally good ambient air quality and is currently in attainment of all national ambient air quality standards (NAAQS) in the vicinity of this project.  As can be seen in Figure 7, Florida’s air monitor design values are well within attainment of the NAAQS for ozone, SO2, NO2, CO, PM10 and PM2.5.

In addition, air pollutant emissions have seen a significant decrease (Figure 8).  Statewide actual annual emissions from stationary sources have decreased significantly from 2000 to 2016; specifically, PM emissions have decreased 76%, SO2 emission 88%, NOX emissions 71%, and CO emissions 56% since 2000.  These emission decreases have occurred in spite of the population of Florida increasing by over four and a half million, or 28%, through the same period.  A variety of national rules that are currently being implemented are expected to maintain these lower levels or even reduce them further in the foreseeable future.

Figure 7.  Florida Ambient Air Monitoring Network Design Values for 2014-2016 (design values are based on expected exceedances).

Figure 8.  Actual Annual Emissions of CO, NOX, SO2, and PM in Florida from 2000 to 2016.

    - County Level

Pasco County, 2016 population of 512,368, is rural in nature near the project site.  The nearest city to the project site is New Port Richey, about 2 km southwest of the project site, with a population of approximately 16,000.  Table 17 includes emissions of CO, NOX, SO2, and PM from stationary sources in Pasco County in 2007 and 2016.  Emissions of these pollutants in the county have decreased significantly, even more than the trend in statewide stationary source emissions.

Table 17 - Actual annual emissions of CO, NOX, SO2, and pm by stationary sources in PASCO county, Florid.

| Pollutant | 2007 Actual Emissions (TPY) | 2016 Actual Emissions (TPY) | Percent Change |
| --- | --- | --- | --- |
| CO | 718.5 | 211.7 | -70.5% |
| NOX | 7,221.0 | 3,590.7 | -50.3% |
| SO2 | 27,077.3 | 44.5 | -99.8% |
| PM | 993.3 | 189.0 | -81.0% |

    - Nearby Sources

Pasco County contains few significant stationary sources of air pollutants.  Most existing sources within Pasco County are generally very small and outside of population centers, providing for clean ambient air.  Table 18 provides some perspective on the relative size of the project and nearby sources by comparing its maximum potential future emissions of CO, NOX, SO2, and PM with the actual 2016 emissions from the five largest sources of each pollutant within 50 km (see Figure 9).

Table 18 - ACTUAL 2016 EMISSIONS OF CO, NOX, SO2, and PM FROM THE LARGEST STATIONARY SOURCES NEAR THE PROJECT SITE.

| Owner | Facility Name | County | 2016 CO Emissions (TPY) |
| --- | --- | --- | --- |
| CEMEX Construction Materials Florida | CEMEX Brooksville South Cement Plant | Hernando | 696.7 |
| Envirofocus Technologies | Envirofocus Technologies | Hillsborough | 339.7 |
| Florida Power Development | Brooksville Power Plant | Hernando | 278.3 |
| Shady Hills Energy Center, LLC | This Project | Pasco | 187.5 |
| Duke Energy Florida | Anclote Power Plant | Pasco | 150.6 |
| Florida Gas Transmission Company | FGTC Station No. 27, Hillsborough | Hillsborough | 36.3 |

| Owner | Facility Name | County | 2016 NOX Emissions (TPY) |
| --- | --- | --- | --- |
| Duke Energy Florida | Anclote Power Plant | Pasco | 2,641.4 |
| Pasco County | Pasco County Resource Recovery Facility | Pasco | 1,177.5 |
| CEMEX Construction Materials Florida | CEMEX Brooksville South Cement Plant | Hernando | 982.9 |
| Florida Power Development | Brooksville Power Plant | Hernando | 366.7 |
| Quantum Pasco Power | Quantum Pasco Power | Pasco | 341.0 |
| Shady Hills Energy Center, LLC | This Project | Pasco | 126.2 |

| Owner | Facility Name | County | 2016 SO2 Emissions (TPY) |
| --- | --- | --- | --- |
| Mosaic Fertilizer | Mosaic Fertilizer – Plant City | Hillsborough | 1,738.8 |
| Envirofocus Technologies | Envirofocus Technologies | Hillsborough | 266.1 |
| Shady Hills Energy Center, LLC | This Project | Pasco | 90.9 |
| Pasco County | Pasco County Resource Recovery Facility | Pasco | 29.1 |
| CEMEX Construction Materials Florida | CEMEX Brooksville South Cement Plant | Hernando | 17.3 |
| Duke Energy Florida | Anclote Power Plant | Pasco | 11.1 |

| Owner | Facility Name | County | 2016 PM Emissions (TPY) |
| --- | --- | --- | --- |
| Duke Energy Florida | Anclote Power Plant | Pasco | 151.4 |
| Ardent Mills | Ardent Mills | Hillsborough | 93.0 |
| Shady Hills Energy Center, LLC | This Project | Pasco | 76.0 |
| CEMEX Construction Materials Florida | CEMEX Brooksville South Cement Plant | Hernando | 59.4 |
| Florida Power Development | Brooksville Power Plant | Hernando | 42.4 |
| Mosaic Fertilizer | Mosaic Fertilizer – Plant City | Hillsborough | 42.1 |

Figure 9.  Reference Map for the Shady Hills Generating Station Project including the Largest Sources of Air Pollutants within 50 km.

    - Monitors

Florida has a robust ambient air monitoring network operated by the Florida Department of Environmental Protection (Department) and its partners (local air pollution control programs).  The network monitors concentrations of each of the criteria pollutants and includes monitors in Florida counties containing 92% of the population.  The representative monitors chosen to evaluate the existing air quality in the area are described in Table 19 and are used to satisfy the preconstruction monitoring requirements for PSD review contained in Rule 62-212.400(7), F.A.C.  These monitors are the nearest monitors to the project site that are in a similar setting (consideration was given to proximity to coast and urban areas).  Several of the chosen monitors are located near or downwind of urban Tampa, FL, providing conservative estimates for the project, which is located in a more rural area. Design values at these monitors are well below the applicable NAAQS.

Table 19 - CRITERIA POLLUTANT DESIGN VALUES FOR FLORIDA DEP AMBIENT AIR MONITOR CHOSEN TO CONSERVATIVELY CHARACTERTIZE THE PROJECT AREA.

| Pollutant | Location (Site Number) | Averaging Period | Ambient Concentration |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Compliance Period | Value | Standard | Unitsa |
| CO | Sydney, FL | 1-hour | 2016 | 0.6b | 35c | ppm |
|  | (057-3002) | 8-hour | 2016 | 0.5b | 9c | ppm |
| NO2 | Tampa, FL | 1-hour | 2014-2016 | 31 | 100d | ppb |
|  | (057-1065) | Annual | 2014-2016 | 4.2 | 53e | ppb |
| SO2 | Sydney, FL (057-3002) | 1-hour | 2014-2016 | 13 | 75j | ppb |
|  |  | 24-hour | 2016 | 1b | 140c | ppb |
|  |  | Annual | 2016 | 0.26 | 30e | ppb |
| PM10 | Azalea Park, FL | 24-hour | 2016 | 24b | 150g | µg/m3 |
|  | (103-0018) |  |  |  |  |  |
| PM2.5 | Azalea Park, FL | 24-hour | 2014-2016 | 15 | 35h | µg/m3 |
|  | (103-0018) | Annual | 2014-2016 | 6.7 | 12.0i | µg/m3 |
| Ozone | San Antonio, FL | 8-hour | 2014-2016 | 0.061 | 0.070f | ppm |
|  | (101-0005) |  |  |  |  |  |
| - Units are in: micrograms per cubic meter (μg/m3); parts per billion (ppb); or parts per million (ppm). - Exceedance based standard - Maximum 2016 concentration given for comparison - Not to be exceeded more than once per year. - Three-year average of the annual 98th percentile, daily maximum 1-hour average concentration. - Arithmetic annual mean. - Three-year average of the annual 98th percentile, daily maximum 8-hour average concentration. - Not to be exceeded more than once per year on average over a three-year period. - Three-year average of the annual 98th percentile, daily 24-hour average concentrations. - Three-year average of the arithmetic annual means. - Three-year average of the annual 99th percentile, daily maximum 1-hour average concentration. |  |  |  |  |  |  |

  - Source Impact Analysis

A source impact analysis is required by Rule 62-212.400(5), F.A.C. to demonstrate that allowable emission increases from the proposed project will not cause or contribute to a violation of any NAAQS or PSD increment as defined in 40 CFR Part 50 and 40 CFR 52.21(c) respectively.  This analysis is performed using approved air quality models and analysis techniques as described in Appendix W (Guideline on Air Quality Models) of 40 CFR 51.

    - Dispersion Modeling Approach

Dispersion modeling for the source impact analysis typically occurs in six steps:

- Class II SIL Analysis: Initial modeling is performed to determine if the maximum predicted concentrations due to the new source(s) alone are likely to cause a significant impact on ambient air quality.  Modeling is performed using five years of actual meteorological data and the highest resultant concentrations are compared to the EPA suggested SILs for each pollutant that is subject to PSD review. For each pollutant that is less than the SIL, steps two and three are skipped.  For all others, refined NAAQS and Class II increment analyses are required.

- NAAQS Analysis: Cumulative source modeling is performed for each pollutant and averaging time that exceeded the Class II SIL.  This analysis includes modeled emissions from all nearby sources that are considered to have a significant impact and a non-modeled background concentration intended to represent all other sources of pollutants.  The resulting concentrations are evaluated on a receptor-by-receptor basis for comparison to each NAAQS using the following methods:

- CO 1-Hour Average: Highest of yearly second-high 1-hour average concentrations;

- CO 8-Hour Average: Highest of yearly second-high 8-hour average concentrations;

- NO2 1-Hour Average: 5-year average of the yearly 8th-high daily maximum 1-hour average concentration;

- NO2 Annual Average: Highest annual mean over five years;

- PM2.5 24-Hour Average: 5-year average of the yearly 8th-high 24-hour average concentration;

- PM2.5 Annual Average: 5-year average of the annual mean;

- PM10 24-Hour Average: 6th-high 24-hour concentration over five years;

- SO2 1-Hour Average: 5-year average of the yearly 4th-high daily maximum 1-hour average concentration;

- SO2 24-Hour Average: Highest of yearly second-high 24-hour average concentrations;

- SO2 Annual Average: Highest annual mean over five years.

- Class II Increment Analysis:  Cumulative source modeling is performed with nearby PSD increment consuming or expanding sources.  For annual averaging periods, the highest five-year annual average is compared to the increment.  For all other short-term averaging periods, the 2nd-highest concentration from each of five years is compared.

- Class I SIL Analysis:  A Class I analysis is typically required if a source is within 200 km of a Federal Class I area.  Almost all of Florida is within this distance of at least one Class I area and therefore an analysis is always required.  This analysis is identical to the Class II SIL analysis except that the SILs are smaller and only evaluated within the boundaries of the Class I area.

- Class I Increment Analysis:  For those pollutants that exceed the applicable Class I SIL, an increment analysis is required.  Again this analysis mirrors the Class II increment analysis except with smaller increments that are only evaluated within the Class I area.

- Class I AQRV Visibility and Deposition Analysis:  A visibility and deposition analysis is required for any Class I area that does not pass a specific screening criterion.  This analysis is typically performed with CALPUFF.

    - Models

The AERMOD (AMS (American Meteorological Society)/EPA Regulatory Model) modeling system is a near-field, Gaussian, steady-state plume dispersion model that simulates pollutant dispersion methods based on planetary boundary layer turbulence structure and scaling concepts, including the treatment of both surface and elevated sources, and both simple and complex terrain.  The system is comprised of the AERMET meteorological processor, the AERMAP terrain processor, and the actual AERMOD model.  AERMOD was commissioned by EPA for regulatory use and was developed by AERMIC (AMS/EPA Regulatory Model Improvement Committee) from 1991 to 2005 when EPA officially promulgated it as the preferred regulatory model.  Between 2005 and 2016 the program has undergone 12 major updates.  It is the recommended model for assessing air quality impacts up to 50 km from the source.

CALPUFF is a multi-layer, multi-species, non-steady-state, puff dispersion model that simulates the effects of time- and space-varying meteorological conditions on pollution transport, transformation and removal.  It is capable of evaluating sub-grid scale effects as well as longer range effects such as pollutant removal, chemical transformation, and visibility.  It is approved for use on scales of tens to hundreds of kilometers and is generally utilized for long-range transport between 50 and 300 km from the source.

For this project, AERMOD was used to evaluate the Class II SILs for PM2.5, PM10, NO2, SO2, and CO; CALPUFF was used to evaluate AQRVs in Class I areas.

    - Class II SIL Analysis

The general modeling approach for the SIL, NAAQS, and PSD increment analyses followed current EPA and the Department’s modeling guidance.  The applicant used a series of specific model features recommended by EPA that are referred to as the regulatory options and the latest version of each model component available at the time of the analysis.  It should be noted that ambient concentrations of modeled pollutants in the area near the project site are significantly below the applicable NAAQS for each and therefore use of SILs in this case satisfies Section 165(a)(3) of the CAA.  The applicant has chosen to use more recent SIL values for PM2.5 developed by EPA, which EPA believes is sufficient to conclude whether the proposed project will cause or contribute to any violation of the PM2.5 NAAQS.

      - Meteorological Data

The AERMET v.16216 meteorological input used with the AERMOD v.16216R model consisted of a concurrent 5-year period of hourly surface-weather observations from the National Weather Service (NWS) Automated Surface Observing System (ASOS) station at Hernando County Airport (BKV) and upper air sounding (RAOB) data from Tampa International Airport (TBW).  This data was compiled by the Department for the period 2012 – 2016 and included land cover and land use parameters derived from the 1992 National Land Cover Database (NLCD) by AERSURFACE v.13016 and 1-minute ASOS wind data extracted by AERMINUTE v.11059 with a minimum wind speed threshold of 0.5 meters per second (m/s). The ASOS station at BKV is located approximately 15 km NNE of the project site and is the closest primary weather station.  Table 20 summarizes the annual average land use parameters for the project site and the ASOS location.  These parameters were derived seasonally and for twelve 30-degree wind direction sectors.  Given the similarity of the land surrounding both sites, the ASOS data are considered to be representative of the project site.

Table 20 - ANNUAL AVERAGE LAND USE PARAMETER COMPARISON BETWEEN THE BKV ASOS STATION AND THE PROJECT SITE.

| Location | Albedo | Bowen Ratio | Surface Roughness |
| --- | --- | --- | --- |
| BKV ASOS Station | 0.16 | 0.68 | 0.115 |
| Shady Hills Project Site | 0.16 | 0.59 | 0.241 |

      - Building Downwash

Building downwash effects were simulated for 4 structures at the facility. For each stack, direction-specific building heights and maximum projected widths were calculated by the Building Profile Input Program (BPIP v.04274) incorporating the Plume Rise Model Enhancement (PRIME) algorithm developed by the Electric Power Research Institute (EPRI).  This wind direction-specific information was then output to AERMOD which simulates aerodynamic downwash based on stack and building locations and heights.

      - Receptors and Terrain

A combination of fence line, near-field, and far-field receptors was chosen for predicting maximum concentrations in the vicinity of the project for comparison to the Class II SILs.  Receptor locations used in the modeling analysis were based on Universal Transverse Mercator (UTM) coordinates from Zone 17 North, North American Datum 1983 (NAD83).  The modeling domain was set as a 4 km X 4 km grid centered at UTM 17N east and north coordinates of 347,465 and 3,138,694 meters, respectively.  A discrete Cartesian grid of 1,924 receptors was located at the following intervals and distances:

- 50 m spacing along the property boundary and fence line;

- 100 m spacing from the fence line to 2,000 m from the domain origin;

- 500 m spacing from 2,000 m to 4,000 m from the domain origin.

This receptor placement is considered to be sufficient to resolve the areas of highest concentration in Florida’s flat terrain.

Base elevations were extracted from the US Geological Survey’s (USGS) 1-second National Elevation Dataset (NED) by AERMOD’s terrain processor AERMAP v.11103 for all receptors and sources.

      - Onsite Modeled Sources

The SIL analysis evaluates whether the increase in potential emissions from the new project alone are capable of significantly contributing to a modeled NAAQS exceedance.  The onsite modeled sources for the project include the proposed combustion turbine/heat recovery steam generator (CT/HRSG) and a 6-cell mechanical draft cooling tower.  The CT/HRSG was modeled with nine different sets of parameters for each pollutant in order to identify the worst-case scenarios: three ambient temperatures (30°F, 59°F, and 95°F) and three loads (100% with duct burning, 100% percent load without duct burning, and minimum emission compliance load or MECL.  The MECL is approximately 25%, but varies with ambient temperature.  The worst-case scenario differed for each pollutant, and thus all scenarios are summarized in Table 21.

The CT/HRSG is expected to operate continuously as a baseload unit. To avoid shutdowns and cold startups, the unit will operate at MECL load instead of shutting down when possible. Therefore, because very few startups/shutdowns are anticipated for this unit with typical operation, startups/shutdowns are not included in the modeling. The load analysis as described above covers both full load and MECL, so all scenarios expected with typical operation of the unit are included in the modeling.

Table 21 - Modeling parameters for new source associated with the project.

| Stack Parameter | Units | 100% Load w/ duct burning |  |  | 100% Load |  |  | MECL |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 30°F | 59°F | 95°F | 30°F | 59°F | 95°F | 30°F | 59°F | 95°F |
| Height | ft | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |
| Diameter | ft | 23.0 | 23.0 | 23.0 | 23.0 | 23.0 | 23.0 | 23.0 | 23.0 | 23.0 |
| Exit Temp | °F | 159.7 | 161.1 | 167.3 | 165.7 | 166.1 | 175.0 | 151.3 | 151.9 | 161.6 |
| Exit Velocity | ft/sec | 67.5 | 65.2 | 62.9 | 68.1 | 66.2 | 65.6 | 32.1 | 31.4 | 35.8 |

The PM10 modeling also included the cooling tower.  Emissions from the cooling tower are based on a Total Dissolved Solids (TDS) concentration that results in maximum PM emissions.

      - Secondary PM2.5

Secondary PM2.5 is formed in the atmosphere by chemical reactions mainly involving the precursor pollutants NOX and SO2.  Appendix W to 40 CFR Part 51 recommends a two-tiered demonstration approach for addressing single-source impacts on the formation of secondary PM2.5.  The first tier involves use of relationships between precursor emissions and ambient concentrations of ozone and PM2.5 that have been developed from modeling to evaluate a source’s impacts.  The second tier involves application of a photochemical grid model to evaluate secondary impacts.

A Modeled Emission Rate for Precursors (MERP) is the level of emissions (tons per year) of a precursor that would result in the formation of a secondary pollutant at a concentration equal to its significant impact level (SIL), the SIL being the level at which a concentration is considered to be a statistically significant change.  MERPs are a tier 1 screening method that can be used to estimate a project’s secondary PM2.5 impacts.  Although the applicant used the most conservative MERP values for the Eastern US from EPA’s original MERP guidance, the Department completed the analysis using updated MERP values provided by EPA in an errata memorandum to estimate the project’s secondary PM2.5 impacts (see Table 22).

Table 22 - Modeled emission rates for precursors, and emissions and secondary pm2.5 impacts for the project.

| MERPs and Emissions (TPY) | NOX | SO2 | Class II SILs | Project Secondary Impacts |
| --- | --- | --- | --- | --- |
| 24-hour PM2.5 MERPs | 2,295 | 628 | 1.2 µg/m3 | 0.240 |
| Annual PM2.5 MERPs | 10,144 | 4,013 | 0.2 µg/m3 | 0.007 |
| Project Emissions | 126.2 | 90.9 | - | - |

These secondary PM2.5 impacts were added to the primary PM2.5 impacts before comparison to the SIL.

      - Results

The results of the SIL modeling summarized in Table 23 indicate that refined cumulative source modeling is not required for any pollutants.

Table 23 - MAXIMUM PREDICTED AIR QUALITY IMPACTS FOR THE PROJECT, COMPARED TO THE CLASS II SILS.

| Pollutant | Averaging Time | Max Impact (μg/m3) | Secondary PM2.5 (μg/m3) | SIL (μg/m3) | Percent of SIL | Significant Impact? |
| --- | --- | --- | --- | --- | --- | --- |
| PM2.5 | Annual 24-Hour | 0.08 | 0.007 | 0.2 | 44% | No |
|  |  | 0.83 | 0.240 | 1.2 | 89% | No |
| PM10 | Annual | 0.09 | - | 1 | 9% | No |
|  | 24-Hour | 1.16 | - | 5 | 23% | No |
| SO2 | Annual | 0.09 | - | 1 | 9% | No |
|  | 24-Hour | 0.94 | - | 5 | 19% | No |
|  | 3-Hour | 2.49 | - | 25 | 10% | No |
|  | 1-Hour | 2.36 | - | 7.86 | 30% | No |
| NO2 | Annual | 0.11 | - | 1 | 11% | No |
|  | 1-Hour | 3.05 | - | 7.52 | 41% | No |
| CO | 8-Hour | 5.2 | - | 500 | 1% | No |
|  | 1-Hour | 8.4 | - | 2,000 | 0.4% | No |

    - Class I Analysis

All areas not explicitly designated as Class I in 40 CFR 81 Subpart D (such as national parks and wilderness areas) are considered Class II areas.  While the NAAQS apply to all areas equally, more stringent SILs and increments exist for Class I areas.  A Class I analysis is required for any project that may affect a Federal Class I area.  The Class I area closest to the project site is Chassahowitzka National Wilderness Area (CNWA), 28.2 km to the north-northwest (see Figure 9).  All other Class I areas are more than 200 km away from the project site.

      - Class I SIL analysis

A screening analysis was performed using AERMOD to evaluate the annual, 24-hour and 3-hour SO2 SILs; the annual and 24-hour PM2.5 and PM10 SILs; and the annual NO2 SIL.  AERMOD was run using a ring of receptors located 28.2 km from the project site (the distance to the nearest Class I area) and spaced at 1-degree intervals.  For 24-hour and annual PM2.5, because the applicant did not provide an analysis of secondary PM2.5 impacts for Class I areas, the Department estimated the project’s secondary impacts using the MERP values in Table 24.  These secondary impacts were added to the primary impacts in AERMOD before comparison to the SIL.

Table 24 - Modeled emission rates for precursors, and emissions and secondary pm2.5 impacts for the project.

| MERPs and Emissions (TPY) | NOX | SO2 | Class I SILs | Project Secondary Impacts |
| --- | --- | --- | --- | --- |
| 24-hour PM2.5 MERPs | 2,295 | 628 | 0.27 µg/m3 | 0.054 |
| Annual PM2.5 MERPs | 10,144 | 4,013 | 0.05 µg/m3 | 0.002 |
| Project Emissions | 126.2 | 90.9 | - | - |

The results in Table 25 show that the maximum impacts are below all SILs; therefore, a cumulative Class I increment analysis is not required.

Table 25 - MAXIMUM PREDICTED AIR QUALITY IMPACTS 28 KM FROM THE PROJECT SITE COMPARED TO THE CLASS I SIL.

| Pollutant | Averaging Time | Max Impact (μg/m3) | Secondary PM2.5 (μg/m3) | SIL (μg/m3) | Percent of SIL | Significant Impact? |
| --- | --- | --- | --- | --- | --- | --- |
| PM2.5 | Annual | 0.004 | 0.002 | 0.05 | 12% | No |
|  | 24-Hour | 0.05 | 0.054 | 0.27 | 39% | No |
| PM10 | Annual | 0.005 | - | 0.2 | 3% | No |
|  | 24-Hour | 0.06 | - | 0.3 | 20% | No |
| SO2 | Annual | 0.01 | - | 0.1 | 10% | No |
|  | 24-Hour | 0.09 | - | 0.2 | 45% | No |
| NO2 | 3-Hour | 0.29 | - | 1 | 29% | No |
|  | Annual | 0.009 | - | 0.1 | 9% | No |

    - Ozone Analysis

Ozone is a secondarily formed pollutant that is known to be caused by the regional emissions of VOC and NOX in combination with certain meteorological conditions (temperature, humidity, solar insolation, etc.).  Projects with VOC or NOX potential emissions increases of 40 TPY or greater are required to perform a source impact analysis for ozone.  The applicant estimated maximum annual potential VOC and NOX emissions from the project to be 32.0 and 126.2 TPY respectively and is therefore required to provide an analysis for ozone.  Just as for secondary PM2.5, the applicant must use a two-tiered demonstration to analyze the project’s impacts on secondary ozone formation.  Because the applicant did not provide an ozone analysis, the Department performed one for the project using the most conservative MERP values for the Eastern US from EPA guidance to estimate the project’s secondary ozone impacts (see Table 26).

Table 26 - Modeled emission rates for precursors, and emissions and secondary ozone impacts for the project.

| MERPs and Emissions (tons per year) | NOX | VOC | Project Secondary Impacts |
| --- | --- | --- | --- |
| 8-hour Ozone | 170 | 1,159 | 0.77 ppb |
| Project Emissions | 126.2 | 32.0 | - |

These secondary ozone impacts are below the SIL.  Therefore, the Department has reasonable assurance that the project will not significantly contribute to or cause any violation of the ozone NAAQS.

  - Additional Impacts Analysis

The applicant is required by Rule 62-212.400(8), F.A.C. to provide an analysis of the project’s potential impacts on visibility, soils, vegetation, and wildlife due to the proposed project or any general commercial residential, or industrial growth associated with the project.

    - Growth

The 18 to 24 month construction phase of this project will require approximately 230 workers during that time, with many workers commuting to the site.  Once construction is complete, only about 11 to 15 permanent personnel will remain.  This is a small fraction of the population in the area and no air quality impacts are expected from the small increase in vehicular traffic.  Operation of the facility is not expected to result in any commercial or industrial growth in the area because existing commercial and industrial infrastructure is more than sufficient to meet the needs of the facility.

    - Soils, Vegetation, and Wildlife

Emissions of pollutants have the potential to negatively affect soils, vegetation and wildlife near sources.  The project’s maximum predicted air quality impacts are less than the NAAQS which were established to protect both public health and welfare. In addition, secondary NAAQS have been set to protect against visibility impairment and damage to animals, crops, vegetation, and buildings.  All ambient air quality impacts from the project have been predicted to remain well below the applicable secondary NAAQS and therefore the impact on soils, vegetation, and wildlife is expected to be negligible.

    - Class I AQRV

The Federal Land Manager (FLM) for every Class I area that may be affected by a source is charged with protecting all air quality related values (AQRV), including visibility and deposition, in that area.  An AQRV analysis is generally required for all PSD projects and the applicant completed such an analysis for this project.

The applicant is required to evaluate the potential impact of the proposed project on all applicable AQRV for any portion of a Class I area located within 50 km of the project and any area beyond 50 km that does not meet the FLAG2010 screening criteria.  The analysis calculates the Q/D ratio, where Q is potential project emissions in TPY of SO2, NO2, particulate matter, and sulfuric acid mist, and D is the distance in kilometers to the Class I area.  For sources with a Q/D ratio of 10 or less, no further AQRV analysis is required.  The proposed project is located within 50 km of all of the CNWA Class I area.  The Q/D screening test was applied for all other Class I areas located with 300 km of the project.  As seen in Table 27, Class I AQRV impact analyses are not required for these Class I areas.

Table 27 - AQRV Analysis Screening Results

| Potential Emissions Increase based on Maximum Allowable Emissions (TPY) |  |  |  |  | Class I Area | Minimum Distance in km (d) | FLAG Screening Ratio Q/d | AQRV Analysis Required? |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| NOx | SO2 | SAM | PM10 | Total (Q) |  |  |  |  |
| 126.2 | 90.9 | 15.2 | 63.1 | 295.4 | Everglades | 295.3 | 1.0 | No |
|  |  |  |  |  | Bradwell Bay | 273.9 | 1.1 | No |
|  |  |  |  |  | Okefenokee | 244.4 | 1.2 | No |
|  |  |  |  |  | St. Marks | 234.3 | 1.3 | No |

      - Visibility Analysis

For distances within 50 km, visibility impairment may take the form of a distinct plume from the source. FLAG guidance requires the use of VISCREEN to assess plume impacts on visibility against a sky background and a terrain background, both looking into and out from the Class I area.

In interpreting results from VISCREEN for CNWA, results looking out from the Class I area can be excluded because these results are only applicable in areas where an integral vista is being protected, and Florida has no integral vistas. The VISCREEN Workbook also indicates that it is reasonable to exclude results against a terrain background if there is no possibility of viewing distant terrain in the Class I area. As seen in Figure 9, CNWA is in a coastal area with no terrain features, with most receptor points having an elevation ranging from zero to only five feet.  Therefore, it was determined that views of distant terrain are not possible at CNWA, and plume impacts against a terrain background are excluded.

The applicant performed two levels of screening with VISCREEN to determine if there could be any significant impacts in the Class I area.  Inputs to VISCREEN are listed in Table 28.

Table 28 - INPUTS USED IN VISCREEN FOR THE LEVEL 1 AND LEVEL 2 VISIBILITY ANALYSIS.

| Model Input | Units | Level 1 | Level 2 |
| --- | --- | --- | --- |
| Particulates | lb/hr | 14.8 | 14.8 |
| NOX | lb/hr | 28.1 | 28.1 |
| Primary NO2 | lb/hr | 0 | 0 |
| Soot | lb/hr | 0 | 0 |
| Primary SO4 | lb/hr | 4.0 | 4.0 |
| Distance to observer | km | 28.2 | 28.2 |
| Distance to closest point | km | 28.2 | 28.2 |
| Distance to farthest point | km | 46 | 46 |
| Background Visual Range | km | 177.8 | 86.7 |
| Wind speed | m/s | 1 | 1 |
| Stability Index | - | 6 (F) | 6 (F) |
| Ozone Background | ppm | 0.04 | 0.04 |
| Plume Offset Angle | degrees | 11.25 | 11.25 |
| Delta E threshold | - | 2.00 | 2.00 |
| Green contrast threshold | - | 0.05 | 0.05 |

The Level 1 analysis assumes the worst possible dispersion condition (combination of wind speed and stability class), regardless of actual meteorology at the site.  Level 1 also assumes a conservative background visual range based on pristine conditions and the scattering angle and line of sight that would maximize plume impacts.  The Department reviewed and verified all Level 1 analysis inputs.  Results of the Level 1 analysis are shown in Table 29.  Because there was an exceedance of the visibility criteria against a sky background, a Level 2 analysis was required.

Table 29 - Level 1 and Level 2 VISCREEN Results.

| Analysis | Background | Thetaa | Azib | Distance | Alphac | Delta E |  | Contrast |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Threshold | Plume | Threshold | Plume |
| Level 1 Results | Sky | 10 | 152 | 46.0 | 17 | 2 | 3.172 | 0.05 | 0.062 |
|  | Sky | 140 | 152 | 46.0 | 17 | 2 | 1.193 | 0.05 | -0.040 |
| Level 2 Results | Sky | 10 | 150 | 43.9 | 19 | 2 | 1.261 | 0.05 | 0.020 |
|  | Sky | 140 | 150 | 43.9 | 19 | 2 | 0.589 | 0.05 | -0.022 |
| a. Scattering angle. b. Azimuthal angle between line connecting source and observer, and line of sight. c. Angle between line of sight and plume centerline. |  |  |  |  |  |  |  |  |  |

The Level 2 analysis also assumes the scattering angle and line of sight that would maximum plume impacts, but uses a more realistic background visual range based on actual annual average natural conditions at CNWA, and uses worst case dispersion conditions that are based on actual meteorology data.  The applicant used surface meteorological data from the BKV ASOS station for the years 2011 to 2015 to find the worst-case dispersion condition when winds were blowing from the source towards the Class I area (S and SSE winds), for hours 0-6, 6-12, 12-18, and 18-24.  First, the dispersion conditions were ranked in order of decreasing severity, and then the frequency of occurrence of each was calculated.  The dispersion condition with a cumulative probability of 1% was used in the VISCREEN modeling.  This dispersion condition was stability class F and wind speed of 1 m/s.

The Department reviewed and verified all Level 2 analysis inputs.  Results of the Level 2 analysis are in Table 29.  Because there is no exceedance of the screening criteria against a sky background, this project will not have a significant impact on visibility at CNWA.

      - Deposition Analysis

In addition to visibility impairment, total nitrogen and sulfur deposition is also a part of the AQRV analysis.  The applicant analyzed nitrogen and sulfur deposition in CNWA.  This analysis was performed using the CALPUFF model and followed the most recent FLM guidance.  The results shown in Table 30 indicate that the project is not expected to have a significant impact with respect to deposition in CNWA.

Table 30 - Summary of AQRV deposition analysis for the project in Chassahowitzka National Wilderness Area.

| Deposition Type | Average Annual Deposition (kg/ha/yr) |  |  | Deposition Threshold (kg/ha/yr) | Max % of Threshold |
| --- | --- | --- | --- | --- | --- |
|  | 2001 | 2002 | 2003 |  |  |
| Sulfur | 0.0036 | 0.0045 | 0.0045 | 0.01 | 45% |
| Nitrogen | 0.0016 | 0.0017 | 0.0021 | 0.01 | 21% |

  - Conclusion

Based on the results presented in the air quality impact analysis, the Department has reasonable assurance that the increased pollutant emissions associated with the project will not cause or significantly contribute to any violation of a NAAQS or PSD increment; in addition, the Department finds that there will be no adverse impact on soils, vegetation, wildlife, or AQRVs in Class I areas.

- Preliminary Determination

The Department makes a preliminary determination that the proposed project will comply with all applicable state and federal air pollution regulations as conditioned by the Draft Permit.  This determination is based on a technical review of the complete application, reasonable assurances provided by the applicant, and the conditions specified in the Draft Permit.  Lara Rabbath is the project engineer responsible for reviewing the application and drafting the permit changes.  Ashley Kung is the meteorologist responsible for reviewing and approving the ambient air quality analyses.  Additional details of this analysis may be obtained by contacting the project engineer at the Department’s Office of Permitting and Compliance at Mail Station #5505, 2600 Blair Stone Road, Tallahassee, Florida  32399-2400 at 850-717-9082 or by email Lara.Rabbath@dep.state.fl.us..

Link to Application.  Click “Public Oculus Login” button to access the application.

EPA RBLC

GE 7HA.01/7HA.02 Gas Turbine Product Specifications website

AP-42 Vol. I, 3.1: Stationary Gas Turbines- US EPA

Information from EIA website.

Environmental Appeals Board September 1, 2016 Maricopa County Air Quality Department Ruling.

U.S. EPA, “PSD and Title V Permitting Guidance for Greenhouse Gases,” (November 2010) p. 42.

EIA “Electric Power Annual 2016 Revision Notice – March 8, 2018”

GE 7HA.01/7HA.02 Gas Turbine Product Specifications website

AP-42 VOL. I: 1.4 Natural Gas Combustion

EPA, “SF6 Leak Rates from High Voltage Circuit Breakers - U.S. EPA Investigates Potential Greenhouse Gas Emissions Source”

Assessing the Methane Emissions from Natural Gas-Fired Power Plants and Oil Refineries

EPA, “Leak Detection and Repair, a Best Practices Guide”

U.S. EPA’s Draft “Guidance on Significant Impact Levels for Ozone and Fine Particles in the Prevention of Significant Deterioration Permitting Program,” August 18, 2016.

U.S. EPA’s Draft “Guidance on the Development of Modeled Emission Rates for Precursors (MERPs) as a Tier 1 Demonstration Tool for Ozone and PM2.5 under the PSD Permitting Program,” December 2, 2016.

U.S. EPA’s “Distribution of the EPA’s modeling data used to develop illustrative examples in the draft Guidance on the Development of Modeled Emission Rates for Precursors (MERPs) as a Tier 1 Demonstration Tool for Ozone and PM2.5 under the PSD Permitting Program,” February 23, 2017

U.S. EPA’s “Distribution of the EPA’s modeling data used to develop illustrative examples in the draft Guidance on the Development of Modeled Emission Rates for Precursors (MERPs) as a Tier 1 Demonstration Tool for Ozone and PM2.5 under the PSD Permitting Program,” February 23, 2017