## Smith 2 Run Summary
Smith Phase 2 Run Summary Worksheet
Unit 2
Date | Run # | Load | Start | End | Description | Opacity | PM stack | Hg CEMS | Hg Stack | Hg Fuel | HCl CEM | HCl Stack | Comments
[6 empty] | Outlet | lb/Mbtu | lb/Tbtu | lb/Tbtus | lb/Tbtu | lb/Mbtu | lb/Mbtu |  | = denotes significant runs
[7 empty] | Sanders | SCS CEMS | Sanders | Inlet | Spectrum | Sanders | OOS= Out of Service
2013 Ultra-low Sulfur Fuel Data
2013-11-14 | 1 | 195 | 1345 | 1526 | Initial ULS coal Baseline No Injection | 8 | 0.0084 | [5 empty] | PM 0.0084 lb/mbtu: below MATS
| 2 | 147 | 1526 | 1631 | Initial ULS coal Baseline No Injection | 8 | 0.00085 | [5 empty] | PM 0.0085 lb/mbtu: below MATS
2013-11-15 | 3 | 188 | 855 | 1035 | Initial ULS coal Baseline No Injection | 8 | 0.0087 | [5 empty] | PM 0.0087 lb/mbtu: below MATS
| 4 | 192 | 1035 | 1142 | Initial ULS coal Baseline No Injection | 8 | 0.0072 | [5 empty] | PM 0.0072 lb/mbtu: below MATS
| 5 | 190 | 1203 | 1309 | Initial ULS coal Baseline No Injection | 8 | 0.00094 | [5 empty] | PM 0.0094 lb/mbtu: below MATS
2014 Ultra-low Sulfur Fuel Data
2014-01-21 | 1A | 75 | 920 | 1010 | Inlet hot ESP PM Low Load | 10 |  | N/A |  |  |  |  | Inlet Hot ESP PM Baseline
| 1B | 75 | 1200 | 1245 | Inlet hot ESP PM Low Load | 11 |  | N/A |  |  |  |  | Inlet Hot ESP PM Baseline
| 2A | 75 | 1000 | 1200 | Hg at 60 lb/hr BASF | 10 |  | 1.07
| 2B | 75 | 1200 | 1250 | Hg at 100 lb/hr BASF | 10 |  | 0.56
| 3 | 185 | 1510 | 1800 | Hg at 100 lb/hr BASF | 17 |  | 2.64 |  |  |  |  | Cancelled due to unit problem
2014-01-22 | 4A | 195 | 840 | 940 | Inlet hot ESP PM | 20 |  | 3.47
| 4B | 195 | 840 | 1250 | Hg at 400 lb/hr BASF | 23 |  | 1.26 |  |  |  |  | High opacity 31% CAM
| 5 | 180-195 | 1325 | 1420 | Hg at 400 lb/hr BASF | 23 |  | 2.36
| 6 | 195 | 1500 | 1600 | Hg at 200 lb/hr BASF | 29 |  | 1.89 |  |  |  |  | Stopped due to 29% CAM
2014-01-23 | 7 | 195 | 920 | 1024 | PM baseline; no injection | 22 | 0.0519 | 5.92 |  | 5.2 |  |  | Baseline PM oulet
| 8 | 195 | 1030 | 1330 | Hg at 300 lb/hr BASF | 22 |  | 1.69 |  | 5.2
| 9 | 195 | 1205 | 1310 | PM outlet @ 300 lb/hr BASF | 22 | 0.0409 | 1.75 |  | 5.2 |  |  | SNCR off due to urea shortage
| 10 | 195 | 1330 | 1415 | Hg at 350 lb/hr BASF | 22 |  | 1.79 |  | 5.2 |  |  | SNCR off due to urea shortage
| 11 | 195 | 1415 | 1455 | PM outlet @Hg at 350 lb/hr BASF | 21 |  | 3.13(no sorbent) |  | 5.2 |  |  | SNCR off due to urea shortage
| 12 | 195 | 1457 | 1645 | Hg @ 200 lb/hr Norit | 20 |  | 2.9 |  | 5.2 |  |  | Injection Skid Failure noted; bad run
2014-01-24 | 13 | 194 | 1050 | 1148 | PM + Hg@ 200 lb/hr Norit | 20 |  | 2.59 | 3.52 | 4.4 |  |  | Stopped run at 1140 due to B mill problem
| 14 | 194 | 1530 | 1553 | PM + Hg@ 200 lb/hr Norit | 18 |  | 1.61 |  | 4.4 |  |  | Stopped run due to Skid issue
| 15 | 194 | 1554 | 1730 | Hg @ 300 lb/hr Norit | 16 |  | 1.41 |  | 4.4
2014-01-27 | 16 | 194 | 830 | 1010 | Hg @ 300 lb/hr Norit | 14 |  | 1.53 |  | 7.2 |  |  | CEM Hg @ 8 down to ~1.2 during run
| 17 | 196 | 1010 | 1118 | PM + Hg@ 300 lb/hr Norit | 13 | 0.0298 | 1.35 | 1.91 | 7.2 |  |  | Preliminary PM @ 0.29 lb/mmbtu
| 18 | 195 | 1640 | 1747 | PM + Hg @ 300 lb/hr BASF | 16 | 0.0615 | 1.9 | 2.42 | 7.2 |  |  | opacity before injection @ 7%
2014-01-28 | 19 | 195 | 725 | 836 | PM + Hg Baseline ; No Injection | 14 | 0.0426 | OOS | 5.59 | 7.7 |  |  | Baseline PM + Wet Hg Baseline
| 20 | 195 | 910 | 1010 | HCl Baseline Run | 14 |  | OOS |  | 7.7 |  | 0.0077 | Baseline Wet HCl
| 21 | 85-96 | 1403 | 1510 | PM + Hg Wet @ 100 lb/hr BASF | 9% |  | 0.8 | 1.57 | 7.7 |  |  | 6% opacity before injection
2014-01-30 | 22A | 150 | 1052 | 1152 | Hg @ 250 lb/hr BASF | 12 |  | 0.95 | 1.59 | 5 |  |  | Hg Wet Run
| 22B |  | 950 | 1055 | PM wet @ 250 lb/hr BASF | 12 | 0.0364 | 1.06 |  | 5 |  |  | PM Wet Run
| 23 | 176 | 1314 | 1420 | PM + Hg Wet @ 250 lb/hr BASF | 13 | 0.0401 | 1.05 | 1.62 | 5 |  |  | PM and Hg Wet Run
| 24 | 195 | 1516 | 1621 | PM + Hg Wet @ 325 lb/hr BASF | 21 | 0.0769 | 1.43 | 2.34 | 5 |  |  | PM and Hg Wet Run
| 25 | 195 | 1700 | 1730 | Hg @ 400 lb/hr BASF | 23 |  | 1.3 | 2.52 | 5 |  |  | Hg CEMs only; opacity high
2014-01-31 | 26 | 90 | 942 | 1050 | Hg @ 100 lb/hr BASF | 10 |  | 0.99 |  | 4.4 |  |  | Opacity spike (60%) at 9:50
2014-02-01 | 27 | 150 | 920 | 1020 | Hg @ 250 lb/hr BASF | 13 |  | 1.03 |  | 5.5 |  |  | Hg CEMs only
| 28 | 150 | 1030 | 1100 | Hg @ 300 lb/hr BASF | 13 |  | 1.06 |  | 5.5 |  |  | Hg CEMs only
| 29 | 170 | 1200 | 1230 | Hg @ 300 lb/hr BASF | 22 |  | 1.41 |  | 5.5 |  |  | Hg CEMs only
| 30A | 170 | 1300 | 1400 | Hg @ 325 lb/hr BASF | 20 |  | 1.37 |  | 5.5 |  |  | Hg CEMs only; actual injection @ 316 lb/hr
| 30B | 170 | 1340 | 1400 | Hg @ 400 lb/hr BASF | 20 |  | 1.34 |  | 5.5 |  |  | Hg CEMs only; decision not for 195 due to results at 170
| 31A | 85 | 1430 | 1510 | Hg @ 200 lb/hr BASF | 10 |  | 0.38 |  | 5.5 |  |  | Hg CEMs only
| 31B | 85 | 1510 | 1600 | Hg @ 100 lb/hr BASF | 10 |  | 0.41 |  | 5.5 |  |  | Hg CEMs only
2014-02-02 | 32 | 150 | 845 | 945 | Hg @ 250 lb/hr BASF | 16 |  | 1.1 |  | 4.2 |  |  | Hg CEMs only
| 33 | 150 | 1000 | 1030 | Hg @ 300 lb/hr BASF | 13 |  | 1.12 |  | 4.2 |  |  | Hg CEMs only
| 34 | 175 | 1050 | 1120 | Hg @ 300 lb/hr BASF | 18 |  | 1.47 |  | 4.2 |  |  | Hg CEMs only
2014-02-03 | 35 | 195 | 1300 | 1403 | Hg @ 230 lb/hr HLI | 10 | 0.0252 | 7.26 |  | 4.6 | 0.0026 |  | PM + Hg CEMS
| 36 | 195 | 1530 | 1642 | HCl @ 600 lb/hr HLI | 8 |  | 6.63 |  | 4.6 | 0.0021 | 0.0015 | PM + Hg CEMS
| 36B | 195 | 1530 | 1745 | HCl @ 800 lb/hr HLI | 8 | 0.016 | 6.38 |  | 4.6 | 0.0018 |  | HCl Wet; Hg CEM
| 37 | 150 | 1740 | 1900 | HCl @ 780 lb/hr HLI | 9 |  | 5.23 |  | 4.6 | 0.00176 |  | HCl & Hg CEMS only
| 38 | 75 | 1925 | 2025 | HCl @ 780 lb/hr HLI | 8 |  | 5.88 |  | 4.6 | 0.00137 |  | HCl & Hg CEMS only
2014-02-06 | 39 | 195 | 1250 | 1400 | HCl @ 850 lb/hr HLI | 16 |  | 5.63 |  | 5.7 | 0.00176 | 0.0024 | PM & wet HCl; HCl & Hg CEMS
| 40 | 195 | 1440 | 1552 | HL @ 850 lb/hr+ BASF @ 200 lb/hr | 32 |  | 1.79 |  | 5.7 | 0.00195 | 0.0025 | PM & wet HCl; HCl & Hg CEMS
| 41 | 113 AGC | 1700 | 1730 | HL @ 850 lb/hr+ BASF @ 200 lb/hr | 26 |  | 0.9 |  | 5.7 | 0.002 |  | Hg & HCl CEMS only
2014-02-07 | 42 | 195 | 730 | 840 | ULS Coal Baseline Test | 10 | 0.028 | 5.19 |  | 4.6 | 0.00437 | 0.0067 | PM & wet HCl; HCl & Hg CEMS
| 43 | 170 | 850 | 935 | HCl @ 850 lb/hr HLI | 10 | 0.0168 | 5.02 |  | 4.6 | 0.0024 | 0.002 | PM & wet HCl; HCl & Hg CEMS
| 44 | 160 | 1155 | 1304 | HL @ 850+ BASF @ 300 lb/hr | 21 | 0.0718 | 0.8 |  | 4.6 | 0.00254 | 0.0016 | PM & wet HCl; HCl & Hg CEMS
| 45 | 170 | 1453 | 1602 | HL @ 1000+ BASF @ 200 lb/hr | 23 | 0.0678 | 0.82 |  | 4.6 | 0.002 | 0.002 | PM & wet HCl; HCl & Hg CEMS
| 46 | 195 | 1635 | 1700 | HL @ 1000+ BASF @ 200 lb/hr | 32 |  | 1.31 |  | 4.3 | 0.0021 |  | PM & wet HCl; HCl & Hg CEMS
2014-02-08 | 47 | 195 | 930 | 1000 | HL @ 1000 lb/hr | 11 |  | 5.69 |  | 4.3 | 0.0017 |  | Hg & HCl CEMS only
| 48 | 195 | 1015 | 1045 | HL @ 1500 lb/hr | 16 |  | 5.72 |  | 4.3 | 0.0015 |  | Hg & HCl CEMS only
| 49 | 195 | 1410 | 1440 | HL @ 2000 lb/hr | 22 |  | 5.62 |  | 4.3 | 0.0014 |  | Hg & HCl CEMS only
| 50 | 195 | 1630 | 1700 | HL @ 250 lb/hr | 22 |  | 5.4 |  | 4.3 | 0.0025 |  | Hg & HCl CEMS only
2014-02-09 | 51 | 195 | 1521 | 1700 | BASF @ 200 + ADA 50 | 24 |  | 1.44 |  | 5.3 | 0.0061 |  | Hg & HCl CEMS only
| 52 | 195 | 1730 | 1800 | BASF @ 200 + ADA 100 | 23 |  | 0.98 |  | 5.3 |  |  | Hg & HCl CEMS only
2014-02-10 | 53 | 195 | 9.05 | 1010 | BASF @ 150 + ADA 50 | 19 |  | 1.71 |  | 4.8 |  |  | Hg & HCl CEMS only
| 54 | 195 | 1030 | 1131 | BASF @ 200 + ADA 50 | 21 |  | 1.65 |  | 4.8 | 0.0074 |  | Hg & HCl CEMS only
| 55 | 195 | 1230 | 1340 | BASF @ 200 + ADA 75 | 23 |  | 1.63 |  | 4.8 | 0.0075 |  | Hg & HCl CEMS only
| 56 | 195 | 1640 | 1800 | BASF @ 250 + ADA 100 | 27 |  | 1.24 |  | 4.8 | 0.0064 |  | Hg & HCl CEMS only
2014-02-11 | 57 | 195 | 835 | 910 | BASF @ 200 + ADA 100 | 25 |  | 1.2 |  | 5.5 |  |  | Hg & HCl CEMS only
| 58 | 155 | 915 | 1040 | BASF @ 200 + ADA 125 | 26 |  | 0.79 |  | 5.5 | 0.0069 |  | Hg & HCl CEMS only
| 59 | 155 | 1040 | 1425 | ADA @ 125 | 20 |  | 1 |  | 5.5 |  |  | Hg & HCl CEMS only

## Smith 2 Fuel Plus
Smith Sorbent Phase 2.2 Test Project | [15 empty] | Calculated |  |  | Measured | Measured | Measured |  | Calculated |  |  | Measured | Measured | Comments
Unit 2 Fuel Analysis Projections to Stack Measurement Comparisons (SO2, HCl, Hg) | [15 empty] | HCL Inlet Emissions by Fuel Usage |  |  | Spectrum Results | Sanders Results | SO2 Inlet to Stack Exit |  | Hg Inlet Emissions by Fuel Usage |  |  | Sanders Results | SCS Results
Ultra-Low Sulfur Coal 01/21/2014 | [7 empty] | Unit 2 | Unit 2 | Unit 2 | Unit 2 | Unit 2 | Unit 2 | Unit 2 |  | Total | Total | Total | Unit 2 Tiger | Unit 2 Method 26 | Fuel | CEM | Total | Total | Total | Total Stack | Total
|  |  | Mill | Mill | Mill | Mill | Mill | Fuel Based | Sanders | Fuel Lab | Sulfur | Cl | Hg | Ash |  | lbs | HCL | HCL | HCL | HCL | SO2 | SO2 | lbs | Hg | Hg | Hg M30B | Hg CEMS
Run 1 |  | Unit 2 | 2A | 2B | 2C | 2D | 2E | Calculation | HI lb/mmbtu | Number | percent | ppm | ppm | percent |  | Coal/Run | lbs/Run | lb/mmbtu | lb/mmbtu | lb/mmbtu | lb/mmbtu | lb/mmbtu | Coal/Run | lbs/Run | lb/tbtu | lb/tbtu | lb/ltbtu
920 | 1022 | 75 MW | 297806 | 474060 | 870609 | 399557 | 412064 | [7 empty] | Target Goal = |  |  | 0.002 | 0.002 | 0.002 | 0.74 | 0.74 |  |  | 1.2 | 1.2 | 1.2 | Red indicates above compliance target limit
|  |  | 297806 | 474060 | 870843 | 399905 | 412407 | [20 empty] | Green indicates meets compliance target limit
|  | Delta = | 0 | 0 | 234 | 348 | 343 | 925 | [19 empty] | Fuel Analysis @ lab detection level (default value)
|  | Coal mmbtu = | [5 empty] | 8684 |  | AU01715 | 0.26 | 25 | 0.033 | 5.41 |  | 92500 | 2.3782 | 0.0029607 | NA | NA | 0.56886 | 0.54 | 92500 | 0.0030525 | 3.8001 | NA | NA | Significant baseline comparison values
|  | mmbtu/run = | [5 empty] | 803.27
|  | mmbtu/hr = | [5 empty] | 777.3581 | NA
Run 3 |  | Unit 2
1510 | 1820 | 185 MW | 298589 | 474902 | 872297 | 401633 | 414137
BASF Injection @ 60-100 |  |  | 300041 | 476055 | 873743 | 403092 | 415584
|  | Delta = | 1452 | 1153 | 1446 | 1459 | 1447 | 6957
|  | Coal mmbtu = | [5 empty] | 8684 |  | AU01715 | 0.26 | 25 | 0.033 | 5.41 |  | 695700 | 17.887 | 0.0029607 | NA | NA | 0.56886 | 0.47 | 695700 | 0.022958 | 3.8001 | NA | 0.56
|  | mmbtu/run = | [5 empty] | 6041.4588
|  | mmbtu/hr = | [5 empty] | 1812.4376 | NA
Ultra-Low Sulfur Coal 01/22/2014
Run 4 |  | Unit 2
840 | 1255 | 195 MW | 303102 | 480911 | 878610 | 407957 | 420438
BASF Injection @ 400 |  |  | 304997 | 482804 | 880511 | 409854 | 422333
|  | Delta = | 1895 | 1893 | 1901 | 1897 | 1895 | 9481
|  | Coal mmbtu = | [5 empty] | 8684 |  | AU01715 | 0.26 | 25 | 0.033 | 5.41 |  | 948100 | 24.3764 | 0.0029607 | NA | NA | 0.56886 | 0.51 | 948100 | 0.031287 | 3.8001 | NA | 1.26
|  | mmbtu/run = | [5 empty] | 8233.3004
|  | mmbtu/hr = | [5 empty] | 1937.2472 | NA
Ultra-Low Sulfur Coa 01/23/2014
Run 7 |  | Unit 2
920 | 1024 | 195 MW | 307390 | 488354 | 887830 | 417170 | 429602
No Injection |  |  | 307915 | 488859 | 888336 | 417676 | 430109
Baseline Run |  | Delta = | 525 | 505 | 506 | 506 | 507 | 2549
|  | Coal mmbtu = | [5 empty] | 9156 |  | AU02054 | 0.3 | 26 | 0.048 | 4.61 |  | 254900 | 6.8158 | 0.0029204 | NA | NA | 0.62254 | 0.5 | 254900 | 0.012235 | 5.2425 | NA | 5.92
|  | mmbtu/run = | [5 empty] | 2333.8644
|  | mmbtu/hr = | [5 empty] | 2187.9979 | 1977
Run 9 |  | Unit 2
1205 | 1310 | 195 MW | 308667 | 489579 | 889059 | 418399 | 436831
BASF Injection @ 300 |  |  | 309182 | 490075 | 889556 | 418897 | 437327
|  | Delta = | 515 | 496 | 497 | 498 | 496 | 2502
|  | Coal mmbtu = | [5 empty] | 9156 |  | AU02054 | 0.3 | 26 | 0.048 | 4.61 |  | 250200 | 6.6901 | 0.0029204 | NA | NA | 0.62254 | 0.51 | 250200 | 0.01201 | 5.2425 | NA | 1.75
|  | mmbtu/run = | [5 empty] | 2290.8312
|  | mmbtu/hr = | [5 empty] | 2114.6134 | 1905
Run 11 |  | Unit 2
1415 | 1455 | 195 MW | 309688 | 490560 | 890041 | 419382 | 431810
BASF Injection @ 350 |  |  | 309986 | 490847 | 890307 | 419669 | 432097
SNCR off due to urea supply |  | Delta = | 298 | 287 | 266 | 287 | 287 | 1425
|  | Coal mmbtu = | [5 empty] | 9156 |  | AU02054 | 0.3 | 26 | 0.048 | 4.61 |  | 142500 | 3.8103 | 0.0029204 | NA | NA | 0.62254 | 0.52 | 142500 | 0.00684 | 5.2425 | NA | 3.13 | Sorbent loss in run
|  | mmbtu/run = | [5 empty] | 1304.73
|  | mmbtu/hr = | [5 empty] | 1957.095 | NA
Ultra-Low Sulfur Coal 01/24/2014
Run 13 |  | Unit 2
1050 | 1148 | 195 MW | 313922 | 495965 | 897205 | 426556 | 438970
Norit Injection @ 200 |  |  | 314400 | 496300 | 897605 | 426900 | 439350
B mill issue at 1140 |  | Delta = | 478 | 335 | 400 | 344 | 380 | 1937
|  | Coal mmbtu = | [5 empty] | 8894 |  | AU0256 | 0.29 | 83 | 0.039 | 5.61 |  | 193700 | 16.5342 | 0.0095974 | NA | NA | 0.61952 | 0.5 | 193700 | 0.0075543 | 4.385 | 3.52 | 2.59
|  | mmbtu/run = | [5 empty] | 1722.7678
|  | mmbtu/hr = | [5 empty] | 1782.1736 | NA
Run 14 |  | Unit 2
1530 | 1553 | 195 MW | 315915 | 496614 | 899235 | 428586 | 440996
Norit Injection @ 200 |  |  | 316105 | 496803 | 899425 | 428777 | 441186
|  | Delta = | 190 | 189 | 190 | 191 | 190 | 950
|  | Coal mmbtu = | [5 empty] | 8894 |  | AU0256 | 0.29 | 83 | 0.039 | 5.61 |  | 95000 | 8.1092 | 0.0095974 | NA | NA | 0.61952 | 0.49 | 95000 | 0.003705 | 4.385 | NA | 1.61
|  | mmbtu/run = | [5 empty] | 844.93
|  | mmbtu/hr = | [5 empty] | 2204.1652 | NA
Run 15 |  | Unit 2
1554 | 1730 | 195 MW | 316105 | 496803 | 899425 | 428777 | 441186
Norit Injection @ 300 |  |  | 316829 | 497523 | 900144 | 429495 | 441902
|  | Delta = | 724 | 720 | 719 | 718 | 716 | 3597
|  | Coal mmbtu = | [5 empty] | 8894 |  | AU0256 | 0.29 | 83 | 0.039 | 5.61 |  | 359700 | 30.7039 | 0.0095974 | NA | NA | 0.61952 | 0.49 | 359700 | 0.014028 | 4.385 | NA | 1.41
|  | mmbtu/run = | [5 empty] | 3199.1718
|  | mmbtu/hr = | [5 empty] | 1999.4824 | NA
Ultra-Low Sulfur Coal 01/27/2014
Run 17 |  | Unit 2
1015 | 1118 | 196 MW | 319542 | 511427 | 918037 | 449496 | 461871
Norit Injection @ 300 |  |  | 320035 | 511906 | 918515 | 449977 | 462350
|  | Delta = | 493 | 479 | 478 | 481 | 479 | 2410
|  | Coal mmbtu = | [5 empty] | 8933 |  | AU02391 | 0.29 | 20 | 0.064 | 5.16 |  | 241000 | 4.957 | 0.0023025 | NA | NA | 0.61681 | 0.56 | 241000 | 0.015424 | 7.1644 | 1.91 | 1.35
|  | mmbtu/run = | [5 empty] | 2152.853
|  | mmbtu/hr = | [5 empty] | 2050.3362 | 1892
Run 18 |  | Unit 2
1640 | 1750 | 196 MW | 322145 | 514230 | 920833 | 452312 | 464677
Norit Injection @ 300 |  |  | 322700 | 514750 | 921351 | 452833 | 465196
|  | Delta = | 555 | 520 | 518 | 521 | 519 | 2633
|  | Coal mmbtu = | [5 empty] | 8933 |  | AU02391 | 0.29 | 20 | 0.064 | 5.16 |  | 263300 | 5.4157 | 0.0023025 | NA | NA | 0.61681 | 0.51 | 263300 | 0.016851 | 7.1644 | 2.42 | 1.9
|  | mmbtu/run = | [5 empty] | 2352.0589
|  | mmbtu/hr = | [5 empty] | 2016.0505 | 1851
Ultra-Low Sulfur Coal 01/28/2014
Run 19 |  | Unit 2
725 | 836 | 195 MW | 323807 | 516980 | 925362 | 457119 | 469469
Baseline No Injection |  |  | 324365 | 517535 | 925918 | 457674 | 470024
|  | Delta = | 558 | 555 | 556 | 555 | 555 | 2779
|  | Coal mmbtu = | [5 empty] | 8596 |  | AU02393 | 0.25 | 32 | 0.066 | 5 |  | 277900 | 9.1456 | 0.0038285 | NA | 0.0077 | 0.55258 | 0.46 | 277900 | 0.018341 | 7.678 | 5.59 | NA
|  | mmbtu/run = | [5 empty] | 2388.8284
|  | mmbtu/hr = | [5 empty] | 2018.7282 | 1835
Run 20 |  | Unit 2
910 | 1010 | 195 MW | 324627 | 517798 | 926180 | 457937 | 470286
Baseline No Injection |  |  | 325121 | 518292 | 926675 | 458431 | 470780
|  | Delta = | 494 | 494 | 495 | 494 | 494 | 2471
|  | Coal mmbtu = | [5 empty] | 8596 |  | AU02393 | 0.25 | 32 | 0.066 | 5 |  | 247100 | 8.132 | 0.0038285 | NA | NA | 0.55258 | 0.52 | 247100 | 0.016309 | 7.678 | NA | NA
|  | mmbtu/run = | [5 empty] | 2124.0716
|  | mmbtu/hr = | [5 empty] | 2124.0716 | NA
Run 21 |  | Unit 2
1403 | 1510 | 85 MW | 325375 | 519035 | 927698 | 459458 | 471807
BASF @ 100 |  |  | 325375 | 519272 | 928022 | 459834 | 472182
|  | Delta = | 0 | 237 | 324 | 376 | 375 | 1312
|  | Coal mmbtu = | [5 empty] | 8596 |  | AU02393 | 0.25 | 32 | 0.066 | 5 |  | 131200 | 4.3178 | 0.0038285 | NA | NA | 0.55258 | 0.52 | 131200 | 0.0086592 | 7.678 | 1.57 | 0.8
|  | mmbtu/run = | [5 empty] | 1127.7952
|  | mmbtu/hr = | [5 empty] | 1009.9659 | 1060
Ultra-Low Sulfur Coal 01/30/2014
Run 22 |  | Unit 2
1052 | 1152 | 150 | 328460 | 531054 | 940836 | 473930 | 486004
BASF @ 250 |  |  | 328740 | 531335 | 941240 | 474335 | 486408
|  | Delta = | 280 | 281 | 404 | 405 | 404 | 1774
|  | Coal mmbtu = | [5 empty] | 8825 |  | AU02444 | 0.22 | 25 | 0.044 | 4.64 |  | 177400 | 4.5611 | 0.0029134 | NA | NA | 0.47365 | 0.42 | 177400 | 0.0078056 | 4.9858 | 1.59 | 0.95
|  | mmbtu/run = | [5 empty] | 1565.555
|  | mmbtu/hr = | [5 empty] | 1565.555 | 1208
Run 23 |  | Unit 2
1314 | 1420 | 176 | 329171 | 531829 | 941814 | 474928 | 487001
BASF @ 250 |  |  | 329622 | 532307 | 942305 | 475419 | 487491
|  | Delta = | 451 | 478 | 491 | 491 | 490 | 2401
|  | Coal mmbtu = | [5 empty] | 8825 |  | AU02444 | 0.22 | 25 | 0.044 | 4.64 |  | 240100 | 6.1732 | 0.0029134 | NA | NA | 0.47365 | 0.42 | 240100 | 0.010564 | 4.9858 | 1.62 | 1.05
|  | mmbtu/run = | [5 empty] | 2118.8825
|  | mmbtu/hr = | [5 empty] | 1926.2568 | 1707
Run 24 |  | Unit 2
1516 | 1620 | 195 | 329985 | 532670 | 942670 | 474928 | 487001
BASF @ 325 |  |  | 330501 | 533185 | 943186 | 475419 | 487491
|  | Delta = | 516 | 515 | 516 | 491 | 490 | 2528
|  | Coal mmbtu = | [5 empty] | 8825 |  | AU02444 | 0.22 | 25 | 0.044 | 4.64 |  | 252800 | 6.4997 | 0.0029134 | NA | NA | 0.47365 | 0.43 | 252800 | 0.011123 | 4.9858 | 2.34 | 1.43
|  | mmbtu/run = | [5 empty] | 2230.96
|  | mmbtu/hr = | [5 empty] | 2028.1455 | 1874
Ultra-Low Sulfur Coal 01/31/2014
Run 26 |  | Unit 2
942 | 1053 | 90 | 332781 | 538403 | 948833 | 481931 | 493992
BASF @ 100 |  |  | 332781 | 538636 | 949175 | 482273 | 494332
|  | Delta = | 0 | 233 | 342 | 342 | 340 | 1257
|  | Coal mmbtu = | [5 empty] | 8595 |  | AU02671 | 0.26 | 56 | 0.038 | 5.24 |  | 125700 | 7.2393 | 0.0067006 | NA | NA | 0.57475 | 0.46 | 125700 | 0.0047766 | 4.4212 | NA | 0.99
|  | mmbtu/run = | [5 empty] | 1080.3915
|  | mmbtu/hr = | [5 empty] | 913.0069 | NA
Ultra-Low Sulfur Coal 02/01/2014
Run 27 |  | Unit 2
920 | 1020 | 150 | 333151 | 542643 | 955532 | 488657 | 500691
BASF @ 250 |  |  | 333474 | 543009 | 955897 | 489024 | 501057
|  | Delta = | 323 | 366 | 365 | 367 | 366 | 1787
|  | Coal mmbtu = | [5 empty] | 8683 |  | AU02673 | 0.25 | 39 | 0.048 | 5.18 |  | 178700 | 7.1674 | 0.0046192 | NA | NA | 0.54705 | 0.44 | 178700 | 0.0085776 | 5.528 | NA | 1.03
|  | mmbtu/run = | [5 empty] | 1551.6521
|  | mmbtu/hr = | [5 empty] | 1551.6521 | NA
Run 30 |  | Unit 2
1300 | 1400 | 170 | 334443 | 544008 | 956894 | 490025 | 502056
BASF @ 325 |  |  | 334820 | 544384 | 957269 | 490402 | 502432
|  | Delta = | 377 | 376 | 375 | 377 | 376 | 1881
|  | Coal mmbtu = | [5 empty] | 8683 |  | AU02673 | 0.25 | 39 | 0.048 | 5.18 |  | 188100 | 7.5445 | 0.0046192 | NA | NA | 0.54705 | 0.44 | 188100 | 0.0090288 | 5.528 | NA | 1.37
|  | mmbtu/run = | [5 empty] | 1633.2723
|  | mmbtu/hr = | [5 empty] | 1633.2723 | NA
Run 31 |  | Unit 2
1435 | 1530 | 85 | 334868 | 544558 | 957457 | 490591 | 502620
BASF @ 200 |  |  | 334868 | 544681 | 957715 | 490851 | 502880
|  | Delta = | 0 | 123 | 258 | 260 | 260 | 901
|  | Coal mmbtu = | [5 empty] | 8683 |  | AU02673 | 0.25 | 39 | 0.048 | 5.18 |  | 90100 | 3.6138 | 0.0046192 | NA | NA | 0.54705 | 0.4 | 90100 | 0.0043248 | 5.528 | NA | 0.38
|  | mmbtu/run = | [5 empty] | 782.3383
|  | mmbtu/hr = | [5 empty] | 782.3383 | NA
Ultra-Low Sulfur Coal 02/02/2014
Run 32 |  | Unit 2
845 | 945 | 150 | 336357 | 548055 | 962952 | 496122 | 508130
BASF @ 250 |  |  | 336705 | 548404 | 963300 | 496471 | 508478
|  | Delta = | 348 | 349 | 348 | 349 | 348 | 1742
|  | Coal mmbtu = | [5 empty] | 8945 |  | AU02783 | 0.28 | 25 | 0.038 | 4.78 |  | 174200 | 4.4788 | 0.0028743 | NA | NA | 0.59475 | 0.47 | 174200 | 0.0066196 | 4.2482 | NA | 1.1
|  | mmbtu/run = | [5 empty] | 1558.219
|  | mmbtu/hr = | [5 empty] | 1558.219 | NA
Run 34 |  | Unit 2
1050 | 1120 | 175 | 337082 | 548782 | 963677 | 496852 | 508859
BASF @ 300 |  |  | 337291 | 548990 | 963885 | 497061 | 509067
|  | Delta = | 209 | 208 | 208 | 209 | 208 | 1042
|  | Coal mmbtu = | [5 empty] | 8945 |  | AU02783 | 0.28 | 25 | 0.038 | 4.78 |  | 104200 | 2.6791 | 0.0028743 | NA | NA | 0.59475 | 0.47 | 104200 | 0.0039596 | 4.2482 | NA | 1.12
|  | mmbtu/run = | [5 empty] | 932.069
|  | mmbtu/hr = | [5 empty] | 1864.138 | NA
Ultra-Low Sulfur Coal 02/03/2014
Run 35 |  | Unit 2
1300 | 1403 | 195 | 339774 | 551598 | 972416 | 505657 | 517633
BASF @ 200 |  |  | 340249 | 552072 | 972888 | 506133 | 518105
|  | Delta = | 475 | 474 | 472 | 476 | 472 | 2369
|  | Coal mmbtu = | [5 empty] | 8639 |  | AU02785 | 0.25 | 25 | 0.04 | 5.13 |  | 236900 | 6.0909 | 0.0029761 | 0.0026 | NA | 0.54983 | 0.47 | 236900 | 0.009476 | 4.6302 | NA | 7.26
|  | mmbtu/run = | [5 empty] | 2046.5791
|  | mmbtu/hr = | [5 empty] | 1949.123 | 1853
Run 36 |  | Unit 2
1530 | 1642 | 195 | 340897 | 552720 | 973534 | 506782 | 518753
HL @ 600 |  |  | 341395 | 553218 | 974029 | 507282 | 519250
|  | Delta = | 498 | 498 | 495 | 500 | 497 | 2488
|  | Coal mmbtu = | [5 empty] | 8639 |  | AU02785 | 0.25 | 25 | 0.04 | 5.13 |  | 248800 | 6.3968 | 0.0029761 | 0.0021 | 0.0015 | 0.54983 | 0.42 | 248800 | 0.009952 | 4.6302 | NA | 6.38
|  | mmbtu/run = | [5 empty] | 2149.3832
|  | mmbtu/hr = | [5 empty] | 1791.1527 | 2038 | ???
Run 37 |  | Unit 2
1740 | 1900 | 150 | 341791 | 553624 | 974435 | 507690 | 519658
HL @ 780 |  |  | 342247 | 554062 | 974872 | 508130 | 520096
|  | Delta = | 456 | 438 | 437 | 440 | 438 | 2209
|  | Coal mmbtu = | [5 empty] | 8639 |  | AU02785 | 0.25 | 25 | 0.04 | 5.13 |  | 220900 | 5.6795 | 0.0029761 | 0.0018 | NA | 0.54983 | 0.4 | 220900 | 0.008836 | 4.6302 | NA | 5.23
|  | mmbtu/run = | [5 empty] | 1908.3551
|  | mmbtu/hr = | [5 empty] | 1431.2663 | NA
Run 38 |  | Unit 2
1925 | 2025 | 75 | 342278 | 554153 | 974991 | 508250 | 520215
HL @ 780 |  |  | 342278 | 554153 | 975286 | 508547 | 520511
|  | Delta = | 0 | 0 | 295 | 297 | 296 | 888
|  | Coal mmbtu = | [5 empty] | 8639 |  | AU02785 | 0.25 | 25 | 0.04 | 5.13 |  | 88800 | 2.2831 | 0.0029761 | 0.0037 | NA | 0.54983 | 0.35 | 88800 | 0.003552 | 4.6302 | NA | 5.88
|  | mmbtu/run = | [5 empty] | 767.1432
|  | mmbtu/hr = | [5 empty] | 767.1432 | NA
Ultra-Low Sulfur Coal 02/06/2014
Run 39 |  | Unit 2
1250 | 1403 | 195 | 346620 | 559775 | 982270 | 515060 | 526729
HL @ 850 |  |  | 347171 | 560304 | 982801 | 515590 | 527259
PM+Wet HCl |  | Delta = | 551 | 529 | 531 | 530 | 530 | 2671
|  | Coal mmbtu = | [5 empty] | 8626 |  | AU03180 | 0.28 | 65 | 0.049 | 6.9 |  | 267100 | 17.8551 | 0.0077496 | 0.0018 | 0.0024 | 0.61674 | 0.42 | 267100 | 0.013088 | 5.6805 | NA | 5.63
|  | mmbtu/run = | [5 empty] | 2304.0046
|  | mmbtu/hr = | [5 empty] | 1893.7024 | NA
Run 40 |  | Unit 2
1440 | 1552 | 195 | 347442 | 560565 | 983062 | 515852 | 527520
HL @ 850 |  |  | 348013 | 561113 | 983611 | 516401 | 528068
PM+Wet HCl |  | Delta = | 571 | 548 | 549 | 549 | 548 | 2765
|  | Coal mmbtu = | [5 empty] | 8626 |  | AU03180 | 0.28 | 65 | 0.049 | 6.9 |  | 276500 | 18.4835 | 0.0077496 | 0.002 | 0.0025 | 0.61674 | 0.41 | 276500 | 0.013548 | 5.6805 | NA | 1.79
|  | mmbtu/run = | [5 empty] | 2385.089
|  | mmbtu/hr = | [5 empty] | 1933.8559 | NA
Run 41 |  | Unit 2
1705 | 1730 | 113 AGC | 348459 | 561568 | 984068 | 516858 | 528524
HL @ 850 + Carbon @ 200 |  |  | 348524 | 561648 | 984178 | 516967 | 528632
PM+Wet HCl |  | Delta = | 65 | 80 | 110 | 109 | 108 | 472
|  | Coal mmbtu = | [5 empty] | 8626 |  | AU03180 | 0.28 | 65 | 0.049 | 6.9 |  | 47200 | 3.1552 | 0.0077496 | 0.002 | NA | 0.61674 | 0.38 | 47200 | 0.0023128 | 5.6805 | NA | 0.9
|  | mmbtu/run = | [5 empty] | 407.1472
|  | mmbtu/hr = | [5 empty] | 977.1533 | NA
Ultra-Low Sulfur Coal 02/07/2014
Run 42 |  | Unit 2
730 | 840 | 195 | 351323 | 565507 | 988480 | 524266 | 532917
Baseline Run |  |  | 351896 | 566042 | 989055 | 524841 | 533491
PM+Wet HCl |  | Delta = | 573 | 535 | 575 | 575 | 574 | 2832
|  | Coal mmbtu = | [5 empty] | 8446 |  | AU03182 | 0.24 | 25 | 0.039 | 5.84 |  | 283200 | 7.2813 | 0.0030441 | 0.0044 | 0.0067 | 0.5399 | 0.48 | 283200 | 0.011045 | 4.6176 | NA | 5.49
|  | mmbtu/run = | [5 empty] | 2391.9072
|  | mmbtu/hr = | [5 empty] | 2050.2062 | 2097
Run 43 |  | Unit 2
935 | 1018 | 170 | 352225 | 566346 | 989385 | 522170 | 533820
HL @ 850 |  |  | 352522 | 566624 | 989686 | 522473 | 534120
PM+Wet HCl |  | Delta = | 297 | 278 | 301 | 303 | 300 | 1479
|  | Coal mmbtu = | [5 empty] | 8446 |  | AU03182 | 0.24 | 25 | 0.039 | 5.84 |  | 147900 | 3.8026 | 0.0030441 | 0.0024 | 0.002 | 0.5399 | 0.41 | 147900 | 0.0057681 | 4.6176 | NA | 5.02
|  | mmbtu/run = | [5 empty] | 1249.1634
|  | mmbtu/hr = | [5 empty] | 1743.0187 | NA
Run 44 |  | Unit 2
1155 | 1304 | 160 | 352527 | 567371 | 990438 | 523225 | 534871
HL @ 850 + Carbon @ 300 |  |  | 352527 | 567910 | 990977 | 523765 | 535398
PM+Wet HCl |  | Delta = | 0 | 539 | 539 | 540 | 527 | 2145
|  | Coal mmbtu = | [5 empty] | 8446 |  | AU03182 | 0.24 | 25 | 0.039 | 5.84 |  | 214500 | 5.515 | 0.0030441 | 0.0025 | 0.0016 | 0.5399 | 0.39 | 214500 | 0.0083655 | 4.6176 | NA | 0.8
|  | mmbtu/run = | [5 empty] | 1811.667
|  | mmbtu/hr = | [5 empty] | 1575.3626 | NA
Run 45 |  | Unit 2
1453 | 1607 | 170 | 353193 | 568649 | 991716 | 524434 | 536052
HL @ 1000 + Carbon @ 300 |  |  | 353682 | 569137 | 992204 | 524866 | 536483
PM+Wet HCl |  | Delta = | 489 | 488 | 488 | 432 | 431 | 2328
|  | Coal mmbtu = | [5 empty] | 8446 |  | AU03182 | 0.24 | 25 | 0.039 | 5.84 |  | 232800 | 5.9855 | 0.0030441 | 0.002 | 0.002 | 0.5399 | 0.39 | 232800 | 0.0090792 | 4.6176 | NA | 0.82
|  | mmbtu/run = | [5 empty] | 1966.2288
|  | mmbtu/hr = | [5 empty] | 1594.2396 | NA
Run 46 |  | Unit 2
1632 | 1707 | 195 | 353868 | 569322 | 992389 | 525041 | 536658
HL @ 1000 + Carbon @ 200 |  |  | 354133 | 569586 | 992653 | 525306 | 536923
PM+Wet HCl |  | Delta = | 265 | 264 | 264 | 265 | 265 | 1323
|  | Coal mmbtu = | [5 empty] | 8446 |  | AU03182 | 0.24 | 25 | 0.039 | 5.84 |  | 132300 | 3.4015 | 0.0030441 | 0.0021 | NA | 0.5399 | 0.4 | 132300 | 0.0051597 | 4.6176 | NA | 1.31
|  | mmbtu/run = | [5 empty] | 1117.4058
|  | mmbtu/hr = | [5 empty] | 1915.5528 | NA
Ultra-Low Sulfur Coal 02/08/2014
Run 47 |  | Unit 2
930 | 1000 | 195 | 357942 | 574609 | 997808 | 530432 | 542062
HL @1000 |  |  | 358150 | 574847 | 998046 | 530640 | 542300
CEMS only |  | Delta = | 208 | 238 | 238 | 208 | 238 | 1130
|  | Coal mmbtu = | [5 empty] | 8804 |  | AU03184 | 0.24 | 25 | 0.038 | 4.85 |  | 113000 | 2.9053 | 0.0029203 | 0.0017 | NA | 0.51795 | 0.39 | 113000 | 0.004294 | 4.3162 | NA | 5.69
|  | mmbtu/run = | [5 empty] | 994.852
|  | mmbtu/hr = | [5 empty] | 1989.704 | NA
Run 48 |  | Unit 2
1015 | 1045 | 195 | 358253 | 574965 | 998164 | 536743 | 542418
HL @1500 |  |  | 358466 | 575208 | 998406 | 536955 | 542661
CEMS only |  | Delta = | 213 | 243 | 242 | 212 | 243 | 1153
|  | Coal mmbtu = | [5 empty] | 8804 |  | AU03184 | 0.24 | 25 | 0.038 | 4.85 |  | 115300 | 2.9644 | 0.0029203 | 0.0015 | NA | 0.51795 | 0.39 | 115300 | 0.0043814 | 4.3162 | NA | 5.72
|  | mmbtu/run = | [5 empty] | 1015.1012
|  | mmbtu/hr = | [5 empty] | 2030.2024 | NA
Run 49 |  | Unit 2
1410 | 1440 | 195 | 359855 | 576776 | 999992 | 532349 | 544254
HL @2000 |  |  | 360072 | 577023 | 1000241 | 532567 | 544503
CEMS only |  | Delta = | 217 | 247 | 249 | 218 | 249 | 1180
|  | Coal mmbtu = | [5 empty] | 8804 |  | AU03184 | 0.24 | 25 | 0.038 | 4.85 |  | 118000 | 3.0339 | 0.0029203 | 0.0014 | NA | 0.51795 | 0.35 | 118000 | 0.004484 | 4.3162 | NA | 5.62
|  | mmbtu/run = | [5 empty] | 1038.872
|  | mmbtu/hr = | [5 empty] | 2077.744 | NA
Run 50 |  | Unit 2
1630 | 1700 | 195 | 360831 | 577890 | 1103 | 533322 | 545194
HL @300 |  |  | 361073 | 578165 | 1378 | 533563 | 545469
CEMS only |  | Delta = | 242 | 275 | 275 | 241 | 275 | 1308
|  | Coal mmbtu = | [5 empty] | 8804 |  | AU03184 | 0.24 | 25 | 0.038 | 4.85 |  | 130800 | 3.363 | 0.0029203 | 0.0025 | NA | 0.51795 | 0.43 | 130800 | 0.0049704 | 4.3162 | NA | 5.4
|  | mmbtu/run = | [5 empty] | 1151.5632
|  | mmbtu/hr = | [5 empty] | 2303.1264 | NA
Ultra-Low Sulfur Coal 02/09/2014
Run 51 |  | Unit 2
1522 | 1700 | 195 | 363945 | 583507 | 8557 | 540630 | 552659
BASF @ 200 + ADA @ 50 |  |  | 364674 | 584235 | 9284 | 541358 | 553390
CEMS only |  | Delta = | 729 | 728 | 727 | 728 | 731 | 3643
|  | Coal mmbtu = | [5 empty] | 8550 |  | AU03186 | 0.24 | 25 | 0.045 | 5.78 |  | 364300 | 9.3664 | 0.0030071 | 0.0061 | NA | 0.53333 | 0.5 | 364300 | 0.016393 | 5.2632 | NA | 1.44
|  | mmbtu/run = | [5 empty] | 3114.765
|  | mmbtu/hr = | [5 empty] | 1906.999 | NA
Run 52 |  | Unit 2
1730 | 1800 | 195 | 364913 | 584473 | 9521 | 541594 | 553626
BASF @ 200 + ADA @ 100 |  |  | 365140 | 584696 | 9742 | 541815 | 553846
CEMS only |  | Delta = | 227 | 223 | 221 | 221 | 220 | 1112
|  | Coal mmbtu = | [5 empty] | 8550 |  | AU03186 | 0.24 | 25 | 0.045 | 5.78 |  | 111200 | 2.859 | 0.0030071 | NA | NA | 0.53333 | 0.5 | 111200 | 0.005004 | 5.2632 | NA | 0.98
|  | mmbtu/run = | [5 empty] | 950.76
|  | mmbtu/hr = | [5 empty] | 1901.52 | NA
Ultra-Low Sulfur Coal 02/10/2014
Run 53 |  | Unit 2
904 | 1010 | 195 | 366758 | 587880 | 14739 | 546721 | 558855
BASF @ 150 + ADA @ 50 |  |  | 367252 | 588375 | 15233 | 547180 | 559350
CEMS only |  | Delta = | 494 | 495 | 494 | 459 | 495 | 2437
|  | Coal mmbtu = | [5 empty] | 8470 |  | AU03406 | 0.25 | 37 | 0.041 | 6.71 |  | 243700 | 9.2733 | 0.0044926 | NA | NA | 0.5608 | 0.54 | 243700 | 0.0099917 | 4.8406 | NA | 1.71
|  | mmbtu/run = | [5 empty] | 2064.139
|  | mmbtu/hr = | [5 empty] | 1876.49 | NA
Run 54 |  | Unit 2
1030 | 1131 | 195 | 367419 | 588540 | 15398 | 547332 | 559513
BASF @ 200 + ADA @ 50 |  |  | 367880 | 589001 | 15858 | 547760 | 559974
CEMS only |  | Delta = | 461 | 461 | 460 | 428 | 461 | 2271
|  | Coal mmbtu = | [5 empty] | 8470 |  | AU03406 | 0.25 | 37 | 0.041 | 6.71 |  | 227100 | 8.6416 | 0.0044926 | 0.0074 | NA | 0.5608 | 0.55 | 227100 | 0.0093111 | 4.8406 | NA | 1.65
|  | mmbtu/run = | [5 empty] | 1923.537
|  | mmbtu/hr = | [5 empty] | 1892.0036 | NA
Run 55 |  | Unit 2
1230 | 1352 | 195 | 368318 | 589398 | 16260 | 548169 | 560416
BASF @ 200 + ADA @ 75 |  |  | 368928 | 589999 | 16859 | 548777 | 561029
CEMS only |  | Delta = | 610 | 601 | 599 | 608 | 613 | 3031
|  | Coal mmbtu = | [5 empty] | 8470 |  | AU03406 | 0.25 | 37 | 0.041 | 6.71 |  | 303100 | 11.5335 | 0.0044926 | 0.0075 | NA | 0.5608 | 0.55 | 303100 | 0.012427 | 4.8406 | NA | 1.63
|  | mmbtu/run = | [5 empty] | 2567.257
|  | mmbtu/hr = | [5 empty] | 1878.4807 | NA
Run 56 |  | Unit 2
1640 | 1800 | 195 | 370168 | 591220 | 18077 | 550022 | 562289
BASF @ 250 + ADA @ 100 |  |  | 370789 | 591829 | 18586 | 550642 | 562916
CEMS only |  | Delta = | 621 | 609 | 509 | 620 | 627 | 2986
|  | Coal mmbtu = | [5 empty] | 8470 |  | AU03406 | 0.25 | 37 | 0.041 | 6.71 |  | 298600 | 11.3623 | 0.0044926 | 0.0064 | NA | 0.5608 | 0.46 | 298600 | 0.012243 | 4.8406 | NA | 1.24
|  | mmbtu/run = | [5 empty] | 2529.142
|  | mmbtu/hr = | [5 empty] | 1896.8565 | NA
Ultra-Low Sulfur Coal 02/11/2014
Run 57 |  | Unit 2
835 | 900 | 195 | 372421 | 593577 | 23480 | 555556 | 567903
BASF @ 200 + ADA @ 125 |  |  | 372623 | 593778 | 23680 | 555758 | 568107
CEMS only |  | Delta = | 202 | 201 | 200 | 202 | 204 | 1009
|  | Coal mmbtu = | [5 empty] | 8504 |  | AU03408 | 0.27 | 58 | 0.047 | 5.8 |  | 100900 | 6.0186 | 0.0070142 | NA | NA | 0.60325 | 0.49 | 100900 | 0.0047423 | 5.5268 | NA | 1.2
|  | mmbtu/run = | [5 empty] | 858.0536
|  | mmbtu/hr = | [5 empty] | 2059.3286 | NA
Run 58 |  | Unit 2
915 | 1040 | 155 | 372731 | 593819 | 23787 | 555867 | 568217
BASF @ 200 + ADA @ 125 |  |  | 373353 | 593819 | 24408 | 556500 | 568858
CEMS only |  | Delta = | 622 | 0 | 621 | 633 | 641 | 2517
|  | Coal mmbtu = | [5 empty] | 8504 |  | AU03408 | 0.27 | 58 | 0.047 | 5.8 |  | 251700 | 15.0136 | 0.0070142 | 0.0069 | NA | 0.60325 | 0.49 | 251700 | 0.01183 | 5.5268 | NA | 0.79
|  | mmbtu/run = | [5 empty] | 2140.4568
|  | mmbtu/hr = | [5 empty] | 1510.9107 | NA
Note on E4: Waters, G. Dwain: measured as 100lb flow
Note on F4: Waters, G. Dwain: measured as 100lb flow
Note on G4: Waters, G. Dwain: measured as 100lb flow
Note on H4: Waters, G. Dwain: measured as 100lb flow
Note on I4: Waters, G. Dwain: measured as 100lb flow
Note on K5: Waters, G. Dwain: F-factor Heat Input Calculated in Test Run
Note on B6: Waters, G. Dwain: End Time
Note on D6: Waters, G. Dwain: Unit Load
Note on U6: Waters, G. Dwain: MATS HCl limit
Note on V6: Waters, G. Dwain: MATS HCl limit
Note on W6: Waters, G. Dwain: MATS HCl limit
Note on X6: Waters, G. Dwain: BART SO2 limit
Note on Y6: Waters, G. Dwain: BART SO2 limit
Note on AB6: Waters, G. Dwain: MATS Hg limit
Note on AC6: Waters, G. Dwain: MATS Hg limit
Note on AD6: Waters, G. Dwain: MATS Hg limit
Note on D8: Waters, G. Dwain: total as 100 lbs.
Note on J8: Waters, G. Dwain: as 100lbs flow
Note on O9: Waters, G. Dwain: Default Cl MDL
Note on T9: Waters, G. Dwain: Cl to HCl conversation is 1.02843 factor
Note on AC9: Waters, G. Dwain: Not Available
Note on J11: Waters, G. Dwain: Coal mbtu/hr
Note on O17: Waters, G. Dwain: Default Cl MDL
Note on AC17: Waters, G. Dwain: Not Available
Note on O25: Waters, G. Dwain: Default Cl MDL
Note on AC25: Waters, G. Dwain: Not Available
Note on AC34: Waters, G. Dwain: Not Available
Note on I40: Waters, G. Dwain: GDW revised from 430831. looks like typo
Note on AC43: Waters, G. Dwain: Not Available
Note on AC51: Waters, G. Dwain: Not Available
Note on AC60: Waters, G. Dwain: Not Available
Note on AC68: Waters, G. Dwain: Not Available
Note on AC76: Waters, G. Dwain: Not Available
Note on AD76: Waters, G. Dwain: Not Available
Note on AC85: Waters, G. Dwain: Not Available
Note on AD85: Waters, G. Dwain: Not Available
Note on AC93: Waters, G. Dwain: Not Available
Note on AC102: Waters, G. Dwain: Not Available
Note on AC110: Waters, G. Dwain: Not Available
Note on AC118: Waters, G. Dwain: Not Available
Note on O127: Waters, G. Dwain: Default Cl MDL
Note on AC127: Waters, G. Dwain: Not Available
Note on O135: Waters, G. Dwain: Default Cl MDL
Note on AC135: Waters, G. Dwain: Not Available
Note on O143: Waters, G. Dwain: Default Cl MDL
Note on AC143: Waters, G. Dwain: Not Available
Note on AC152: Waters, G. Dwain: Not Available
Note on AC161: Waters, G. Dwain: Not Available
Note on AC169: Waters, G. Dwain: Not Available
Note on AC177: Waters, G. Dwain: Not Available
Note on O186: Waters, G. Dwain: Default Cl MDL
Note on AC186: Waters, G. Dwain: Not Available
Note on O194: Waters, G. Dwain: Default Cl MDL
Note on AC194: Waters, G. Dwain: Not Available
Note on O203: Waters, G. Dwain: Default Cl MDL
Note on AC203: Waters, G. Dwain: Not Available
Note on O211: Waters, G. Dwain: Default Cl MDL
Note on AC211: Waters, G. Dwain: Not Available
Note on O219: Waters, G. Dwain: Default Cl MDL
Note on AC219: Waters, G. Dwain: Not Available
Note on O227: Waters, G. Dwain: Default Cl MDL
Note on AC227: Waters, G. Dwain: Not Available
Note on AC236: Waters, G. Dwain: Not Available
Note on AC244: Waters, G. Dwain: Not Available
Note on AC252: Waters, G. Dwain: Not Available
Note on O261: Waters, G. Dwain: Default Cl MDL
Note on AC261: Waters, G. Dwain: Not Available
Note on O269: Waters, G. Dwain: Default Cl MDL
Note on AC269: Waters, G. Dwain: Not Available
Note on O277: Waters, G. Dwain: Default Cl MDL
Note on AC277: Waters, G. Dwain: Not Available
Note on O285: Waters, G. Dwain: Default Cl MDL
Note on AC285: Waters, G. Dwain: Not Available
Note on O293: Waters, G. Dwain: Default Cl MDL
Note on AC293: Waters, G. Dwain: Not Available
Note on O302: Waters, G. Dwain: Default Cl MDL
Note on AC302: Waters, G. Dwain: Not Available
Note on O310: Waters, G. Dwain: Default Cl MDL
Note on AC310: Waters, G. Dwain: Not Available
Note on O318: Waters, G. Dwain: Default Cl MDL
Note on AC318: Waters, G. Dwain: Not Available
Note on O326: Waters, G. Dwain: Default Cl MDL
Note on AC326: Waters, G. Dwain: Not Available
Note on O335: Waters, G. Dwain: Default Cl MDL
Note on AC335: Waters, G. Dwain: Not Available
Note on O343: Waters, G. Dwain: Default Cl MDL
Note on AC343: Waters, G. Dwain: Not Available
Note on AC352: Waters, G. Dwain: Not Available
Note on AC360: Waters, G. Dwain: Not Available
Note on AC368: Waters, G. Dwain: Not Available
Note on AC376: Waters, G. Dwain: Not Available
Note on AC385: Waters, G. Dwain: Not Available
Note on AC393: Waters, G. Dwain: Not Available

## Smith 1 Run Summary
Smith Phase 2 Run Summary Worksheet
Unit 1
Date | Run # | Load | Start | End | Description | Opacity | Comments | PM stack
2014 Ultra-Low Sulfur Coal (No Sorbent Injection) | [7 empty] | lb/MBTU
2014-02-04 | 1 | 172 | 920 | 1030 | Baseline ULS Coal PM Outlet | 10 | Full Load Outlet Cold ESP PM Baseline | 0.0187
| 2 | 170 | 1113 | 1222 | Baseline ULS Coal PM Outlet | 10 | Full Load Outlet Cold ESP PM Baseline | 0.02
| 3 | 173 | 1246 | 1353 | Baseline ULS Coal PM Outlet | 10 | Full Load Outlet Cold ESP PM Baseline | 0.0218
2014-02-05 | 4 | 79 | 905 | 1016 | Baseline ULS Coal PM Outlet | 8 | Low Load Outlet Cold ESP PM Baseline | 0.0163
| 5 | 130 | 1432 | 1520 | Baseline ULS Coal PM Inlet | 8 | Mid Load Inlet Hot ESP PM Baseline/Particle Sizing | NA
| 6 | 130 | 1610 | 1656 | Baseline ULS Coal PM Inlet | 9 | Mid Load Inlet Hot ESP PM Baseline/Grain Loading | NA
2014-02-06 | 7 | 170 | 810 | 852 | Baseline ULS Coal PM Inlet | 13 | Full Load Inlet Hot ESP PM Baseline/Grain Loading | NA
| 8 | 160 | 920 | 1004 | Baseline ULS Coal PM Inlet | 13 | Full Load Inlet Hot ESP PM Baseline/Particle Sizing | NA

## Smith 1 Fuel Plus
Smith Sorbent Phase 2.2 Test Project | [15 empty] | Calculated |  |  | Measured | Calculated |  |  | Comments
Unit 1 Fuel Analysis Projections to Stack Measurement Comparisons (SO2, HCl, Hg) | [15 empty] | HCL Inlet Emissions by Fuel Usage |  |  | SO2 Inlet to Stack Exit | Hg Inlet Emissions by Fuel Usage
Ultra-Low Sulfur Coal 02/4/2014 | [7 empty] | Unit 1 | Unit 1 | Unit 1 | Unit 1 | Unit 1 | Unit 1 | Unit 1 |  | Total | Total | Total | Fuel | Total | Total | Total
|  |  | Mill | Mill | Mill | Mill |  | Fuel Based | Sanders | Fuel Lab | Sulfur | Cl | Hg | Ash |  | lbs | HCL | HCL | SO2 | lbs | Hg | Hg
Run 1 |  | Unit 1 | 1A | 1B | 1C | 1D |  | Calculation | HI lb/mmbtu | Number | percent | ppm | ppm | percent |  | Coal/Run | lbs/Run | lb/mmbtu | lb/mmbtu | Coal/Run | lbs/Run | lb/tbtu
920 | 1030 | 172 | 522504 | 508103 | 659100 | 76860 | [8 empty] | Target Goal = |  |  | 0.002 | 0.74 |  |  | 1.2 | Red indicates above compliance target limit
|  |  | 523091 | 508686 | 659676 | 77434 | [16 empty] | Green indicates meets compliance target limit
|  | Delta = | 587 | 583 | 576 | 574 | 0 | 2320
|  | Coal mmbtu = | [5 empty] | 8945 |  | AU02783 | 0.28 | 25 | 0.038 | 4.78 |  | 232000 | 5.9649 | 0.0028743 | 0.59475 | 232000 | 0.008816 | 4.2482 | Full Load Outlet Cold ESP PM Baseline
|  | mmbtu/run = | [5 empty] | 2075.24 | [14 empty] | No DSI or ACI control Run
|  | mmbtu/hr = | [5 empty] | 1778.7771 | NA
Run 2 |  | Unit 1 | 1A | 1B | 1C | 1D
1113 | 1225 | 172 | 523448 | 509043 | 660018 | 77775
|  |  | 524033 | 509615 | 660576 | 78326
|  | Delta = | 585 | 572 | 558 | 551 | 0 | 2266
|  | Coal mmbtu = | [5 empty] | 8945 |  | AU02783 | 0.28 | 25 | 0.038 | 4.78 |  | 226600 | 5.8261 | 0.0028743 | 0.59475 | 226600 | 0.0086108 | 4.2482 | Full Load Outlet Cold ESP PM Baseline
|  | mmbtu/run = | [5 empty] | 2026.937 | [14 empty] | No DSI or ACI control
|  | mmbtu/hr = | [5 empty] | 1815.1675 | NA
Run 3 |  | Unit 1 | 1A | 1B | 1C | 1D
1246 | 1353 | 172 | 524227 | 509803 | 660759 | 78508
|  |  | 524798 | 510365 | 661307 | 79050
|  | Delta = | 571 | 562 | 548 | 542 | 0 | 2223
|  | Coal mmbtu = | [5 empty] | 8945 |  | AU02783 | 0.28 | 25 | 0.038 | 4.78 |  | 222300 | 5.7155 | 0.0028743 | 0.59475 | 222300 | 0.0084474 | 4.2482 | Full Load Outlet Cold ESP PM Baseline
|  | mmbtu/run = | [5 empty] | 1988.4735 | [14 empty] | No DSI or ACI control
|  | mmbtu/hr = | [5 empty] | 1780.7225 | NA
Ultra-Low Sulfur Coal 02/5/2014
Run 4 |  | Unit 1 | 1A | 1B | 1C | 1D
902 | 1019 | 80 | 528023 | 515456 | 666897 | 84638
|  |  | 528345 | 515456 | 667331 | 85073
|  | Delta = | 322 | 0 | 434 | 435 | 0 | 1191
|  | Coal mmbtu = | [5 empty] | 8866 |  | AU03003 | 0.27 | 25 | 0.056 | 6.36 |  | 119100 | 3.0622 | 0.0028999 | 0.57861 | 119100 | 0.0066696 | 6.3163 | Low Load Outlet Cold ESP PM Baseline
|  | mmbtu/run = | [5 empty] | 1055.9406 | [14 empty] | No DSI or ACI control
|  | mmbtu/hr = | [5 empty] | 822.8109 | NA
Run 5 |  | Unit 1 | 1A | 1B | 1C | 1D
1432 | 1520 | 130 | 529660 | 516675 | 668816 | 86556
|  |  | 529947 | 517002 | 669143 | 86883
|  | Delta = | 287 | 327 | 327 | 327 | 0 | 1268
|  | Coal mmbtu = | [5 empty] | 8866 |  | AU03003 | 0.27 | 25 | 0.056 | 6.36 |  | 126800 | 3.2601 | 0.0028999 | 0.57861 | 126800 | 0.0071008 | 6.3163 | Mid Load Inlet Hot ESP PM Baseline/Particle Sizing
|  | mmbtu/run = | [5 empty] | 1124.2088 | [14 empty] | No DSI or ACI control
|  | mmbtu/hr = | [5 empty] | 1297.164 | NA
Run 6 |  | Unit 1 | 1A | 1B | 1C | 1D
1610 | 1705 | 130 | 530215 | 517309 | 669451 | 87190
|  |  | 530523 | 517659 | 669801 | 87540
|  | Delta = | 308 | 350 | 350 | 350 | 0 | 1358
|  | Coal mmbtu = | [5 empty] | 8866 |  | AU03003 | 0.27 | 25 | 0.056 | 6.36 |  | 135800 | 3.4915 | 0.0028999 | 0.57861 | 135800 | 0.0076048 | 6.3163 | Mid Load Inlet Hot ESP PM Baseline/Grain Loading
|  | mmbtu/run = | [5 empty] | 1204.0028 | [14 empty] | No DSI or ACI control
|  | mmbtu/hr = | [5 empty] | 1313.4576 | NA
Ultra-Low Sulfur Coal 02/6/2014
Run 7 |  | Unit 1 | 1A | 1B | 1C | 1D
810 | 857 | 170 | 534017 | 522355 | 674491 | 92230
PM Grain Loading |  |  | 534400 | 522740 | 674868 | 92608
Inlet Hot ESP |  | Delta = | 383 | 385 | 377 | 378 | 0 | 1523
|  | Coal mmbtu = | [5 empty] | 8626 |  | AU03180 | 0.28 | 65 | 0.049 | 6.9 |  | 152300 | 10.1809 | 0.0077496 | 0.61674 | 152300 | 0.0074627 | 5.6805 | Full Load Inlet Hot ESP PM Baseline/Grain Loading
|  | mmbtu/run = | [5 empty] | 1313.7398 | [14 empty] | No DSI or ACI control
|  | mmbtu/hr = | [5 empty] | 1677.1146 | NA
Run 8 |  | Unit 1 | 1A | 1B | 1C | 1D
920 | 1019 | 160 | 534573 | 522912 | 675021 | 92776
PM Grain Loading |  |  | 535051 | 523397 | 675418 | 93243
Inlet Hot ESP |  | Delta = | 478 | 485 | 397 | 467 | 0 | 1827
|  | Coal mmbtu = | [5 empty] | 8626 |  | AU03180 | 0.28 | 65 | 0.049 | 6.9 |  | 182700 | 12.2131 | 0.0077496 | 0.61674 | 182700 | 0.0089523 | 5.6805 | Full Load Inlet Hot ESP PM Baseline/Particle Sizing
|  | mmbtu/run = | [5 empty] | 1575.9702 | [14 empty] | No DSI or ACI control
|  | mmbtu/hr = | [5 empty] | 1602.6816 | NA
Note on E4: Waters, G. Dwain: measured as 100lb flow
Note on F4: Waters, G. Dwain: measured as 100lb flow
Note on G4: Waters, G. Dwain: measured as 100lb flow
Note on H4: Waters, G. Dwain: measured as 100lb flow
Note on I4: Waters, G. Dwain: measured as 100lb flow
Note on K5: Waters, G. Dwain: F-factor Heat Input Calculated in Test Run
Note on B6: Waters, G. Dwain: End Time
Note on D6: Waters, G. Dwain: Unit Load
Note on U6: Waters, G. Dwain: MATS HCl limit
Note on Y6: Waters, G. Dwain: MATS Hg limit
Note on D8: Waters, G. Dwain: total as 100 lbs.
Note on J8: Waters, G. Dwain: as 100lbs flow
Note on O9: Waters, G. Dwain: Default Cl MDL
Note on T9: Waters, G. Dwain: Cl to HCl conversation is 1.02843 factor
Note on J11: Waters, G. Dwain: Coal mbtu/hr
Note on B14: Waters, G. Dwain: End Time
Note on D14: Waters, G. Dwain: Unit Load
Note on D16: Waters, G. Dwain: total as 100 lbs.
Note on J16: Waters, G. Dwain: as 100lbs flow
Note on O17: Waters, G. Dwain: Default Cl MDL
Note on T17: Waters, G. Dwain: Cl to HCl conversation is 1.02843 factor
Note on J19: Waters, G. Dwain: Coal mbtu/hr
Note on B22: Waters, G. Dwain: End Time
Note on D22: Waters, G. Dwain: Unit Load
Note on D24: Waters, G. Dwain: total as 100 lbs.
Note on J24: Waters, G. Dwain: as 100lbs flow
Note on O25: Waters, G. Dwain: Default Cl MDL
Note on T25: Waters, G. Dwain: Cl to HCl conversation is 1.02843 factor
Note on J27: Waters, G. Dwain: Coal mbtu/hr
Note on K29: Waters, G. Dwain: F-factor Heat Input Calculated in Test Run
Note on B30: Waters, G. Dwain: End Time
Note on D30: Waters, G. Dwain: Unit Load
Note on D32: Waters, G. Dwain: total as 100 lbs.
Note on J32: Waters, G. Dwain: as 100lbs flow
Note on O33: Waters, G. Dwain: Default Cl MDL
Note on T33: Waters, G. Dwain: Cl to HCl conversation is 1.02843 factor
Note on J35: Waters, G. Dwain: Coal mbtu/hr
Note on K37: Waters, G. Dwain: F-factor Heat Input Calculated in Test Run
Note on B38: Waters, G. Dwain: End Time
Note on D38: Waters, G. Dwain: Unit Load
Note on D40: Waters, G. Dwain: total as 100 lbs.
Note on J40: Waters, G. Dwain: as 100lbs flow
Note on O41: Waters, G. Dwain: Default Cl MDL
Note on T41: Waters, G. Dwain: Cl to HCl conversation is 1.02843 factor
Note on J43: Waters, G. Dwain: Coal mbtu/hr
Note on K45: Waters, G. Dwain: F-factor Heat Input Calculated in Test Run
Note on B46: Waters, G. Dwain: End Time based on operator log; different than actual stack test period.
Note on D46: Waters, G. Dwain: Unit Load
Note on D48: Waters, G. Dwain: total as 100 lbs.
Note on J48: Waters, G. Dwain: as 100lbs flow
Note on O49: Waters, G. Dwain: Default Cl MDL
Note on T49: Waters, G. Dwain: Cl to HCl conversation is 1.02843 factor
Note on J51: Waters, G. Dwain: Coal mbtu/hr
Note on K53: Waters, G. Dwain: F-factor Heat Input Calculated in Test Run
Note on B54: Waters, G. Dwain: End Time based on operator log; different than actual stack test period.
Note on D54: Waters, G. Dwain: Unit Load
Note on D56: Waters, G. Dwain: total as 100 lbs.
Note on J56: Waters, G. Dwain: as 100lbs flow
Note on T57: Waters, G. Dwain: Cl to HCl conversation is 1.02843 factor
Note on J59: Waters, G. Dwain: Coal mbtu/hr
Note on K61: Waters, G. Dwain: F-factor Heat Input Calculated in Test Run
Note on B62: Waters, G. Dwain: End Time
Note on D62: Waters, G. Dwain: Unit Load
Note on D64: Waters, G. Dwain: total as 100 lbs.
Note on J64: Waters, G. Dwain: as 100lbs flow
Note on T65: Waters, G. Dwain: Cl to HCl conversation is 1.02843 factor
Note on J67: Waters, G. Dwain: Coal mbtu/hr