## Project Summary
St. Petersburg - SW WRF
Biosolids Improvement Project (BIP)
Major/Minor Source & 62-210.300, FAC Exemption Applicability Determination
| PSD Applicability Determination[3] |  |  |  |  | 62-210.300, FAC Exemption Applicability Determination
|  | Projected Annual Emissions (tpy) of PSD Pollutants from BIP Project |  |  |  |  | Exemption for Natural Gas Boilers (62-210.300(3)(a)(34), FAC ) | [5 empty] | Exemption for Natural Diesel Generators (62-210.300(3)(a)(35),FAC )
|  |  | BIP PTE | Major Source Threshold (tpy) | Equals/ExceedsMajor Source Threshold? (Yes/No) |  | Per Unit Threshold for Exemption (mmscf/yr) | Per Unit Projected Fuel Use | Combined Fuel Use Threshold for Exemption (tpy) | Combined Projected Fuel Use from Both Units | Qualifies for Exemption? |  | Combined Fuel Use Threshold for Exemption (gallons/year) | Combined Projected Fuel Use from Both Units | Qualifies for Exemption?
|  | NOX | 38.582 | 250 | No |  | 150 | 54.8273 | 375 | 109.6546 | Yes |  | 64000 | 26400 | Yes
|  | CO | 55.0155 | 250 | No
|  | VOC | 16.1074 | 250 | No |  | Generic Exemption Applicability for Flares, Carbon Scrubbers, & Cooling Tower (62-210.300(3)(b)(1)(c), FAC)
|  | SO2 | 40.0279 | 250 | No
|  | PM(filterable)[4] | 1.4246 | 250 | No |  | Threshold | Lead | HAPs |  | Other[1]
|  | PM10(filterable+condensible) | 2.5707 | 250 | No |  |  |  | Indvidual | Total |  | Exemption Applies? (Yes/No)
|  | PM2.5(filterable+condensible) | 2.5281 | 250 | No |  |  | 500 lb/yr | 1,000 lb/yr | 2,500 lb/yr | 5.0 tpy
|  | Lead | 2.7414e-05 | 250 | No |  | Flare 1 | NA |  |  | 2.2861 | Yes
|  | H2SO4 | 0.12814 | 250 | No |  | Flare 2 |  |  |  | 0.86532 | Yes
|  | H2S | 1.5343 | 250 | No |  | Flare 3 |  |  |  | 36.7926 | No
|  | CO2 | 19203.3787 | -- | -- |  | Flare 4 |  |  |  | 0.04244 | Yes
|  | CH4 | 106.3759 | -- | -- |  | Scrubbers |  |  |  | 1.5343 | Yes
|  | N2O | 0.12062 | -- | -- |  | Cooling Tower |  |  |  | 0.10649 | Yes
|  | GHG - Mass Basis | 19309.8753 | -- | --
|  | GHG - CO2e Basis | 21898.7222 | 100000 | No |  | Generic Exemption Applicability for Flares, Carbon Scrubbers, & Cooling Tower (62-210.300(3)(b)(1)(b), FAC)
[8 empty] | Facility PTE | Title V Threshold (tpy) | Equals/Exceeds Threshold? (Yes/No)
| Title V Applicability Determination | [5 empty] | NOX | 40.1932 | 100 | No
[7 empty] | CO | 55.1042 | 100 | No
[7 empty] | VOC | 16.1399 | 100 | No
|  | Projected Annual Emissions (tpy) From Entire Facility |  |  |  |  | SO2 | 40.0294 | 100 | No
|  |  | PTE | Major Source Threshold (tpy) | Equals/ExceedsMajor Source Threshold? (Yes/No) |  | PM(filterable)[4] | 1.432 | 100 | No
|  | NOX | 40.1932 | 100 | No |  | PM10(filterable+condensible) | 2.5781 | 100 | No
|  | CO | 55.1042 | 100 | No |  | PM2.5(filterable+condensible) | 2.5355 | 100 | No
|  | VOC | 16.1399 | 100 | No |  | Lead | 2.7414e-05 | 100 | No
|  | SO2 | 40.0294 | 100 | No |  | H2SO4 | 0.13038 | 100 | No
|  | PM(filterable)[4] | 1.432 | 100 | No |  | H2S | 1.5343 | 100 | No
|  | PM10(filterable+condensible) | 2.5781 | 100 | No |  | CO2 | 19358.9347 | -- | --
|  | PM2.5(filterable+condensible) | 2.5355 | 100 | No |  | CH4 | 106.3845 | -- | --
|  | Lead | 2.7414e-05 | 5 | No |  | N2O | 0.12062 | -- | --
|  | H2SO4 | 0.13038 | 100 | No |  | GHG - Mass Basis | 19465.4398 | -- | --
|  | H2S | 2.717 | 100 | No |  | GHG - CO2e Basis | 22054.4909 | 100000 | No
|  | CO2 | 19358.9347 | -- | --
|  | CH4 | 106.3845 | -- | --
|  | N2O | 0.12062 | -- | --
|  | GHG - Mass Basis[5] | 19465.4398 | 100 | Yes
|  | GHG - CO2e Basis | 22054.4909 | 100000 | No
|  | Projected Annual Emissions (tpy) of Individual HAPs from Entire Project |  | Major Source Threshold (tpy) | Equals/ExceedsMajor Source Threshold? (Yes/No)
PTE
|  | 1,1,2,2 Tetrachloroethane | 0.0033644 | 10 | No
|  | 1,1,2 Trichloroethane | 0.0026747 | 10 | No
|  | 1,3 Butadiene | 0.022457 | 10 | No
|  | 1,3 Dichloropropene | 0.0022205 | 10 | No
|  | 2,2,4 Trimethylpentane | 0.021027 | 10 | No
|  | Acetaldehyde | 0.7032 | 10 | No
|  | Acrolein | 0.43234 | 10 | No
|  | Benzene | 0.038526 | 10 | No
|  | Biphenyl | 0.017831 | 10 | No
|  | Carbon Tetrachloride | 0.0030868 | 10 | No
|  | Chlorobenzene | 0.0025569 | 10 | No
|  | Chloroform | 0.0023971 | 10 | No
|  | Dichlorobenzene | 6.5793e-05 | 10 | No
|  | Ethylene Dibromide | 0.003726 | 10 | No
|  | Formaldehyde | 4.4452 | 10 | No
|  | Methanol | 0.21027 | 10 | No
|  | Methylene Chloride | 0.0016822 | 10 | No
|  | Napthalene | 0.0065263 | 10 | No
|  | Hexane | 0.19205 | 10 | No
|  | Phenol | 0.0020186 | 10 | No
|  | Styrene | 0.001985 | 10 | No
|  | Tetrachloroethylene | 0.00020859 | 10 | No
|  | Toluene | 0.035011 | 10 | No
|  | Vinyl Chloride | 0.0012532 | 10 | No
|  | Xylene | 0.015825 | 10 | No
|  | Polycyclic Organic Matter[2] | 0.0087914 | 10 | No
|  | Lead | 2.7414e-05 | 10 | No
|  | Arsenic | 1.8876e-05 | 10 | No
|  | Beryllium | 5.3109e-06 | 10 | No
|  | Cadmium | 7.9853e-05 | 10 | No
|  | Chromium | 0.00016517 | 10 | No
|  | Cobalt | 4.6055e-06 | 10 | No
|  | Manganese | 4.0377e-05 | 10 | No
|  | Mercury | 5.1479e-05 | 10 | No
|  | Nickel | 0.00042968 | 10 | No
|  | Selenium | 1.3159e-06 | 10 | No
|  | Total HAPs Project PTE (tpy) | 6.1771 | 25 | No
Notes [ ]:
1. 62-210.300(3)(b)(1)(c.), FAC specifies that the unit must not have the potential to emit 5.0 tpy of any regulated pollutant (other than HAPs and Lead) as defined by 62-210.200, FAC.
For the BIP Project flares and cooling tower, these "other" pollutants include NOX, VOC, SO2, PM10, PM2.5 and PM, PM10 and PM2.5, respectively. Only the maximum amount emitted is shown
here. Please see "Flares", "Carbon Scrubber Emissions", and "Cooling Tower" for individual pollutant emissions.
2. Polycyclic Organic Matter includes Polycyclic Aromatic Hydrocarbons (PAH) emissions from the relocated diesel generator.
3. The 1,750 kW diesel generator is being relocated from the Albert Whitted facility to the SWWRF. Therefore, it is considered a new emissions source and is included as a component of
the BIP Project and its PTE is included in the PSD major source applicability deteremination. The 2,000 kW generator is currently located at the SWWRF. Therefore, the 2,000 kW emissions are
not included in the PSD major source applicability determination and it is only shown in this appendix in order to determine Title V Major Source applicability and the applicability of exemptions
pursuant to 62-210.300, FAC.
4. USEPA issued a final rule (Reference 2) which removed a requirement in the definition of "regulated NSR pollutant" to include condensable PM when measuring one of the emissions-related
indicators for particulate pollutant" to include condensable PM when measuring one of the emissions-related indicators for particulate matter known as "particulate matter emissions" in
the context of the PSD and NSR regulations; therefore, only the filterable portion is regulated with regards to PM emissions.
5. According to USEPA guidance after July 1, 2011 existing and newly constructed facilites must have GHG PTEs that equal or exceed 100 tpy on a mass basis and 100,000 tpy on a CO2e basis.

## Gas Engines
St. Petersburg - SW WRF
Biosolids Improvement Project (BIP)
Potential to Emit - Gas - Fired Engine Generators
Cummins Model C1100 N6C
| No. of Engines | 2
| Engine Output | 1517 | hp[1]
| Heat Input (HHV) | 9.6015 | MBtu/hr[1,6]
| Exhaust Gas Flow @100% Load | 6650 | acfm[1]
| Annual Hours of Operation | 8760 | hrs
| Exhaust Gas Temperature | 757 | °F[1]
| SO2 to SO3 Conversion Rate (assumed) | 100 | %
| Molecular Weight of SO2 | 64 | lb/lb-mol
| Molecular Weight of H2SO4 | 98 | lb/lb-mol
Emission Factors PSD Pollutants
| NOX | 1 | g/hp-hr[1,2]
| NMHC (VOCs) | 0.5 | g/hp-hr[1,2]
| PM10(filterable) | 0.03 | g/hp-hr[1,2]
| PM2.5(filterable) | 0.03 | g/hp-hr[1,2]
| PM(filterable) | 0.03 | g/hp-hr[1,2]
| PM(condensible) | 0.00991 | lb/Mbtu[4]
| SO2 | 0.000588 | lb/Mbtu[4]
| CO | 1.6 | g/hp-hr[1]
| CO2 | 6.4 | % (dry)[1,3]
|  | 64000 | ppmvd
| CH4 | 1.25 | lb/Mbtu[4]
Annual Emissions of PSD Pollutants with Both Engines Operating
| NOX | 29.2972 | tpy
| NMHC (VOCs) | 14.6486 | tpy
| PM10(Filterable+Condensible) | 1.7124 | tpy[5]
| PM2.5(Filterable+Condensible) | 1.7124 | tpy[5]
| PM(filterable) | 0.87892 | tpy[5,7]
| SO2 | 0.049456 | tpy
| H2SO4[9] | 0.07573 | tpy
| CO | 46.8755 | tpy
| CO2 | 11078.8587 | tpy
| CH4 | 105.1364 | tpy
| CO2e[8] | 13707.2693 | tpy
| Hazardous Air Pollutants (HAPS) | Emission Factors (lb/MBtu)[4] | Emission Rate (lb/hr) (per unit) | PTE (tpy) (Both Engines Operating)
| 1,1,2,2 Tetrachloroethane | 4e-05 | 0.00038406 | 0.0033644
| 1,1,2 Trichloroethane | 3.18e-05 | 0.00030533 | 0.0026747
| 1,3 Butadiene | 0.000267 | 0.0025636 | 0.022457
| 1,3 Dichloropropene | 2.64e-05 | 0.00025348 | 0.0022205
| 2,2,4 Trimethylpentane | 0.00025 | 0.0024004 | 0.021027
| Acetaldehyde | 0.00836 | 0.080269 | 0.70315
| Acrolein | 0.00514 | 0.049352 | 0.43232
| Benzene | 0.00044 | 0.0042247 | 0.037008
| Biphenyl | 0.000212 | 0.0020355 | 0.017831
| Carbon Tetrachloride | 3.67e-05 | 0.00035238 | 0.0030868
| Chlorobenzene | 3.04e-05 | 0.00029189 | 0.0025569
| Chloroform | 2.85e-05 | 0.00027364 | 0.0023971
| Ethylene Dibromide | 4.43e-05 | 0.00042535 | 0.003726
| Formaldehyde | 0.0528 | 0.50696 | 4.441
| Methanol | 0.0025 | 0.024004 | 0.21027
| Methylene Chloride | 2e-05 | 0.00019203 | 0.0016822
| Napthalene | 7.44e-05 | 0.00071435 | 0.0062577
| Hexane | 0.00111 | 0.010658 | 0.093361
| Phenol | 2.4e-05 | 0.00023044 | 0.0020186
| Styrene | 2.36e-05 | 0.0002266 | 0.001985
| Tetrachloroethylene | 2.48e-06 | 2.3812e-05 | 0.00020859
| Toluene | 0.000408 | 0.0039174 | 0.034317
| Vinyl Chloride | 1.49e-05 | 0.00014306 | 0.0012532
| Xylene | 0.000184 | 0.0017667 | 0.015476
| Polycyclic Organic Matter | -- | 0.00095927 | 0.0084032
| 2 Methylnaphthalene | 3.32e-05 | 0.00031877 | --
| Acenaphthene | 1.25e-06 | 1.2002e-05 | --
| Acenaphthylene | 5.53e-06 | 5.3096e-05 | --
| Benzo(b)fluoranthene | 1.66e-07 | 1.5938e-06 | --
| Benzo(g,h,i)perylene | 4.14e-07 | 3.975e-06 | --
| Benzo(e)pyrene | 4.15e-07 | 3.9846e-06 | --
| Chrysene | 6.93e-07 | 6.6538e-06 | --
| Ethylbenzene | 3.97e-05 | 0.00038118 | --
| Fluoranthene | 1.11e-06 | 1.0658e-05 | --
| Fluorene | 5.67e-06 | 5.4441e-05 | --
| Phenanthrene | 1.04e-05 | 9.9856e-05 | --
| Pyrene | 1.36e-06 | 1.3058e-05 | --
|  |  | Total HAPs | 6.07
Notes [ ]:
1. Based on preliminary vendor data.
2. Emissions assuming 5% O2 concentration in exhaust gas.
3. Preliminary vendor data contains CO2 exaust percentage by volume on a dry basis. The value is conservatively
assumed to be on an actual basis in this Appendix.
4. Emission factor obtained from AP-42 (Reference 1a).
5. Assumes all PM is less than 2.5 microns.
6. Based on ratio of average heat content of natural gas at LHV & HHV. HHV=LHV*1.11
7. USEPA issued a final rule (Reference 2) which removed a requirement in the definition of "regulated NSR
pollutant" to include condensable PM when measuring one of the emissions-related indicators for particulate
matter known as "particulate matter emissions" in the context of the PSD and NSR regulations; therefore,
only the filterable portion is regulated with regards to PM emissions.
8. CO2 equivalents (CO2e) based on the global warming potential for applicable pollutant as listed in
Table A-1 to Subpart A of 40 CFR Part 98 - Global Warming Potentials.
9. Assumes 100% (by volume) of SO2 oxidized to form SO3.
References:
1. | USEPA, AP-42, Fifth Edition, Vol. I. Chapter 3 "Stationary Internal Combustion Sources", Section 3.2
"Natural Gas-Fired Reciprocating Engines". April 2000.
a. Table 3.2-2 "Uncontrolled Emission Factors For 4-Stroke Lean-Burn Engines."
2. | “Implementation of the New Source Review (NSR) Program for Particulate Matter Less Than 2.5
Micrometers (PM2.5): Amendment to the Definition of "Regulated NSR Pollutant" Concerning
Condensable Particulate Matter”, 77 Federal Register 207 (25 October 2012), pp. 65107 - 65119.

## Flares
St. Petersburg - SW WRF
Biosolids Improvement Project (BIP)
Potential to Emit - Flares
| Flare | Maximum Output (scfm)[1]
| Flare 1 - Enclosed Flare to Combust Excess Gas from Digesters 1 & 2 | 760 | scfm
| Flare 2 - Candlestick Flare to Combust Excess Gas from Digester 3 (16-inch pressure zone) | 600 | scfm
| Flare 3 - Thermal Oxidizer to Combust Waste Gas From BUS | 140 | scfm
| Flare 4 - Candlestick Startup Flare Combusting BUS Product Gas | 200 | scfm
| Emissions Factors | Flare 1 [1] | Flare 3[1] | Flares 2 & 4[2]
| NOX (lb/MBtu) | 0.06 | 0.06 | 0.068
| CO (lb/MBtu) | 0.15 | 0.3 | 0.37
| VOC (lb/MBtu) | 0.08 | 0.08 | 0.14
| PM (lb/mmscf)[3] | 60 | -- | --
| PM10 (lb/mmscf)[3] | 60 | -- | --
| PM2.5 (lb/mmscf)[3] | 60 | -- | --
| CO2 (lb/MBtu)[4] | 116.98 | 116.98 | 116.98
| CH4 (lb/MBtu)[5] | 0.077 | 0.077 | 0.077
| N2O(lb/Mbtu)[4] | 0.00022 | 0.00022 | 0.00022
Add N2O Emissions Part 98 Table C-1
| H2S Concentration in Digester Gas Upstream of Biogas Upgrade System (BUS) | 3000 | ppmv[6]
| H2S Concentration in BUS Product Gas | 50 | ppmv[1]
| Heat Content of Digester Gas Upstream of Biogas Upgrade System (BUS) | 645 | Btu/scf[6]
| Heat Content of BUS Waste Gas | 186 | Btu/scf[1]
| Heat Content of BUS Product Gas | 990 | Btu/scf[1]
| Heat Content of Pilot Fuel Gas | 1020 | Btu/scf[9]
| Temperature of Digester Gas | 83 | °F[1]
| Temperature of BUS Product Gas | 100 | °F[1]
| Moecular Weight of SO2 | 64 | lb/lb-mol
| Flare 1 Gas Throughput | 9435039 | scf/yr[6]
| Flare 1 Pilot Gas Throughput | 438000 | scf/yr[6]
| Flare 2 Gas Throughput | 3570459 | scf/yr[6]
| Flare 2 Pilot Gas Throughput | 438000 | scf/yr[6]
| Flare 3 Gas Throughput | 73584000 | scf/yr[6]
| Flare 3 Pilot Gas Throughput | 876000 | scf/yr[6]
| Flare 4 Gas Throughput | 6088 | scf/yr[6]
| Flare 4 Pilot Gas Throughput | 219000 | scf/yr[6]
Annual Emissions (tpy) of PSD Pollutants from Flaring of Gas
|  | Flare 1 | Flare 2 | Flare 3 | Flare 4
| NOX | 0.18257 | 0.0783 | 0.4106 | 0.00020492
| CO | 0.45642 | 0.42605 | 2.053 | 0.001115
| VOC | 0.24342 | 0.16121 | 0.54746 | 0.0004219
| SO2 | 2.2858 | 0.865 | 36.792 | 2.3835e-05
| PM[3] | 0.28305 | -- | -- | --
| PM10[3] | 0.28305 | -- | -- | --
| PM2.5[3] | 0.28305 | -- | -- | --
| CO2 | 355.9468 | 134.6993 | 800.5306 | 0.35253
| CH4 | 0.2343 | 0.088663 | 0.52694 | 0.00023204
| N2O | 0.00066942 | 0.00025332 | 0.0015055 | 6.6298e-07
| CO2e[8] | 362.0036 | 136.9914 | 814.1527 | 0.35852
Annual Emissions (tpy) of PSD Pollutants from Flare Pilots[2]
|  | Flare 1 | Flare 2 | Flare 3 | Flare 4
| NOX | 0.01519 | 0.01519 | 0.03038 | 0.0075949
| CO | 0.082651 | 0.082651 | 0.1653 | 0.041325
| VOC | 0.031273 | 0.031273 | 0.062546 | 0.015637
| SO2[7] | 0.00031286 | 0.00031286 | 0.00062571 | 0.00015643
| CO2[4] | 26.131 | 26.131 | 52.262 | 13.0655
| CH4 | 0.0172 | 0.0172 | 0.034401 | 0.0083472
| N2O | 4.9144e-05 | 4.9144e-05 | 9.8287e-05 | 2.3849e-05
| CO2e[8] | 26.5756 | 26.5756 | 53.1513 | 13.2813
Total Annual Emissions (tpy) of PSD Pollutants from Flaring of Gas & Pilot Emissions
|  | Flare 1 | Flare 2 | Flare 3 | Flare 4
| NOX | 0.19776 | 0.09349 | 0.44098 | 0.0077998
| CO | 0.53907 | 0.5087 | 2.2183 | 0.04244
| VOC | 0.2747 | 0.19248 | 0.61001 | 0.016058
| SO2[7] | 2.2861 | 0.86532 | 36.7926 | 0.00018026
| PM[3] | 0.28305 | -- | -- | --
| PM10[3] | 0.28305 | -- | -- | --
| PM2.5[3] | 0.28305 | -- | -- | --
| CO2[4] | 382.0777 | 160.8303 | 852.7926 | 13.418
| CH4 | 0.2515 | 0.10586 | 0.56134 | 0.0085792
| N2O | 0.00071856 | 0.00030247 | 0.0016038 | 2.4512e-05
| CO2e[8] | 388.5793 | 163.567 | 867.3039 | 13.6398
Notes [ ]:
1. Information obtained from Brown & Caldwell 30% Preliminary Design Report (PDR) and Technical
Specifications - Volume No. 2, 60% Submittal.
2. Emission factor obtained from AP-42 (Reference 1a).
3. Assumed to be both filterable and condensible & less than 2.5 microns.
4. CO2 emission factor obtained from Table C-1 to Subpart C of 40 CFR Part 98. Conservatively used
emission factor for natural gas for each flare as the value is greater than the emission factor for
combusted biogas.
5. Emission factor obtained from AP-42 (Reference 1b.). Methane emissions are assumed to be 55%
of total VOC emissions.
6. Calculated using information obtained from "Air Permit Info.xlsx" sent to Black & Veatch on 12/6/2013
from Christian Aristizabal of Brown & Caldwell.
7. Assumes 1 grain per 100 scf sulfur content in the pilot gas and all sulfur in the fuel is converted to SO2
during combustion.
8. CO2 equivalents (CO2e) based on the global warming potential for applicable pollutant as listed in
Table A-1 to Subpart A of 40 CFR Part 98 - Global Warming Potentials.
9. Assumed value.
1. | References:
USEPA, AP-42, Fifth Edition, Vol. I. Chapter 13 "Miscellaneous Sources", Section 13.5
"Industrial Flares". April 2000.
a. Table 13.5-1 "Emission Factors for Flare Operations".
b. Table 13.5-2 "Hydrocarbon Composition of Flare Emission"

## Boilers
St. Petersburg - SW WRF
Biosolids Improvement Project (BIP)
Potential to Emit - Backup Heating Boilers for Digesters
Basis:
Number of Units |  |  | 2
Fuel |  |  | Natural Gas
Heat Input |  |  | 6.384 | mmBtu/hr [1]
Heating Value of Fuel |  |  | 990 | Btu/scf [2]
Fuel Burn Rate |  |  | 0.0062588 | mmscf/hr[1]
SO2 to SO3 Conversion Rate |  |  | 100 | % by volume (assumed)
Fuel consumed by each unit operating 8760 hours per year |  |  | 54.8273 | mmscf/yr
Combined fuel consumed by both units operating 8760 hours per year |  |  | 109.6546 | mmscf/yr
Global Warming Potentials [3]
CO2 | 1
CH4 | 25
N2O | 298
Annual Potential Emissions
Pollutant | Mass Emission Rate (Per Unit) |  |  | Annual Emissions When Both Units Operating 8760 hrs (tpy)
| (lb/mmscf) | Notes | (lb/hr)
CO | 84 | [4] | 0.52574 | 4.6055
NOX | 100 | [4] | 0.62588 | 5.4827
PM | 1.9 | [6, 7] | 0.011892 | 0.10417
PM10 | 7.6 | [6, 8] | 0.047567 | 0.41669
PM2.5 | 7.6 | [6, 8] | 0.047567 | 0.41669
SO2 | 0.6 | [9] | 0.0037553 | 0.032896
VOC | 5.5 | [6] | 0.034424 | 0.30155
Lead | 0.0005 | [6] | 3.1294e-06 | 2.7414e-05
H2SO4 | 0.91875 | [10] | 0.0057503 | 0.050373
CO2 | 120000 | [6] | 751.0588 | 6579.2753
CH4 | 2.3 | [6] | 0.014395 | 0.1261
N2O | 2.2 | [6] | 0.013769 | 0.12062
GHG-CO2e | -- | [11] | -- | 6618.3726
CAS | Pollutant | Mass Emission Rate (per unit) |  |  | PTE
Number |  | (lb/mmscf) | Notes | (lb/hr) | (tpy)
71-43-2 | Benzene | 0.0021 | [12] | 1.3144e-05 | 0.00011514
25321-22-6 | Dichlorobenzene | 0.0012 | [12] | 7.5106e-06 | 6.5793e-05
50-00-0 | Formaldehyde | 0.075 | [12] | 0.00046941 | 0.004112
110-54-3 | Hexane | 1.8 | [12] | 0.011266 | 0.098689
91-20-3 | Naphthalene | 0.00061 | [12] | 3.8179e-06 | 3.3445e-05
-- | Polycyclic Organic Matter | 8.82e-05 | [12, 4] | 5.5203e-07 | 4.8358e-06
91-57-6 | 2-Methylnaphthalene | 2.4e-05 | [12, 5] | -- | --
56-49-5 | 3-Methylchloranthrene | 1.8e-06 | [12, 5] | -- | --
57-97-6 | 7,12-Dimethylbenz(a)anthracene | 1.6e-05 | [12, 5] | -- | --
83-32-9 | Acenaphthene | 1.8e-06 | [12, 5] | -- | --
203-96-8 | Acenaphthylene | 1.8e-06 | [12, 5] | -- | --
120-12-7 | Anthracene | 2.4e-06 | [12, 5] | -- | --
56-55-3 | Benz(a)anthracene | 1.8e-06 | [12, 5] | -- | --
50-32-8 | Benzo(a)pyrene | 1.2e-06 | [12, 5] | -- | --
205-99-2 | Benzo(b)fluoranthene | 1.8e-06 | [12, 5] | -- | --
191-24-2 | Benzo(g,h,i)perylene | 1.2e-06 | [12, 5] | -- | --
205-82-3 | Benzo(k)fluoranthene | 1.8e-06 | [12, 5] | -- | --
218-01-9 | Chrysene | 1.8e-06 | [12, 5] | -- | --
53-70-3 | Dibenzo(a,h)anthracene | 1.2e-06 | [12, 5] | -- | --
206-44-0 | Fluoranthene | 3e-06 | [12, 5] | -- | --
86-73-7 | Fluorene | 2.8e-06 | [12, 5] | -- | --
193-39-5 | Indeno(1,2,3-cd)pyrene | 1.8e-06 | [12, 5] | -- | --
85-01-8 | Phenanathrene | 1.7e-05 | [12, 5] | -- | --
129-00-0 | Pyrene | 5e-06 | [12, 5] | -- | --
108-88-3 | Toluene | 0.0034 | [12] | 2.128e-05 | 0.00018641
[6] | Lead | 0.0005 | [13] | 3.1294e-06 | 2.7414e-05
[6] | Arsenic | 0.0002 | [13] | 1.2518e-06 | 1.0965e-05
[6] | Beryllium | 1.2e-05 | [13] | 7.5106e-08 | 6.5793e-07
[6] | Cadmium | 0.0011 | [13] | 6.8847e-06 | 6.031e-05
[6] | Chromium | 0.0014 | [13] | 8.7624e-06 | 7.6758e-05
[6] | Cobalt | 8.4e-05 | [13] | 5.2574e-07 | 4.6055e-06
[6] | Manganese | 0.00038 | [13] | 2.3784e-06 | 2.0834e-05
[6] | Mercury | 0.00026 | [13] | 1.6273e-06 | 1.4255e-05
[6] | Nickel | 0.0021 | [13] | 1.3144e-05 | 0.00011514
[6] | Selenium | 2.4e-05 | [13] | 1.5021e-07 | 1.3159e-06
|  |  |  | Total HAPs | 0.10354
Notes [ ]:
1. Based on preliminary vendor data.
2. Based on design data.
3. CO2 equivalents (CO2e) based on the global warming potential for applicable pollutant as listed in
Table A-1 to Subpart A of 40 CFR Part 98 - Global Warming Potentials.
4. Emission factor obtained from AP-42 (Reference 1a); for a small boiler (<100 mmBtu/hr), uncontrolled.
5. Pollutant is assumed to be a POM.
6. Emission factor obtained from AP-42 (Reference 1b).
7. USEPA issued a final rule (Reference 2) which removed a requirement in the definition of "regulated NSR
pollutant" to include condensable PM when measuring one of the emissions-related indicators for particulate
matter known as "particulate matter emissions" in the context of the PSD and NSR regulations; therefore,
only the filterable portion is regulated with regards to PM emissions.
8. Based on information provided in AP-42 (Reference 1), all particulate matter (filterable and condensable) is
assumed to be less than 1.0 micrometer in diameter.
9. Assumed all sulfur in the fuel is converted to SO2.
10. Assumes 100% (by volume) of SO2 is oxidized to form SO3.
11. The GHG emissions is the sum of all applicable GHG pollutants.
12. Emission factor obtained from AP-42 (Reference 1c).
13. Emission factor obtained from AP-42 (Reference 1d).
14. Polycyclic Organic Matter (POM) emissions is the summation of individual POM pollutants.
References:
1. USEPA, AP-42, Fifth Edition, Vol. I. Chapter 1 "External Combustion Sources", Section 1.4 "Natural Gas
Combustion". July 1998.
a. | Table 1.4-1 "Emission Factors for Nitrogen Oxides (NOX) and Carbon Monoxide (CO) from
Natural Gas Combustion".
b. | Table 1.4-2 "Emission Factors for Criteria Pollutants and Greenhouse Gases from Natural
Gas Combustion".
c. | Table 1.4-3 "Emission Factors for Speciated Organic Compounds from Natural
Gas Combustion".
d. | Table 1.4-4 "Emission Factors for Metals from Natural Gas Combustion".
2. “Implementation of the New Source Review (NSR) Program for Particulate Matter Less Than 2.5
Micrometers (PM2.5): Amendment to the Definition of "Regulated NSR Pollutant" Concerning
Condensable Particulate Matter”, 77 Federal Register 207 (25 October 2012), pp. 65107 - 65119.

## New Carbon Scrubber Emissions
St. Petersburg - SW WRF
Biosolids Improvement Project (BIP)
Potential to Emit - Proposed Odor Control Systems
H2S Emissions
| H2S Concentration in Foul Air (Primary Clarifiers & Gravity Belt Thickener Building) |  | 10 | ppmvd[1]
| H2S Concentration in Foul Air (Dewatering Building) |  | 45 | ppmvd[3]
| AverageTemperature of Foul Air |  | 68 | °F[1]
| Molecular Weight of H2S |  | 34.0834 | lb/lb-mol
| Assumes Continuous Annual Operation |  | 8760 | hours
| Control Efficiency (per scrubber)[1,2] |  | 95 | %
Design Capacity[1]
| Scrubber 1 - Primary Clarifiers & Gravity Belt Thickener Building |  | 12000 | scfm
| Scrubber 2 - Primary Clarifiers & Gravity Belt Thickener Building |  | 12000 | scfm
| Scrubber 3 - Dewatering Building[5] |  | 24000 | scfm
H2S PTE (tons per year)[4]
| Scrubber 1 - Primary Clarifiers & Gravity Belt Thickener Building |  | 0.13948 | tpy
| Scrubber 2 - Primary Clarifiers & Gravity Belt Thickener Building |  | 0.13948 | tpy
| Scrubber 3 - Dewatering Building[5] |  | 1.2553 | tpy
|  | Total | 1.5343 | tpy
Notes: [ ]:
1. Information obtained from Brown & Caldwell 30% Preliminary Design Report (PDR) and Technical
Specifications - Volume No. 3, 60% Submittal. Value is downstream of Biotrickling Filters at inlet
of carbon scrubbers.
2. Specifications are for 99% control efficiency. 95% conservatively assumed.
3. Based on engineering estimates. Conservatively assumes maximum H2S concentration of 45 ppmvd.
4. 3 total scrubbers available to Primary Clarifiers & Gravity Belt Thickener Building, however, only 2 in use at any
one time, with one stand-by.
5. Foul air flow through scrubber 3 assumed to be equal to aggregate of scrubbers 1 & 2.

## Existing Scrubber Emissions
St. Petersburg - SW WRF
Biosolids Improvement Project (BIP)
Potential to Emit - Existing Headworks Odor Control Systems
H2S Emissions
| H2S Concentration in Foul Air (Headworks) | 275 | ppmvd[1]
| AverageTemperature of Foul Air | 68 | °F[3]
| Molecular Weight of H2S | 34.0834 | lb/lb-mol
| Assumes Continuous Annual Operation | 8760 | hours
| Control Efficiency (per scrubber)[2] | 95 | %
Design Capacity[1]
| Existing Scrubber - Headworks | 3700 | scfm
H2S PTE (tons per year)
| Existing Scrubber - Headworks | 1.1827 | tpy
Notes: [ ]:
1. Maximum measured influent H2S concentration as monitored by SWWRF odor loggers located in the wet-well and headworks.
Specifications - Volume No. 3, 60% Submittal. Value is downstream of Biotrickling Filters at inlet
of carbon scrubbers.
2. Specifications are for 99% control efficiency. 95% conservatively assumed.
3. Assumed value based on engineering data from proposed odor control systems.

## 1750 kW Diesel Generator
St. Petersburg - SW WRF
Biosolids Improvement Project (BIP)
Potential to Emit - Relocated 1750 kW Diesel Emergency Generator (New Source)
Basis:
Number of Units |  |  | 1
Fuel |  |  | Diesel Fuel Oil
Power Rating |  |  | 2347 | HP
Heat Input |  |  | 17.262 | mmBtu/hr
Heating Value of Fuel |  |  | 137000 | Btu/gal [2]
Fuel Burn Rate |  |  | 126 | gal/hr [1]
Hours of Operation |  |  | 100 | hours per year
Density of Fuel |  |  | 7.05 | lb/gal [2]
Sulfur Content of Fuel |  |  | 0.0015 | % [3]
Global Warming Potentials [4]
CO2 | 1
CH4 | 25
N2O | 298
Pollutant | Mass Emission Rate |  |  | PTE
| g/hp-hr | Notes | (lb/hr) | (tpy)
CO | 0.87356 | [1,10] | 4.52 | 0.226
NOX | 11.8355 | [1,10] | 61.24 | 3.062
PM | 0.201 | [1,10] | 1.04 | 0.052
PM10 | 0.201 | [5] | 1.04 | 0.052
PM2.5 | 0.201 | [5] | 1.04 | 0.052
SO2 | 0.0051503 | [6] | 0.026649 | 0.0013324
VOC | 0.24738 | [1,10] | 1.28 | 0.064
Lead | -- |  | -- | --
H2SO4 | 0.0078864 | [7] | 0.040806 | 0.0020403
Fluorides | -- |  | -- | --
TRS (including H2S) | -- |  | -- | --
GHG-Mass | 526.1959 | [9] | 2722.6689 | 136.1334
CO2 | 526.1671 | [8] | 2722.52 | 136.126
CH4 | 0.02878 | [8] | 0.14892 | 0.0074459
N2O | -- |  | -- | --
GHG-CO2e | 526.8867 | [9] | 2726.2429 | 136.3121
CO2 | 526.1671 | [4] | 2722.52 | 136.126
CH4 | 0.71951 | [4] | 3.7229 | 0.18615
N2O | -- |  | -- | --
Notes [ ]:
1. Caterpillar Model 3516 1750 kW generator installed at Albert Whitted facility in 2000, to be
relocated at SWWRF as part of BIP. Data from this specific engine is unavailable. Therefore, calculations
based on 1999 performance data from vendor for Model 3516B 1825 kW diesel generator.
2. Based on diesel fuel characteristics listed in Reference 2.
3. Based on the requirements of 40 CFR Part 63, Subpart ZZZZ and 40 CFR Part 80.510(b).
4. CO2 equivalents (CO2e) based on the global warming potential for applicable pollutant as listed in
Table A-1 to Subpart A of 40 CFR Part 98 - Global Warming Potentials.
5. Conservatively assumed all particulate matter emissions are less than 2.5 micrometers in diameter.
6. Assumed all sulfur in the fuel is converted to SO2.
7. Assumed 100% conversion of SO2 to H2SO4.
8. Greenhouse gases (CO2 and CH4) emission factors obtained from AP-42 (Reference 1a), for a large stationary
diesel engine (2-02-004-01).
9. The GHG emissions is the sum of all applicable GHG pollutants.
10. Emission factors enveloped across varying operational conditions to represent worst-case emissions.
References:
1. USEPA, AP-42, Fifth Edition, Vol. I. Chapter 3 "Stationary Internal Combustion Sources", Section 3.4 "Large
Stationary Diesel and All Stationary Duel-Fuel Engines". October 1996.
a. | Table 3.4-1 "Gaseous Emission Factors for Large Stationary Diesel and All Stationary
Duel-Fuel Engines".
2. USEPA, AP-42, Fifth Edition, Vol. I. Appendix A "Miscellaneous Data & Conversion Factors". September 1985.

## 1750 kW HAP Emissions
St. Petersburg - SW WRF
Biosolids Improvement Project (BIP)
HAP Emissions - Relocated 1750 kW Diesel Emergency Generator (New Source)
Basis:
Number of Units |  |  | 1
Fuel |  |  | Diesel Fuel Oil
Power Rating |  |  | 2347 | HP
Heat Input |  |  | 17.262 | mmBtu/hr
Heating Value of Fuel |  |  | 137000 | Btu/gal [2]
Fuel Burn Rate |  |  | 126 | gal/hr [1]
Hours of Operation |  |  | 100 | hours per year
Density of Fuel |  |  | 7.05 | lb/gal [2]
Pollutant | Composition [3]
(%wt)
Arsenic | 8.5e-06
Beryllium | 5e-06
Cadmium | 2.1e-05
Chromium | 9.5e-05
Manganese | 2.1e-05
Mercury | 4e-05
Nickel | 0.000338
Pollutant | Mass Emission Rate |  |  | PTE
| (lb/mmBtu) | Notes | (lb/hr) | (tpy)
Benzene | 0.000776 | [4] | 0.013395 | 0.00066977
Toluene | 0.000281 | [4] | 0.0048506 | 0.00024253
Xylenes | 0.000193 | [4] | 0.0033316 | 0.00016658
Formaldehyde | 7.89e-05 | [4] | 0.001362 | 6.8099e-05
Acetaldehyde | 2.52e-05 | [4] | 0.000435 | 2.175e-05
Acrolein | 7.88e-06 | [4] | 0.00013602 | 6.8012e-06
Naphthalene | 0.00013 | [5] | 0.0022441 | 0.0001122
PAH | 0.000212 | [5] | 0.0036595 | 0.00018298
Arsenic | 4.3741e-06 | [6, 7] | 7.5505e-05 | 3.7753e-06
Beryllium | 2.573e-06 | [6, 7] | 4.4415e-05 | 2.2207e-06
Cadmium | 1.0807e-05 | [6, 7] | 0.00018654 | 9.3272e-06
Chromium | 4.8887e-05 | [6, 7] | 0.00084389 | 4.2194e-05
Manganese | 1.0807e-05 | [6, 7] | 0.00018654 | 9.3272e-06
Mercury | 2.0584e-05 | [6, 7] | 0.00035532 | 1.7766e-05
Nickel | 0.00017393 | [6, 7] | 0.0030025 | 0.00015012
|  |  | Total HAPs | 0.0017054
Notes [ ]:
1. Caterpillar Model 3516 1750 kW generator installed at Albert Whitted facility in 2000, to be
relocated at SWWRF as part of BIP. Data from this specific engine is unavailable. Therefore, calculations
based on 1999 performance data from vendor for Model 3516B 1825 kW diesel generator.
2. Based on diesel fuel characteristics listed in Reference 2.
3. Based on data provided by USEPA (Reference 3a) for No. 2 fuel oil/diesel fuel.
4. Emission factor obtained from AP-42 (Reference 1a).
5. Emission factor obtained from AP-42 (Reference 1b).
6. Conservatively assumed all metal in the fuel oil is emitted into the atmosphere.
7. Emission factor based on the metal composition in the fuel. See Table C47 of this Appendix for details.
References:
1. USEPA, AP-42, Fifth Edition, Vol. I. Chapter 3 "Stationary Internal Combustion Sources", Section 3.4 "Large
Stationary Diesel and All Stationary Duel-Fuel Engines". October 1996.
a. | Table 3.4-3 "Speciated Organic Compound Emission Factors for Large Uncontrolled
Stationary Diesel Engines".
b. | Table 3.4-4 "PAH Emission Factors for Large Uncontrolled Stationary Diesel Engines".
2. USEPA, AP-42, Fifth Edition, Vol. I. Appendix A "Miscellaneous Data & Conversion Factors".
September 1985.
3. USEPA, EPCRA Section 313: Industry Guidance: Electricity Generating Facilities. EPA-745-B-00-004.
February 2000.
a. | Table 3-4 "Estimated Concentration Values of EPCRA Section 313 Constituents in Crude
Oil and Petroleum Products (Weight Percent)".

## 2000 kW Diesel Generator
St. Petersburg - SW WRF
Biosolids Improvement Project (BIP)
Potential to Emit - 2000 kW Diesel Emergency Generator
Basis:
Number of Units |  |  | 1
Fuel |  |  | Diesel Fuel Oil
Power Rating |  |  | 2682 | HP
Heat Input |  |  | 18.906 | mmBtu/hr
Heating Value of Fuel |  |  | 137000 | Btu/gal [2]
Fuel Burn Rate |  |  | 138 | gal/hr [1]
Hours of Operation |  |  | 100 | hours per year
Density of Fuel |  |  | 7.05 | lb/gal [2]
Sulfur Content of Fuel |  |  | 0.0015 | % [3]
Global Warming Potentials [4]
CO2 | 1
CH4 | 25
N2O | 298
Pollutant | Mass Emission Rate |  |  | PTE
| g/hp-hr | Notes | (lb/hr) | (tpy)
CO | 0.3 | [1,10] | 1.7738 | 0.088692
NOX | 5.45 | [1,10] | 32.2249 | 1.6112
PM | 0.025 | [1,10] | 0.14782 | 0.007391
PM10 | 0.025 | [5] | 0.14782 | 0.007391
PM2.5 | 0.025 | [5] | 0.14782 | 0.007391
SO2 | 0.0049362 | [6] | 0.029187 | 0.0014594
VOC | 0.11 | [1,10] | 0.65041 | 0.032521
Lead | -- |  | -- | --
H2SO4 | 0.0075586 | [7] | 0.044693 | 0.0022346
Fluorides | -- |  | -- | --
TRS (including H2S) | -- |  | -- | --
GHG-Mass | 526.1959 | [9] | 3111.2902 | 155.5645
CO2 | 526.1671 | [8] | 3111.12 | 155.556
CH4 | 0.02878 | [8] | 0.17017 | 0.0085086
N2O | -- |  | -- | --
GHG-CO2e | 526.8867 | [9] | 3115.3743 | 155.7687
CO2 | 526.1671 | [4] | 3111.12 | 155.556
CH4 | 0.71951 | [4] | 4.2543 | 0.21272
N2O | -- |  | -- | --
Notes [ ]:
1. Based on performance data for Caterpillar model 3516C 2000 eKW Diesel Generator Set.
2. Based on diesel fuel characteristics listed in Reference 2.
3. Based on the requirements of 40 CFR Part 63, Subpart ZZZZ and 40 CFR Part 80.510(b).
4. CO2 equivalents (CO2e) based on the global warming potential for applicable pollutant as listed in
Table A-1 to Subpart A of 40 CFR Part 98 - Global Warming Potentials.
5. Conservatively assumed all particulate matter emissions are less than 2.5 micrometers in diameter.
6. Assumed all sulfur in the fuel is converted to SO2.
7. Assumed 100% conversion of SO2 to H2SO4.
8. Greenhouse gases (CO2 and CH4) emission factors obtained from AP-42 (Reference 1a), for a large stationary
diesel engine (2-02-004-01).
9. The GHG emissions is the sum of all applicable GHG pollutants.
References:
1. USEPA, AP-42, Fifth Edition, Vol. I. Chapter 3 "Stationary Internal Combustion Sources", Section 3.4 "Large
Stationary Diesel and All Stationary Duel-Fuel Engines". October 1996.
a. | Table 3.4-1 "Gaseous Emission Factors for Large Stationary Diesel and All Stationary
Duel-Fuel Engines".
2. USEPA, AP-42, Fifth Edition, Vol. I. Appendix A "Miscellaneous Data & Conversion Factors". September 1985.

## 2000 kW HAP Emissions
St. Petersburg - SW WRF
Biosolids Improvement Project (BIP)
HAP Emissions - 2,000 kW Diesel Emergency Generator
Basis:
Number of Units |  |  | 1
Fuel |  |  | Diesel Fuel Oil
Power Rating |  |  | 2682 | HP
Heat Input |  |  | 18.906 | mmBtu/hr
Heating Value of Fuel |  |  | 137000 | Btu/gal [2]
Fuel Burn Rate |  |  | 138 | gal/hr [1]
Hours of Operation |  |  | 100 | hours per year
Density of Fuel |  |  | 7.05 | lb/gal [2]
Pollutant | Composition [3]
(%wt)
Arsenic | 8.5e-06
Beryllium | 5e-06
Cadmium | 2.1e-05
Chromium | 9.5e-05
Manganese | 2.1e-05
Mercury | 4e-05
Nickel | 0.000338
Pollutant | Mass Emission Rate |  |  | PTE
| (lb/mmBtu) | Notes | (lb/hr) | (tpy)
Benzene | 0.000776 | [4] | 0.014671 | 0.00073355
Toluene | 0.000281 | [4] | 0.0053126 | 0.00026563
Xylenes | 0.000193 | [4] | 0.0036489 | 0.00018244
Formaldehyde | 7.89e-05 | [4] | 0.0014917 | 7.4584e-05
Acetaldehyde | 2.52e-05 | [4] | 0.00047643 | 2.3822e-05
Acrolein | 7.88e-06 | [4] | 0.00014898 | 7.449e-06
Naphthalene | 0.00013 | [5] | 0.0024578 | 0.00012289
PAH | 0.000212 | [5] | 0.0040081 | 0.0002004
Arsenic | 4.3741e-06 | [6, 7] | 8.2696e-05 | 4.1348e-06
Beryllium | 2.573e-06 | [6, 7] | 4.8645e-05 | 2.4322e-06
Cadmium | 1.0807e-05 | [6, 7] | 0.00020431 | 1.0215e-05
Chromium | 4.8887e-05 | [6, 7] | 0.00092426 | 4.6213e-05
Manganese | 1.0807e-05 | [6, 7] | 0.00020431 | 1.0215e-05
Mercury | 2.0584e-05 | [6, 7] | 0.00038916 | 1.9458e-05
Nickel | 0.00017393 | [6, 7] | 0.0032884 | 0.00016442
|  |  | Total HAPs | 0.0018679
Notes [ ]:
1. Based on performance data for Caterpillar model 3516C 2000 eKW Diesel Generator Set.
2. Based on distillate oil characteristics listed in Reference 2.
3. Based on data provided by USEPA (Reference 3a) for No. 2 fuel oil/diesel fuel.
4. Emission factor obtained from AP-42 (Reference 1a).
5. Emission factor obtained from AP-42 (Reference 1b).
6. Conservatively assumed all metal in the fuel oil is emitted into the atmosphere.
7. Emission factor based on the metal composition in the fuel. See Table C47 of this Appendix for details.
References:
1. USEPA, AP-42, Fifth Edition, Vol. I. Chapter 3 "Stationary Internal Combustion Sources", Section 3.4 "Large
Stationary Diesel and All Stationary Duel-Fuel Engines". October 1996.
a. | Table 3.4-3 "Speciated Organic Compound Emission Factors for Large Uncontrolled
Stationary Diesel Engines".
b. | Table 3.4-4 "PAH Emission Factors for Large Uncontrolled Stationary Diesel Engines".
2. USEPA, AP-42, Fifth Edition, Vol. I. Appendix A "Miscellaneous Data & Conversion Factors".
September 1985.
3. USEPA, EPCRA Section 313: Industry Guidance: Electricity Generating Facilities. EPA-745-B-00-004.
February 2000.
a. | Table 3-4 "Estimated Concentration Values of EPCRA Section 313 Constituents in Crude
Oil and Petroleum Products (Weight Percent)".

## Cooling Tower
St. Petersburg SW WRF
Biosolids Improvement Project (BIP)
Potential to Emit - Proposed Cooling Tower
Emissions Equation
PM
where,
E = | emissions, tons |  | see Table below
CWF = | circulating water flow, gpm |  | 650 | gpm [1]
DR = | drift rate, % |  | 0.005 | % [1]
ρH2O = | density of water, lb/gal |  | 8.3454 | lb/gal
TDS = | cycled water TDS, ppmw |  | 1494 | ppmw [2]
Hours of Op. = | hours of operation, hrs/yr |  | 8760 | hrs/yr
PM10
where,
E = | emissions, tons
EPM = | PM emissions
FPM10/PM = | PM10 fraction, dimensionless |  | 1 | [3]
PM2.5
where,
E = | emissions, tons
EPM10 = | PM10 emissions
FPM10/PM = | PM2.5 fraction, dimensionless |  | 0.6 | [4]
Cooling Tower Emissions
Potential Emissions
Activity |  | (ton/yr)
|  | PM | PM10 | PM2.5
Mechanical Draft Cooling Tower |  | 0.10649 | 0.10649 | 0.063894
Notes [ ]:
1. Based on vendor data.
2. Site-specific water data was unavailable. Conservative preliminary engineering
estimate based on Florida experience and 3 cycles of concentration.
3. Conservatively assumed all particulate matter emissions are less than
10 micrometers in diameter.
4. Fraction of PM10 that is PM2.5 was obtained from SCAQMD (Reference 1a).
References:
1. South Coast AQMD, Air Guidance Book "Methodology to Calculate Particulate
Matter (PM) 2.5 and PM 2.5 Significance Thresholds". Final. October 2006.
a. | Appendix A - Table A "Updated CEIDARS Table with PM2.5 Fractions".
𝐸=𝐶𝑊𝐹×𝐷𝑅×𝜌_𝐻2𝑂×𝑇𝐷𝑆×𝐻𝑜𝑢𝑟𝑠 𝑜𝑓 𝑂𝑝. ×(60 𝑚𝑖𝑛)/(1 ℎ𝑟)×(1 𝑡𝑜𝑛)/(2,000 𝑙𝑏𝑠)
𝐸=𝐸_𝑃𝑀×𝐹_(𝑃𝑀10/𝑃𝑀)
𝐸=𝐸_𝑃𝑀10×𝐹_(𝑃𝑀2.5/𝑃𝑀10)