Title V Air Operation Permit Renewal/Revision

Permit No. 0090029-014-AV

Applicant

The applicant for this project is TransMontaigne Operating Company, L.P. The applicant’s responsible official and mailing address are: Dudley Tarlton, Vice President – Environmental, Safety, and Occupational Health, TransMontaigne, 1670 Broadway, Suite 3100, Denver, Colorado 80202.

Facility Description

The applicant operates the existing TransMontaigne – Cape Canaveral, which is located in Brevard County at 8952 N. Atlantic Ave, Cape Canavera1, Florida 32920.

This facility is a bulk gasoline terminal, which contains the following emission units:

- EU 028: Steam Boiler #3 – Sellers-Ygnis (4.2 MMBTU/hr)

- EU 024: Asphalt Heaters #5 & # 6 – First Thermal Systems (10.53 MMBTU/hr each)

- EU 025: Thirteen Petroleum Storage Tanks {subject to Rule 62-296.320(1), F.A.C.} as follows:

| Tank # | Worst-Case Product * | Shell Capacity (bbl) | Roof Type | NSPS | NESHAP |
| --- | --- | --- | --- | --- | --- |
| 1 | #6/Asphalt | 80,265 | FR | None | None |
| 2 | #2/Asphalt | 55,778 | FR | None | None |
| 3 | Asphalt | 33,607 | FR | None | None |
| 4 | Asphalt | 20,109 | FR | None | None |
| 6 | Asphalt | 20,097 | FR | None | None |
| 7 | #2 Fuel Oil | 65,270 | FR | None | None |
| 9 | Gasoline | 33,741 | IFR | None | BBBBBB |
| 10 | Asphalt | 3,010 | FR | None | None |
| 12 | Gasoline | 8,955 | IFR | None | BBBBBB |
| 13 | Gasoline | 8,048 | IFR | None | BBBBBB |
| 14 | Asphalt | 1,497 | FR | None | None |
| 15 | Gasoline | 54,919 | EFR w/dome | None | BBBBBB |
| 23 | Additive | 242 | FR | None | None |

*  Worst-case product is defined as the product that is expected to result in the highest emission of volatile organic compounds. It does not limit the storage of lower vapor products (e.g. storage tanks that identify gasoline as the worst-case product are also authorized to store ethanol).

- EU 026: Three Petroleum Storage Tanks {subject to 40 CFR 60, NSPS, Subpart Kb and K} as follows:

| Tank # | Primary Seal / Secondary Seal | Worst-Case Product | Shell Capacity (bbl) | Roof Type | NSPS | NESHAP |
| --- | --- | --- | --- | --- | --- | --- |
| 8 | Mechanical Shoe Rim-Mounted | Gasoline | 121,838 | IFR | Kb | BBBBBB |
| 17 | Vapor-Mounted Rim-Mounted | Gasoline | 99,388 | IFR | K | BBBBBB |
| 18 | Vapor-Mounted Rim-Mounted | Gasoline | 98,317 | IFR | K | BBBBBB |

*  Worst-case product is defined as the product that is expected to result in the highest emission of volatile organic compounds. It does not limit the storage of lower vapor products (e.g. storage tanks that identify gasoline as the worst-case product are also authorized to store ethanol).

40 CFR Part 60, Subpart K applies to storage vessels for petroleum liquids for which construction, reconstruction, or modification commenced after June 11, 1973, and prior to May 19, 1978. This regulation applies to Tanks 17 and 18, because both tanks were built in 1974.

40 CFR Part 60 Subpart Kb applies to volatile organic liquid storage vessels (including petroleum liquid storage vessels) for which construction, reconstruction, or modification commenced after July 23, 1984. This regulation applies to Tank 8, because it was built in 1992.

- EU 006: South Rack (for loading of gasoline, Ethanol, and other light fuels) with John Zink Vapor Control Unit; and Fugitive Emissions. The South Rack is subject to 40 CFR 60 Subpart XX because it is a loading rack at a bulk gasoline terminal which delivers liquid product into gasoline tank trucks; therefore, it meets the applicability requirements of 40 CFR 60.500. Compliance Assurance Monitoring (CAM) applies to this emission unit because this emission unit meets the applicability requirements of 40 CFR 64.2, which are stated below:

- The unit is subject to an emission limitation or standard for the applicable regulated air pollutant (or a surrogate thereof), other than an emission limitation or standard that is exempt under paragraph (b)(1) of this section;

- The unit uses a control device to achieve compliance with any such emission limitation or standard; and

- The unit has potential pre-control device emissions of the applicable regulated air pollutant that are equal to or greater than 100 percent of the amount, in tons per year, required for a source to be classified as a major source. For purposes of this paragraph, “potential pre-control device emissions” shall have the same meaning as “potential to emit,” as defined in §64.1, except that emission reductions achieved by the applicable control device shall not be taken into account.

The facility is not subject to 40 CFR 63, NESHAP, Subpart R based on the PTE (potential to emit) calculations provided in the most recent application (submitted on 7/6/2018). The potential to emit for total (combined) HAP emissions is 6.24 tons per year; the individual HAP emission with the highest PTE is toluene, which is 1.64 tons per year. By definition, the facility is not a major source of HAPS (major source thresholds for “hazardous air pollutants” (HAP) are 10 tons/year for a single HAP or 25 tons/year for any combination of HAP.) As such, per 40 CFR 63.420(a)(2), the terminal is not subject to requirements of NESHAP Subpart R.

40 CFR 63.420(a): The affected source to which the provisions of this subpart apply is each bulk gasoline terminal, except those bulk gasoline terminals:

40 CFR 63.420(a)(2): For which the owner or operator has documented and recorded to the Administrator's satisfaction that the facility is not a major source, or is not located within a contiguous area and under common control of a facility that is a major source, as defined in §63.2 of subpart A of this part (40 CFR 63, Subpart A).

40 CFR 63.2 Major source means any stationary source or group of stationary sources located within a contiguous area and under common control that emits or has the potential to emit considering controls, in the aggregate, 10 tons per year or more of any hazardous air pollutant or 25 tons per year or more of any combination of hazardous air pollutants, unless the Administrator establishes a lesser quantity, or in the case of radionuclides, different criteria from those specified in this sentence.

- EU 019 which consists of:

- North Rack (for Loading of Asphalt)

- Marine Dock (where Loading and Unloading of Marine Vessels occurs)

Asphalt loading at the North Rack limited to 100,800,000 gallons per consecutive twelve months of asphalt.  Marine Loading of Diesel or Lower Vapor Pressure Petroleum Product at the Marine Dock limited to 500,000,000 gallons per consecutive twelve months.

None of the Federal Regulations require the tracking of fugitive emissions for these operations.

- EU 029: A Back-Up Generator (RICE Engine – 157 HP)

The applicable emission limitations are as follows:

- EU 028 Steam Boiler #3- VE limit per Rule 62-296.406(1), F.A.C.; BACT per Rule 62-296.406(2) & (3), F.A.C.; excess emissions per Rule 62-210.700(1), (2), (3), & (4), F.A.C.; annual PM, NOX, & SO2 limits per construction permit

- EU 024 Asphalt Heaters #5 and #6 - VE limit per Rule 62-296.406(1), F.A.C.; BACT per Rule 62-296.406(2) & (3), F.A.C.; excess emissions per Rule 62-210.700(1), (2), (3), & (4), F.A.C.; annual PM, NOX, & SO2 limits per construction permit; (heaters only) 40 CFR Part 60, NSPS, Subparts A and Dc

- EU 025 Thirteen Petroleum Storage Tanks - General VOC standard per Rule 62-296.320(1)(a), F.A.C., and 40 CFR 63 Subparts A and BBBBBB.  40 CFR 60 Subparts K and Kb do not apply to any of the 13 Petroleum Tanks in EU 025.  40 CFR Part 60, Subpart K applies to storage vessels for petroleum liquids for which construction, reconstruction, or modification commenced after June 11, 1973, and prior to May 19, 1978.  40 CFR Part 60 Subpart Kb applies volatile organic liquid storage vessels (including petroleum liquid storage vessels) for which construction, reconstruction, or modification commenced after July 23, 1984.  Gasoline Tanks 9, 12, 13 and 15 were constructed in 1958 (Tanks 9), 1961 (Tanks 12 and 13), and 1969 (Tank 15), which predates the applicability construction dates for 40 CFR 60 Subparts K and Kb.

- EU 026 Three Petroleum Storage Tanks - 40 CFR Part 60, NSPS, Subparts A, Kb and K, and 40 CFR 63 Subparts A and BBBBBB. 40 CFR Part 60, Subpart K applies to storage vessels for petroleum liquids for which construction, reconstruction, or modification commenced after June 11, 1973, and prior to May 19, 1978. This regulation applies to Tanks 17 and 18, because both tanks were built in 1974.  40 CFR Part 60 Subpart Kb applies to volatile organic liquid storage vessels (including petroleum liquid storage vessels) for which construction, reconstruction, or modification commenced after July 23, 1984. This regulation applies to Tank 8, because it was built in 1992.

- EU 006 South Rack (for Loading of Gasoline, Ethanol, and other light fuels) with John Zink Vapor Control Unit; and Fugitive Emissions - Rule 62-297.401, F.A.C., and 40 CFR Part 60, NSPS, Subparts A and XX and 40 CFR 63 Subparts A and BBBBBB. CAM (Compliance Assurance Monitoring) does apply to EU 006, which is a Petroleum Liquid Loading Rack where the VOC Emissions are controlled by a vapor combustion unit. CAM applies to this emission unit because this emission unit meets the applicability requirements of 40 CFR 64.2.  See Appendix 40 CFR 64 – Compliance Assurance Monitoring.

[40 CFR 64.1; 40 CFR 64.2; 40 CFR 64.7; 40 CFR 64.9; Rules 62-204.800(12) and 62-213.440(1)(b)1.a., F.A.C.]

- EU 019 North Rack (for Loading of Asphalt); and Marine Dock (where Loading and Unloading of Marine Vessels occurs) - General VOC standard per Rule 62-296.320(1)(a), F.A.C.

- The facility (EU 006, EU 025, and EU 026) is subject to NESHAP, 40 CFR 63, Subpart BBBBBB with a compliance date of January 10, 2011. Therefore, Subpart BBBBBB is included in the permit. The permittee must comply with the requirements of 40 CFR 63 Subpart BBBBBB by the applicable dates specified in 40 CFR 63.11083, except that storage vessels equipped with floating roofs and not meeting the requirements of paragraph (a) of 40 CFR 63.11087 must be in compliance at the first degassing and cleaning activity after January 10, 2011 or by January 10, 2018, whichever is first. [40 CFR 63.11087(b)]

This facility also includes miscellaneous unregulated/insignificant emissions units and/or activities.

Project DESCRIPTION

The purpose of this permitting project is to renew and revise the existing Title V permit for the above referenced facility. The Title V revision involves an increase in the Volatile Organic Compound (VOC) emissions limit for the facility from 146.3 tons per consecutive 12 months to 149.6 tons per consecutive 12 months; authorizes a decrease in the total HAPs emission limit from 25 tons per consecutive 12 months to 10 tons per consecutive 12 months; authorizes a decrease in the individual HAP emissions limit from 10 tons per consecutive 12 months to 4 tons per consecutive 12 months; and removes Tank No. 11 from the Title V air operation permit, because this tank has been removed from the facility. TransMontaigne has switched from using the EPA TANKS 4.0.9d software to the Trinity Consultants Tank ESP software to compute Volatile Organic Compound (VOC) emissions from the tanks. As a result, calculated potential VOC emissions from the facility increased by 3.3 tons per consecutive 12 months. Both HAP emission limits were decreased to provide more reasonable assurance that the facility will not become a major source of HAPs (major HAP threshold is 25 tons total HAPs; 10 tons individual HAP). This Title V Air Operation Permit is a renewal and revision of Permit 0090029-013-AV, which was issued March 6, 2014.  The revision incorporates the changes authorized by Permit No. 0090029-015-AC.  Permit No. 0090029-015-AC, which authorizes the increase in the VOC emissions limit and decreases in the HAP emissions limits (total HAPs and individual HAP), is being processed concurrently with the Title V Permit renewal and revision.

Processing Schedule and Related Documents

Title V Air Operation Permit Renewal issued March 6, 2014

Application for a Title V Air Operation Permit Renewal/Revision received July 6, 2018

Additional Information Request dated July 18, 2018

Additional Information Response received July 20, 2018 (revised application) and July 30, 2018 (PE Certification). Application complete.

Primary Regulatory requirements

Standard Industrial Classification (SIC) Code:  5171 – Petroleum Bulk Stations & Terminals.

North American Industry Classification System (NAICS):  Petroleum Bulk Stations and Terminals.

HAP:  The facility is not identified as a major source of hazardous air pollutants (HAP).

Title V:  The facility is a Title V major source of air pollution in accordance with Chapter 62-213, Florida Administrative Code (F.A.C.).

NSPS:  The facility operates units subject to the New Source Performance Standards (NSPS) of 40 Code of Federal Regulations (CFR) 60.

NESHAP:  The facility operates units subject to the National Emissions Standards for Hazardous Air Pollutants (NESHAP) of 40 CFR 63.

CAM:  Compliance Assurance Monitoring (CAM) does apply to EU 006 South Rack (for Loading of Gasoline, Ethanol, and other light fuels) with John Zink Vapor Control Unit

GHG:  The facility is not identified as a major source of greenhouse gas (GHG) pollutants.

PROJECT REVIEW

Changes to the permit made as part of this revision are shown in strike through format for deletions and in double underline format for additions. For ease of identification, all changes have also been highlighted in yellow within the permit document.

  - Deleted language in Condition FW.8. that pertains to a facility that is currently subject to Section 112(r).  TransMontaigne – Cape Canaveral is not currently subject to Section 112(r).

  - FW8.  Prevention of Accidental Releases (Section 112(r) of CAA).  If, and when, the facility becomes subject to 112(r), the permittee shall:

- Submit its Risk Management Plan (RMP) to the Chemical Emergency Preparedness and Prevention Office (CEPPO) RMP Reporting Center. Any Risk Management Plans, original submittals, revisions or updates to submittals, should be sent electronically through EPA’s Central Data Exchange system at the following address:  https://cdx.epa.gov. Information on electronically submitting risk management plans using the Central Data Exchange system is available at:  http://www2.epa.gov/rmp. The RMP Reporting Center can be contacted at:  RMP Reporting Center, Post Office Box 10162, Fairfax, VA  22038, Telephone: (703) 227-7650.

- Submit to the permitting authority Title V certification forms or a compliance schedule in accordance with Rule 62-213.440(2), F.A.C.

- Any required written reports, notifications, certifications, and data required to be sent to the Division of Emergency Management, should be sent to:  Division of Emergency Management, 2555 Shumard Oak Boulevard, Tallahassee, FL  32399-2100, Telephone: (850) 413-9900.

- Any required reports (incidents involving oil and chemical spills - the criteria for reporting such incidents is found in 40 CFR 110 for oil discharges, as well as, 40 CFR 117 and 40 CFR 302 for hazardous substances discharges) to be sent to the National Response Center, should be sent to:

NATIONAL RESPONSE CENTER

c/o United States Coast Guard (CG-5335) - Stop 7581

2100 2nd Street, SW

Washington, DC  20593-0001

Telephone: (800) 424-8802.

An NRC on-line reporting tool is available at http://www.nrc.uscg.mil/

[40 CFR 68; Part IV, Chapter 252, F.S.; and, Rule 27P-21, F.A.C.]

  - Added FW.9. Condition relating to Semi-Annual Monitoring Reports. This condition is part of the current template for Title V permits. The language is located in the Appendix RR.

  - FW9.  Semi-Annual Monitoring Reports. The permittee shall monitor compliance with the terms and conditions of this permit and shall submit reports of any deviations from the requirements of these conditions at least every six (6) months. All instances of deviations from permit requirements must be clearly identified in such reports, including reference to the specific requirement and the duration of such deviation. All reports shall be accompanied by a certification by a responsible official, pursuant to subsection 62-213.420(4), F.A.C.  (See also Conditions RR2. – RR4. of Appendix RR, Facility-wide Reporting Requirements, for additional reporting requirements related to deviations.)  [Rule 62-213.440(1)(b)3.a., F.A.C.]

{Permitting Note:  EPA has clarified that, pursuant to 40 CFR 70.6(a)(3), the word “monitoring” is used in a broad sense and means monitoring (i.e., paying attention to) the compliance of the source with all emissions limitations, standards, and work practices specified in the permit.}

  - Changed the Facility-Wide VOC emission limit from 146.3 tons per consecutive 12 months to 149.6 tons per consecutive 12 months, changed total HAP emissions limit from 25 tons per consecutive month to 10 tons per consecutive 12 months, and changed individual HAP emissions limit from 10 tons perc consecutive 12 months to 4 tons per consecutive 12 months pursuant to Permit 0090029-015-AC.

  - FW9. FW10. Facility-Wide Emissions Limits. The maximum facility-wide total HAP emissions are limited to less than 25.0 tons per consecutive twelve months and each HAP emission is limited to less than 10.0 tons per consecutive twelve months.  The maximum facility-wide total VOC emissions are limited to less than 146.3 tons per consecutive twelve months. The maximum total Volatile Organic Compound (VOC) emissions, maximum total Hazardous Air Pollutant (HAP) emissions, and maximum individual HAP emissions from the facility shall not exceed the following limits:

| Pollutant | Maximum Emissions Rate (Tons Per Any Consecutive 12-month period) |
| --- | --- |
| VOC Emissions | 146.3 149.6 |
| HAP Emissions (total) | 25 10 |
| Individual HAP | 10 4 |

[Application No. 0090029-015-AC and Rule 62 210.200, (Potential to Emit), F.A.C.] Facility-Wide

  - Renumbered condition and removed reference to emergency generator from the condition.

  - FW10. FW11.  Hours of Operation: Each unit, except for the emergency generator, is allowed to operate a maximum of 8,760 hours per consecutive twelve months.  [Rule 62-210.200, (PTE), F.A.C. and Permits No. 0090029-001-AC and 0090029-011-AC]

  - Updated Condition FW12. to match the updated rule.

  - FW12. Test Notification: At least 15 days prior to the date on which each formal compliance test is due to begin, the permittee shall provide written notification of the test to the air compliance section of this office.  The notification must include the following information:  the date, time and location of each test; the name and telephone number of the facility’s contact person who will be responsible for coordinating the test; and the name, company and telephone number of the person conducting the test on which each required emissions test is to begin, the owner or operator shall notify the Compliance Authority, unless shorter notice is agreed to by the appropriate Compliance Authority. The notification shall include the date, time, place of each such test, Facility ID Number, Emission Unit ID Number, and description, test methods, pollutants to be tested along with the name and telephone number of the person who will be responsible for conducting such test for the permittee. If a scheduled emissions test needs to be re-scheduled, the owner or operator shall submit to the appropriate air compliance program a revised notification at least seven days prior to the re-scheduled emissions test date or arrange a re-scheduled test date with the appropriate air compliance program by mutual agreement. [Rules 62-297.310(7)(a)9 62-4.070(3) and 62-297.310(9)., F.A.C.]

  - Combined Conditions FW13., FW14., FW15., and FW16.

  - FW13.	Excess Emissions. Excess emissions resulting from startup, shutdown or malfunction shall be permitted providing (1) best operational practices to minimize emissions are adhered to and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration. Excess emissions which are caused entirely or in part by poor maintenance, poor operation or any other equipment or process failure which may be reasonably be prevented during startup, shutdown or malfunction shall be prohibited. Excess emissions from fossil fuel steam generators resulting from startup or shutdown shall be permitted provided that best operational practices to minimize emissions are adhered to and the duration of excess emissions shall be minimized. In case of excess emissions resulting from malfunctions, each owner or operator shall notify the Department in accordance with Rule 62-4.130, F.A.C. A full written report on the malfunctions shall be submitted if requested by the Department.  [Rules 62-210.700(1), (2), and (5), F.A.C.]

  - Reformatted Condition A.1.

  - A.1. Capacity.  The permitted operating capacity (average annual heat input based on calendar year) is the following:

a. steam boiler no. 3 - 4.2 MMBTU/hr.

b. asphalt heater no. 5 - 10.53 MMBTU/hr.

c. asphalt heater no. 6 - 10.53 MMBTU/hr.

A.1. Capacity. The permitted operating capacity (average annual heat input based on calendar year) is the following for Steam Boiler #3, Asphalt Heaters #5 and #6:

| Unit No. | MMBtu/hr Heat Input | Fuel Type and Sulfur Content allowed |
| --- | --- | --- |
| Steam Boiler #3 | 4.2 MMBtu/hr. | Natural Gas and New No. 2 fuel oil (Use New No. 2 fuel oil as a back-up fuel only. New No. 2 fuel shall not exceed 0.05 percent sulfur content, by weight.) |
| Asphalt Heater #5 | 10.53 MMBtu/hr. | Natural Gas and New No. 2 fuel oil (New No. 2 fuel shall not exceed 0.5 percent sulfur content, by weight) |
| Asphalt Heater #6 | 10.53 MMBtu/hr. | Natural Gas and New No. 2 fuel oil (New No. 2 fuel shall not exceed 0.5 percent sulfur content, by weight.) |

  - Combined A.4., A.5., and A.6. and reformatted the condition.

16.	A.4.	 BACT for each Asphalt Heater Determined by DEP:  The BACT is using either natural gas or new No. 2 fuel oil if there is a curtailment of natural gas.  The amount of particulate and sulfur dioxide emissions from each asphalt heater while firing no. 2 oil will be limited by the firing of new no. 2 fuel oil having a sulfur content not to exceed 0.5 percent, by weight. The term “new” means oil which has been refined from crude oil and has not been used.

[Rule 62-296.406(2) and (3), F.A.C.; construction permit 0090029-001-AC; and 40 CFR 60.42c(d)]

{Permitting Note: The following is 40 CFR 60.42c(d), Standard for sulfur dioxide (SO2), which is part of 40 CFR 60 Subpart Dc – Standards of Performance for Small Industrial-Commercial-Institutional Steam Generating Units: On and after the date on which the initial performance test is completed or required to be completed under §60.8, whichever date comes first, no owner or operator of an affected facility that combusts oil shall cause to be discharged into the atmosphere from that affected facility any gases that contain SO2in excess of 215 ng/J (0.50 lb/MMBtu) heat input; or, as an alternative, no owner or operator of an affected facility that combusts oil shall combust oil in the affected facility that contains greater than 0.5 weight percent sulfur. The percent reduction requirements are not applicable to affected facilities under this paragraph.}

A.5.	BACT for Boiler No. 3 Determined by DEP:  The BACT is using either natural gas or new No. 2 fuel oil.  The amount of particulate and sulfur dioxide emissions from the boiler while firing No. 2 oil will be limited by the firing of new No. 2 fuel oil having a sulfur content not to exceed 0.05 percent, by weight. The term “new” means oil which has been refined from crude oil and has not been used. [Rules 62-296.406(2) and (3), F.A.C.; construction permit 0090029-011-AC; and Applicant Request]

{Permitting Note:  Steam Boiler No. 3 is not subject to NSPS Subparts A and Dc because the maximum design heat input capacity is less than 10 MMBtu per hour.}

A.6.	Visible Emissions. Visible emissions shall not exceed 20% opacity except for one two-minute period per hour during which opacity shall not exceed 40%.

[Rule 62-296.406(1), F.A.C.]

- Emissions Standards:

- BACT for each Asphalt Heater Determined by DEP. The BACT is using either natural gas or new No. 2 fuel oil if there is a curtailment of natural gas. The amount of particulate and sulfur dioxide emissions from each asphalt heater while firing No. 2 oil will be limited by the firing of new no. 2 fuel oil having a sulfur content not to exceed 0.5 percent, by weight. The term “new” means oil which has been refined from crude oil and has not been used. [40 CFR 60.42c(d), and Rules 62-296.406(2) and (3), F.A.C., and, Permit No. 0090029-001-AC]

{Permitting Note: The following is 40 CFR 60.42c(d), Standard for sulfur dioxide (SO2), which is part of 40 CFR 60 Subpart Dc – Standards of Performance for Small Industrial-Commercial-Institutional Steam Generating Units: On and after the date on which the initial performance test is completed or required to be completed under §60.8, whichever date comes first, no owner or operator of an affected facility that combusts oil shall cause to be discharged into the atmosphere from that affected facility any gases that contain SO2in excess of 215 ng/J (0.50 lb/MMBtu) heat input; or, as an alternative, no owner or operator of an affected facility that combusts oil shall combust oil in the affected facility that contains greater than 0.5 weight percent sulfur. The percent reduction requirements are not applicable to affected facilities under this paragraph.}

- BACT for Boiler No. 3 Determined by DEP:  The BACT is using either natural gas or new No. 2 fuel oil.  The amount of particulate and sulfur dioxide emissions from the boiler while firing No. 2 oil will be limited by the firing of new No. 2 fuel oil having a sulfur content not to exceed 0.05 percent, by weight. The term “new” means oil which has been refined from crude oil and has not been used. [Rules 62-296.406(2) and (3), F.A.C., and Permit No. 0090029-011-AC]

{Permitting Note:  Steam Boiler No. 3 is not subject to NSPS Subparts A and Dc because the maximum design heat input capacity is less than 10 MMBtu per hour.}

- Visible Emissions:  Visible emissions shall not exceed 20% opacity except for one two-minute period per hour during which opacity shall not exceed 40%.  [Rule 62-296.406(1), F.A.C.]

Test Methods and Procedures

- Renumbered condition and minor template format update.

- A.9. A.5.  Test Method. When required, tests shall be performed in accordance with the following reference method:

| Method | Description of Method and Comments |
| --- | --- |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources. The tests shall last 30 minutes each for Steam Boiler No. 3 and the asphalt heaters. |

The above method is described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Rule 62-204.800, F.A.C]

- Rewrote condition to match permitting template.

- A.6. Common Test Requirements: The permittee shall notify the Compliance Authority in writing at least 15 days prior to any required tests. Tests shall be conducted in accordance with the applicable requirements specified in Appendix D (Common Testing Requirements) of this permit.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310(7)(a)9., F.A.C.]

- Rewrote condition to match the revised rule (Rule 62-297.310(8)(a)5., F.A.C.)

- A.7. Annual Compliance Tests. If Steam Boiler No. 3 or Asphalt Heater No. 5 or Asphalt Heater No. 6 burns No. 2 fuel oil for less than 400 hours during a federal fiscal year (October 1st to September 30th), that emissions unit is not required to be tested to demonstrate compliance with the emissions standards for visible emissions prior to September 30 of that federal fiscal year.

- If Steam Boiler No. 3 or Asphalt Heater No. 5 or Asphalt Heater No. 6 burns No. 2 fuel oil for a total of more than 400 hours during a federal fiscal year (October 1st to September 30th), that emissions unit is required to be tested to demonstrate compliance with the emissions standards for visible emissions prior to September 30 of the federal fiscal year when that emission unit burned fuel for more than 400 hours.

- If Steam Boiler No. 3 or Asphalt Heater No. 5 or Asphalt Heater No. 6 burns No. 2 fuel oil for a total of more than 400 hours during a federal fiscal year (October 1st to September 30th), that emissions unit is required to be tested to demonstrate compliance with the emissions standards for visible emissions prior to September 30 of the federal fiscal year when that emission unit burned fuel for more than 400 hours.

[Rule 62-297.310(7)(a)4 and 5, F.A.C.]

An annual visible emissions test shall not be required for Steam Boiler No. 3, Asphalt Heater No. 5, or Asphalt Heater No. 6, provided New No. 2 fuel oil was not burned for more than 400 hours in the boiler or heater, other than during startup, during the calendar year (January 1st to December 31st).  If Steam Boiler No. 3, Asphalt Heater No. 5, or Asphalt Heater No. 6 burns New No. 2 fuel oil for more than 400 hours, other than during startup, during the calendar year, a visible emissions test for New No. 2 fuel oil shall be completed no later than 60 days after the boiler’s or heater’s burning of New No. 2 fuel oil exceeds 400 hours, or by the end of the calendar year, whichever is later.  [Rule 62-297.310(8)(a)5., F.A.C.]

- Combined Conditions A.10. and A.11. into Condition A.8.

- A.8. Sulfur Dioxide - Sulfur Content.  A.10. The permittee shall demonstrate compliance with the liquid fuel sulfur limit by providing a fuel analysis upon each fuel delivery to the boiler or asphalt heater fuel supply tank.  [Rules 62-213.440 and 62-296.406(3), F.A.C.]  A.11.  Sulfur Dioxide - Sulfur Content.  The fuel sulfur content, percent by weight, for liquid fuels shall be evaluated using one of ASTM D2622-94, ASTM D4294-90(95), ASTM 1552-95, ASTM D1266-91, or both ASTM D4057-88 and ASTM D129-91 or latest editions.  [Rules 62-213.440, 62-296.406(3), and 62-297.440(1), F.A.C.]   The permittee shall demonstrate compliance with the liquid fuel sulfur limit by providing a fuel analysis upon each fuel delivery to the boiler or asphalt heater fuel supply tank.  The fuel sulfur content, percent by weight, for liquid fuels shall be evaluated using one of ASTM D2622-94, ASTM D4294-90(95), ASTM 1552-95, ASTM D1266-91, or both ASTM D4057-88 and ASTM D129-91 or latest editions.  [Rules 62-213.440, 62-296.406(3), and 62-297.440(1), F.A.C.]

- Renumbered condition (A.12. to A.9.) and reworded condition A.9.f. for greater clarity.  Added condition A.9.g. for reasonable assurance.

- A.12. A.9. Operational Data. In order to demonstrate compliance with Condition No. A.1., A.2., and A.4., the permittee shall maintain records at the facility for a period of at least 5 years from the date the data is recorded. The records shall contain the following:

Monthly (The monthly logs shall be completed by the end of the following month.)

- Facility Name, Facility ID No. (i.e., 0090029);

- Month and year of record;

- Most recent monthly totals of operational hours for the steam boiler and each asphalt heater;

- Most recent monthly totals of natural gas (MMSCF) and/or no. 2 fuel oil (gallons) burned by the steam boiler and each asphalt heater;

- Calculated most recent monthly total of heat input in MMBtu based on a lower heating value (LHV) of 905 Btu per SCF for natural gas and 0.132 MMBtu per gallon for no. 2 fuel oil. (This is calculated by multiplying A.9.d. by 905 Btu per SCF for natural gas and 0.132 MMBtu per gallon for no. 2 fuel oil.); and

- Calculate the annual (calendar year) heat input based on the total number of operating hours and fuel usage to verify compliance with Condition A.1.  Monthly average heat input rate per each hour of operation. (This is calculated by dividing A.9.e. by A.9.c.).  This value should not exceed 4.2 MMBtu per hour for the steam boiler and 10.5 MMBtu per hour for each asphalt heater (Specific Condition No. A.1.)

- Certification from the fuel oil supplier of the No. 2 fuel oil sulfur content

[Rules 62-4.070(3) and 62-213.440(1)(b)2, F.A.C.]

- Added condition (Other Reporting Requirements) that is part of the current Title V permit template.

- A.10. Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440(1)(b), F.A.C.]

- Renumbered existing condition.

- A.13. A.11. NSPS Condition – Asphalt Heaters only: The asphalt heaters are subject to 40 CFR Part 60, Subpart A, General Provisions, and 40 CFR Part 60, Subpart Dc, Standards of Performance for Small Industrial-Commercial-Institutional Steam Generating Units. The conditions are incorporated into this permit (see Appendix NSPS, Subpart Dc).  [Rule 62-204.800(8), F.A.C., and 40 CFR Part 60, Subparts A and Subpart Dc.]

{Permitting Note:  EU 028, Steam Boiler No. 3, is not subject to NSPS Subparts A and Dc because the maximum design heat input capacity is less than 10 MMBtu per hour.}

- Removed Tank No. 11 pursuant to Permit 0090029-015-AC and applicant request. Tank No. 11 has been removed from the facility.

- B.1. Permitted Capacity. Individual tanks are permitted as follows:

| Tank # | Worst-Case Product | Shell Capacity (bbl) | Roof Type | NSPS | NESHAP |
| --- | --- | --- | --- | --- | --- |
| 1 | #6/Asphalt | 80,265 | FR | None | None |
| 2 | #2/Asphalt | 55,778 | FR | None | None |
| 3 | Asphalt | 33,607 | FR | None | None |
| 4 | Asphalt | 20,109 | FR | None | None |
| 6 | Asphalt | 20,097 | FR | None | None |
| 7 | #2 Fuel Oil | 65,270 | FR | None | None |
| 9 | Gasoline | 33,741 | IFR | None | BBBBBB |
| 10 | Asphalt | 3,010 | FR | None | None |
| 11 | Asphalt | 3,009 | FR | None | None |
| 12 | Gasoline | 8,955 | IFR | None | BBBBBB |
| 13 | Gasoline | 8,048 | IFR | None | BBBBBB |
| 14 | Asphalt | 1,497 | FR | None | None |
| 15 | Gasoline | 54,919 | EFR w/dome | None | BBBBBB |
| 23 | Additive | 242 | FR | None | None |

[Rule 62-210.200, (PTE), F.A.C. and construction permit 0090029-001-AC]

{Permit Note: Worst-case product is defined as the product that is expected to result in the highest emission of volatile organic compounds. It does not limit the storage of lower vapor products (e.g. storage tanks that identify gasoline as the worst-case product are also authorized to store ethanol).}

- Added “Test Method” Condition.

- B.2. Test Method: When required, tests shall be performed in accordance with the following reference method:

| Method | Description of Method and Comments |
| --- | --- |
| 27 | Vapor Tightness of Gasoline Tank – Pressure Vacuum |

The above method is described in Appendix A of 40 CFR 60 and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Rule 62-204.800, F.A.C.; and Appendix A of 40 CFR 60]

- Deleted “Circumvent any pollution control device” condition. Duplicate condition TV7 found in Appendix TV (Title V General Conditions).

- B.2. No person shall circumvent any pollution control device or allow the emissions of air pollutants without the applicable air pollution control device operating properly.

[Rule 62-210.200, (PTE), F.A.C., and Rule 62-210.650, F.A.C.]

- Expanded Condition B.3. (added the testing and monitoring requirements specified in 40 CFR 63.11092(e)).

- B.3.	Monitoring and Testing: The permittee must comply with the testing and monitoring requirements of 40 CFR 63.11092(e).

- Tanks 9, 12, and 13 (Gasoline Tanks with internal floating roofs): The permittee shall perform inspections of the floating roof system according to the requirements of §60.113b(a) (listed below) if the permittee is complying with option 2(b) in Table 1 to this subpart, or according to the requirements of §63.1063(c)(1) (listed below) if you are complying with option 2(d) in Table 1 to 40 CFR 63 Subpart BBBBBB.

40 CFR 60.113(b)(a) requirements: After installing the control equipment required to meet § 60.112b(a)(1) (permanently affixed roof and internal floating roof), each permittee shall:

- Visually inspect the internal floating roof, the primary seal, and the secondary seal (if one is in service), prior to filling the storage vessel with VOL. If there are holes, tears, or other openings in the primary seal, the secondary seal, or the seal fabric or defects in the internal floating roof, or both, the owner or operator shall repair the items before filling the storage vessel.

- For Vessels equipped with a liquid-mounted or mechanical shoe primary seal, visually inspect the internal floating roof and the primary seal or the secondary seal (if one is in service) through manholes and roof hatches on the fixed roof at least once every 12 months after initial fill. If the internal floating roof is not resting on the surface of the VOL inside the storage vessel, or there is liquid accumulated on the roof, or the seal is detached, or there are holes or tears in the seal fabric, the owner or operator shall repair the items or empty and remove the storage vessel from service within 45 days. If a failure that is detected during inspections required in this paragraph cannot be repaired within 45 days and if the vessel cannot be emptied within 45 days, a 30-day extension may be requested from the Administrator in the inspection report required in § 60.115b(a)(3). Such a request for an extension must document that alternate storage capacity is unavailable and specify a schedule of actions the company will take that will assure that the control equipment will be repaired or the vessel will be emptied as soon as possible.

- For vessels equipped with a double-seal system as specified in § 60.112b(a)(1)(ii)(B):

(i)   Visually inspect the vessel as specified in paragraph (a)(4) of this section at least every 5 years; or

(ii)  Visually inspect the vessel as specified in paragraph (a)(2) of this section.

- Visually inspect the internal floating roof, the primary seal, the secondary seal (if one is in service), gaskets, slotted membranes and sleeve seals (if any) each time the storage vessel is emptied and degassed. If the internal floating roof has defects, the primary seal has holes, tears, or other openings in the seal or the seal fabric, or the secondary seal has holes, tears, or other openings in the seal or the seal fabric, or the gaskets no longer close off the liquid surfaces from the atmosphere, or the slotted membrane has more than 10 percent open area, the owner or operator shall repair the items as necessary so that none of the conditions specified in this paragraph exist before refilling the storage vessel with VOL. In no event shall inspections conducted in accordance with this provision occur at intervals greater than 10 years in the case of vessels conducting the annual visual inspection as specified in paragraphs (a)(2) and (a)(3)(ii) of this section and at intervals no greater than 5 years in the case of vessels specified in paragraph (a)(3)(i) of this section.

40 CFR 63.1063(c)(1) requirements: Internal floating roofing (IFR) inspections and repairs shall be performed as specified in (c), (d), and (e) below.

(c) Inspection frequency requirements for internal floating roofs. Internal floating roofs shall be inspected as specified in paragraph (d)(1) of this section before the initial filling of the storage vessel. Subsequent inspections shall be performed as specified in paragraph (c)(1)(i) or (c)(1)(ii) below.

(i) Internal floating roofs shall be inspected as specified in paragraphs (c)(1)(i)(A) and (c)(1)(i)(B) of this section.

(A) At least once per year the IFR shall be inspected as specified in paragraph (d)(2) of this section.

(B) Each time the storage vessel is completely emptied and degassed, or every 10 years, whichever occurs first, the IFR shall be inspected as specified in paragraph (d)(1) below.

(ii) Instead of the inspection frequency specified in paragraph (c)(1)(i) of this section, internal floating roofs with two rim seals may be inspected as specified in paragraph (d)(1) of this section each time the storage vessel is completely emptied and degassed, or every 5 years, whichever occurs first.

(d) Inspection procedure requirements. Floating roof inspections shall be conducted as specified in paragraphs (d)(1), as applicable. If a floating roof fails an inspection, the owner or operator shall comply with the repair requirements of paragraph (e) of this section.

(1) Floating roof (IFR and EFR) inspections shall be conducted by visually inspecting the floating roof deck, deck fittings, and rim seals from within the storage vessel. The inspection may be performed entirely from the top side of the floating roof, as long as there is visual access to all deck components specified in paragraph (a) of this section. Any of the conditions described in paragraphs (d)(1)(i) through (d)(1)(v) of this section constitutes inspection failure.

(i) Stored liquid on the floating roof.

(ii) Holes or tears in the primary or secondary seal (if one is present).

(iii) Floating roof deck, deck fittings, or rim seals that are not functioning as designed (as specified in paragraph (a) of this section).

(iv) Failure to comply with the operational requirements of paragraph (b) of this section.

(v) Gaps of more than 0.32 centimeters (1⁄8 inch) between any deck fitting gasket, seal, or wiper (required by paragraph (a) of this section) and any surface that it is intended to seal.

(e) Repair requirements. Conditions causing inspection failures under paragraph (d) of this section shall be repaired as specified in paragraph (e)(1) or (e)(2) of this section.

(1) If the inspection is performed while the storage vessel is not storing liquid, repairs shall be completed before the refilling of the storage vessel with liquid.

(2) If the inspection is performed while the storage vessel is storing liquid, repairs shall be completed or the vessel removed from service within 45 days. If a repair cannot be completed and the vessel cannot be emptied within 45 days, the owner or operator may use up to 2 extensions of up to 30 additional days each. Documentation of a decision to use an extension shall include a description of the failure, shall document that alternate storage capacity is unavailable, and shall specify a schedule of actions that will ensure that the control equipment will be repaired or the vessel will be completely emptied as soon as practical.

- Tank 15 (Gasoline Tank with external floating roof): If your gasoline storage tank is equipped with an external floating roof, the permittee must perform inspections of the floating roof system according to the requirements of §60.113b(b) (listed below) if you are complying with option 2(c) in Table 1 to 40 CFR 63 Subpart BBBBBB, or according to the requirements of §63.1063(c)(2) (listed below) if the permittee is complying with option 2(d) in Table 1 to 40 CFR 63 Subpart BBBBBB.

40 CFR 60.113b(b) requirements: After installing the control equipment required to meet §60.112b(a)(2) (external floating roof), the owner or operator shall:

(1) Determine the gap areas and maximum gap widths, between the primary seal and the wall of the storage vessel and between the secondary seal and the wall of the storage vessel according to the following frequency.

(i) Measurements of gaps between the tank wall and the primary seal (seal gaps) shall be performed during the hydrostatic testing of the vessel or within 60 days of the initial fill with VOL and at least once every 5 years thereafter.

(ii) Measurements of gaps between the tank wall and the secondary seal shall be performed within 60 days of the initial fill with VOL and at least once per year thereafter.

(iii) If any source ceases to store VOL for a period of 1 year or more, subsequent introduction of VOL into the vessel shall be considered an initial fill for the purposes of paragraphs (b)(1)(i) and (b)(1)(ii) of this section.

(2) Determine gap widths and areas in the primary and secondary seals individually by the following procedures:

(i) Measure seal gaps, if any, at one or more floating roof levels when the roof is floating off the roof leg supports.

(ii) Measure seal gaps around the entire circumference of the tank in each place where a 0.32-cm diameter uniform probe passes freely (without forcing or binding against seal) between the seal and the wall of the storage vessel and measure the circumferential distance of each such location.

(iii) The total surface area of each gap described in paragraph (b)(2)(ii) of this section shall be determined by using probes of various widths to measure accurately the actual distance from the tank wall to the seal and multiplying each such width by its respective circumferential distance.

(3) Add the gap surface area of each gap location for the primary seal and the secondary seal individually and divide the sum for each seal by the nominal diameter of the tank and compare each ratio to the respective standards in paragraph (b)(4) of this section.

(4) Make necessary repairs or empty the storage vessel within 45 days of identification in any inspection for seals not meeting the requirements listed in (b)(4) (i) and (ii) of this section:

(i) The accumulated area of gaps between the tank wall and the mechanical shoe or liquid-mounted primary seal shall not exceed 212 cm2 per meter of tank diameter, and the width of any portion of any gap shall not exceed 3.81 cm.

(A) One end of the mechanical shoe is to extend into the stored liquid, and the other end is to extend a minimum vertical distance of 61 cm above the stored liquid surface.

(B) There are to be no holes, tears, or other openings in the shoe, seal fabric, or seal envelope.

(ii) The secondary seal is to meet the following requirements:

(A) The secondary seal is to be installed above the primary seal so that it completely covers the space between the roof edge and the tank wall except as provided in paragraph (b)(2)(iii) of this section.

(B) The accumulated area of gaps between the tank wall and the secondary seal shall not exceed 21.2 cm2 per meter of tank diameter, and the width of any portion of any gap shall not exceed 1.27 cm.

(C) There are to be no holes, tears, or other openings in the seal or seal fabric.

(iii) If a failure that is detected during inspections required in paragraph (b)(1) of §60.113b(b) cannot be repaired within 45 days and if the vessel cannot be emptied within 45 days, a 30-day extension may be requested from the Administrator in the inspection report required in §60.115b(b)(4). Such extension request must include a demonstration of unavailability of alternate storage capacity and a specification of a schedule that will assure that the control equipment will be repaired or the vessel will be emptied as soon as possible.

(5) Notify the Administrator 30 days in advance of any gap measurements required by paragraph (b)(1) of this section to afford the Administrator the opportunity to have an observer present.

(6) Visually inspect the external floating roof, the primary seal, secondary seal, and fittings each time the vessel is emptied and degassed.

(i) If the external floating roof has defects, the primary seal has holes, tears, or other openings in the seal or the seal fabric, or the secondary seal has holes, tears, or other openings in the seal or the seal fabric, the owner or operator shall repair the items as necessary so that none of the conditions specified in this paragraph exist before filling or refilling the storage vessel with VOL.

(ii) For all the inspections required by paragraph (b)(6) of this section, the owner or operator shall notify the Administrator in writing at least 30 days prior to the filling or refilling of each storage vessel to afford the Administrator the opportunity to inspect the storage vessel prior to refilling. If the inspection required by paragraph (b)(6) of this section is not planned and the owner or operator could not have known about the inspection 30 days in advance of refilling the tank, the owner or operator shall notify the Administrator at least 7 days prior to the refilling of the storage vessel. Notification shall be made by telephone immediately followed by written documentation demonstrating why the inspection was unplanned. Alternatively, this notification including the written documentation may be made in writing and sent by express mail so that it is received by the Administrator at least 7 days prior to the refilling.

40 CFR 63.1063(c)(2) requirements:  External floating roofs shall be inspected as specified in paragraphs (c)(2)(i) through (c)(2)(iv), and (d)(3) below.

(c)(2)(i) Within 90 days after the initial filling of the storage vessel, the primary and secondary rim seals shall be inspected as specified in paragraph (d)(3) of this section.

(c)(2)(ii) The secondary seal shall be inspected at least once every year, and the primary seal shall be inspected at least every 5 years, as specified in paragraph (d)(3) of this section.

(c)(2)(iii) Each time the storage vessel is completely emptied and degassed, or every 10 years, whichever occurs first, the EFR shall be inspected as specified in paragraph (d)(1) of this section.

(c)(2)(iv) If the owner or operator determines that it is unsafe to perform the floating roof inspections specified in paragraphs (c)(2)(i) and (c)(2)(ii) of this section, the owner or operator shall comply with the requirements of paragraph (c)(2)(iv)(A) or (c)(2)(iv)(B) of this section.

(d)(3) Seal gap inspections for EFR's shall determine the presence and size of gaps between the rim seals and the wall of the storage vessel by the procedures specified in paragraph (d)(3)(i) of this section. Any exceedance of the gap requirements specified in paragraphs (d)(3)(ii) and (d)(3)(iii) of this section constitutes inspection failure.

(i) Rim seals shall be measured for gaps at one or more levels while the EFR is floating, as specified in paragraphs (d)(3)(i)(A) through (d)(3)(i)(F) of this section.

(A) The inspector shall hold a 0.32-centimeter (1⁄8 inch) diameter probe vertically against the inside of the storage vessel wall, just above the rim seal, and attempt to slide the probe down between the seal and the vessel wall. Each location where the probe passes freely (without forcing or binding against the seal) between the seal and the vessel wall constitutes a gap.

(B) The length of each gap shall be determined by inserting the probe into the gap (vertically) and sliding the probe along the vessel wall in each direction as far as it will travel freely without binding between the seal and the vessel wall. The circumferential length along which the probe can move freely is the gap length.

(C) The maximum width of each gap shall be determined by inserting probes of various diameters between the seal and the vessel wall. The smallest probe diameter should be 0.32 centimeter, and larger probes should have diameters in increments of 0.32 centimeter. The diameter of the largest probe that can be inserted freely anywhere along the length of the gap is the maximum gap width.

(D) The average width of each gap shall be determined by averaging the minimum gap width (0.32 centimeter) and the maximum gap width.

(E) The area of a gap is the product of the gap length and average gap width.

(F) The ratio of accumulated area of rim seal gaps to storage vessel diameter shall be determined by adding the area of each gap, and dividing the sum by the nominal diameter of the storage vessel. This ratio shall be determined separately for primary and secondary rim seals.

(ii) The ratio of seal gap area to vessel diameter for the primary seal shall not exceed 212 square centimeters per meter of vessel diameter (10 square inches per foot of vessel diameter), and the maximum gap width shall not exceed 3.81 centimeters (1.5 inches).

(iii) The ratio of seal gap area to vessel diameter for the secondary seal shall not exceed 21.2 square centimeters per meter (1 square inch per foot), and the maximum gap width shall not exceed 1.27 centimeters (0.5 inches), except when the secondary seal must be pulled back or removed to inspect the primary seal.

[40 CFR 63.11087(c) and 40 CFR 63.11092(e)]

- Expanded Condition B.4. (added the leak inspection requirements of 40 CFR 63.11089.)

- B.4.  Leak Inspection Requirements:  The permittee must comply with the leak inspection requirements of 40 CFR 63.11089.

The permittee shall perform a monthly leak inspection of all equipment in gasoline service, as defined in §63.11100. For this inspection, detection methods incorporating sight, sound, and smell are acceptable.

- A log book shall be used and shall be signed by the owner or operator at the completion of each inspection. A section of the log book shall contain a list, summary description, or diagram(s) showing the location of all equipment in gasoline service at the facility.

- Each detection of a liquid or vapor leak shall be recorded in the log book. When a leak is detected, an initial attempt at repair shall be made as soon as practicable, but no later than 5 calendar days after the leak is detected. Repair or replacement of leaking equipment shall be completed within 15 calendar days after detection of each leak, except as provided in 5d. below.

- Delay of repair of leaking equipment will be allowed if the repair is not feasible within 15 days. The owner or operator shall provide in the semiannual report specified in §63.11095(b), the reason(s) why the repair was not feasible and the date each repair was completed.

- Submit applicable notifications as required under 40 CFR 63.11093 and keep records and submit reports as specified in 40 CFR 63.11094 and 40 CFR 63.11095.

[40 CFR 63.11089]

- Combined Conditions B.6. and B.7., deleted obsolete language, and expanded the condition.

- B.6. Recordkeeping Requirements of 40 CFR 63.11094 and Reporting Requirements of 40 CFR 63.11095. The permittee must comply with the requirements of 40 CFR 63 Subpart BBBBBB except that storage vessels equipped with floating roofs and not meeting the requirements of paragraph (a) of 40 CFR 63.11087 must be in compliance at the first degassing and cleaning activity after January 10, 2011 or by January 10, 2018, whichever is first, including the recordkeeping requirements of 40 CFR 63.11094 and the reporting requirements of 40 CFR 63.11095.

Recordkeeping Requirements of 40 CFR 63.11094:

- The permittee whose storage vessels are subject to the provisions of this subpart shall keep records as specified in 40 CFR 60.115b (listed below) if the permittee is complying with Options 2(a), 2(b), or 2(c) in Table 1 (options listed below) to this subpart, except records shall be kept for at least 5 years. If the permittee is complying with the requirements of Option 2(d) in Table 1 (option listed below) to this subpart, the permittee shall keep records as specified in 40 CFR 63.1065.

40 CFR 60.115b:   The owner or operator of each storage vessel as specified in §60.112b(a) shall keep records and furnish reports as required by paragraphs (a), (b), or (c) of this section depending upon the control equipment installed to meet the requirements of §60.112b. The owner or operator shall keep copies of all reports and records required by this section, except for the record required by (c)(1), for at least 2 years. The record required by (c)(1) will be kept for the life of the control equipment.

(a) 	After installing control equipment in accordance with §60.112b(a)(1) (fixed roof and internal floating roof), the owner or operator shall meet the following requirements.

(1) Furnish the Administrator with a report that describes the control equipment and certifies that the control equipment meets the specifications of §60.112b(a)(1) and §60.113b(a)(1). This report shall be an attachment to the notification required by §60.7(a)(3).

(2) Keep a record of each inspection performed as required by §60.113b (a)(1), (a)(2), (a)(3), and (a)(4). Each record shall identify the storage vessel on which the inspection was performed and shall contain the date the vessel was inspected and the observed condition of each component of the control equipment (seals, internal floating roof, and fittings).

(3) If any of the conditions described in §60.113b(a)(2) are detected during the annual visual inspection required by §60.113b(a)(2), a report shall be furnished to the Administrator within 30 days of the inspection. Each report shall identify the storage vessel, the nature of the defects, and the date the storage vessel was emptied or the nature of and date the repair was made.

(4) After each inspection required by §60.113b(a)(3) that finds holes or tears in the seal or seal fabric, or defects in the internal floating roof, or other control equipment defects listed in §60.113b(a)(3)(ii), a report shall be furnished to the Administrator within 30 days of the inspection. The report shall identify the storage vessel and the reason it did not meet the specifications of §61.112b(a)(1) or §60.113b(a)(3) and list each repair made.

(b) 	After installing control equipment in accordance with §61.112b(a)(2) (external floating roof), the owner or operator shall meet the following requirements.

(1) Furnish the Administrator with a report that describes the control equipment and certifies that the control equipment meets the specifications of §60.112b(a)(2) and §60.113b(b)(2), (b)(3), and (b)(4). This report shall be an attachment to the notification required by §60.7(a)(3).

(2) Within 60 days of performing the seal gap measurements required by §60.113b(b)(1), furnish the Administrator with a report that contains:

(i) The date of measurement.

(ii) The raw data obtained in the measurement.

(iii) The calculations described in §60.113b (b)(2) and (b)(3).

(3) Keep a record of each gap measurement performed as required by §60.113b(b). Each record shall identify the storage vessel in which the measurement was performed and shall contain:

(i) The date of measurement.

(ii) The raw data obtained in the measurement.

(iii) The calculations described in §60.113b (b)(2) and (b)(3).

(4) After each seal gap measurement that detects gaps exceeding the limitations specified by §60.113b(b)(4), submit a report to the Administrator within 30 days of the inspection. The report will identify the vessel and contain the information specified in paragraph (b)(2) of this section and the date the vessel was emptied or the repairs made and date of repair.

(c) 	After installing control equipment in accordance with §60.112b (a)(3) or (b)(1) (closed vent system and control device other than a flare), the owner or operator shall keep the following records.

(1) A copy of the operating plan.

(2) A record of the measured values of the parameters monitored in accordance with §60.113b(c)(2).

(d) 	After installing a closed vent system and flare to comply with §60.112b, the owner or operator shall meet the following requirements.

(1) A report containing the measurements required by §60.18(f) (1), (2), (3), (4), (5), and (6) shall be furnished to the Administrator as required by §60.8 of the General Provisions. This report shall be submitted within 6 months of the initial start-up date.

(2) Records shall be kept of all periods of operation during which the flare pilot flame is absent.

(3) Semiannual reports of all periods recorded under §60.115b(d)(2) in which the pilot flame was absent shall be furnished to the Administrator.

40 CFR 63.1065: The permittee shall keep the records required in paragraph (a) of this section for as long as liquid is stored. Records required in paragraphs (b), (c) and (d) of this section shall be kept for at least 5 years. Records shall be kept in such a manner that they can be readily accessed within 24 hours. Records may be kept in hard copy or computer-readable form including, but not limited to, on paper, microfilm, computer, floppy disk, magnetic tape, or microfiche.

(a) 	Vessel dimensions and capacity. A record shall be kept of the dimensions of the storage vessel, an analysis of the capacity of the storage vessel, and an identification of the liquid stored.

(b) 	Inspection results. Records of floating roof inspection results shall be kept as specified in paragraphs (b)(1) and (b)(2) of this section.

(1) If the floating roof passes inspection, a record shall be kept that includes the information specified in paragraphs (b)(1)(i) and (b)(1)(ii) of this section. If the floating roof fails inspection, a record shall be kept that includes the information specified in paragraphs (b)(1)(i) through (b)(1)(v) of this section.

(i) Identification of the storage vessel that was inspected.

(ii) The date of the inspection.

(iii) A description of all inspection failures.

(iv) A description of all repairs and the dates they were made.

(v) The date the storage vessel was removed from service, if applicable.

(2) A record shall be kept of EFR seal gap measurements, including the raw data obtained and any calculations performed.

(c) Floating Roof Landings.  The owner or operator shall keep a record of the date when a floating roof is set on its legs or other support devices. The owner or operator shall also keep a record of the date when the roof was refloated, and the record shall indicate whether the process of refloating was continuous.

(d) An owner or operator who elects to use an extension in accordance with §63.1063(e)(2) or §63.1063(c)(2)(iv)(B) shall keep the documentation required by those paragraphs.

Options listed in Table 1 of 40 CFR 63 Subpart BBBBBB:

Option 2(a) in Table 1: Reduce emissions of total organic HAP or TOC by 95 weight-percent with a closed vent system and control device, as specified in §60.112b(a)(3) of this chapter; or

Option 2(b) in Table 1: Equip each internal floating roof gasoline storage tank according to the requirements in §60.112b(a)(1) of this chapter, except for the secondary seal requirements under §60.112b(a)(1)(ii)(B) and the requirements in §60.112b(a)(1)(iv) through (ix) of this chapter; and

Option 2(c) in Table 1: Equip each external floating roof gasoline storage tank according to the requirements in §60.112b(a)(2) of this chapter, except that the requirements of §60.112b(a)(2)(ii) of this chapter shall only be required if such storage tank does not currently meet the requirements of §60.112b(a)(2)(i) of this chapter; or

Option 2(d) in Table 1: Equip and operate each internal and external floating roof gasoline storage tank according to the applicable requirements in §63.1063(a)(1) and (b), except for the secondary seal requirements under §63.1063(a)(1)(i)(C) and (D), and equip each external floating roof gasoline storage tank according to the requirements of §63.1063(a)(2) if such storage tank does not currently meet the requirements of §63.1063(a)(1).

- Each owner or operator of a bulk gasoline terminal subject to the provisions of this subpart shall keep records of the test results for each gasoline cargo tank loading at the facility as specified in paragraphs (b)(1) and (b)(2) below.

(1) Annual certification testing performed under §63.11092(f)(1) and periodic railcar bubble leak testing performed under §63.11092(f)(2).

(2) The documentation file shall be kept up-to-date for each gasoline cargo tank loading at the facility. The documentation for each test shall include, as a minimum, the following information:

(i) Name of test: Annual Certification Test—Method 27 or Periodic Railcar Bubble Leak Test Procedure.

(ii) Cargo tank owner's name and address.

(iii) Cargo tank identification number.

(iv) Test location and date.

(v) Tester name and signature.

(vi) Witnessing inspector, if any: Name, signature, and affiliation.

(vii) Vapor tightness repair: Nature of repair work and when performed in relation to vapor tightness testing.

(viii) Test results: Test pressure; pressure or vacuum change, mm of water; time period of test; number of leaks found with instrument; and leak definition.

Reporting Requirements of 40 CFR 63.11095:

- The permittee shall include in a semiannual compliance report to the Administrator the following information, as applicable:

(1) For storage vessels, if you are complying with options 2(a), 2(b), or 2(c) in Table 1 to this subpart, the information specified in §60.115b(a), §60.115b(b), or §60.115b(c) of this chapter, depending upon the control equipment installed, or, if you are complying with option 2(d) in Table 1 to this subpart, the information specified in §63.1066.

(2) For loading racks, each loading of a gasoline cargo tank for which vapor tightness documentation had not been previously obtained by the facility.

(3) For equipment leak inspections, the number of equipment leaks not repaired within 15 days after detection.

(4) For storage vessels complying with §63.11087(b) after January 10, 2011, the storage vessel's Notice of Compliance Status information can be included in the next semi-annual compliance report in lieu of filing a separate Notification of Compliance Status report under §63.11093.

- The permittee shall submit an excess emissions report to the Administrator at the time the semiannual compliance report is submitted. Excess emissions events under this subpart, and the information to be included in the excess emissions report, are specified in paragraphs (b)(1) through (5) below:

(1) Each instance of a non-vapor-tight gasoline cargo tank loading at the facility in which the owner or operator failed to take steps to assure that such cargo tank would not be reloaded at the facility before vapor tightness documentation for that cargo tank was obtained.

(2) Each reloading of a non-vapor-tight gasoline cargo tank at the facility before vapor tightness documentation for that cargo tank is obtained by the facility in accordance with §63.11094(b).

(3) Each exceedance or failure to maintain, as appropriate, the monitored operating parameter value determined under §63.11092(b). The report shall include the monitoring data for the days on which exceedances or failures to maintain have occurred, and a description and timing of the steps taken to repair or perform maintenance on the vapor collection and processing systems or the CMS.

(4) Each instance in which malfunctions discovered during the monitoring and inspections required under §63.11092(b)(1)(i)(B)(2) and (b)(1)(iii)(B)(2) were not resolved according to the necessary corrective actions described in the monitoring and inspection plan. The report shall include a description of the malfunction and the timing of the steps taken to correct the malfunction.

(5) For each occurrence of an equipment leak for which no repair attempt was made within 5 days or for which repair was not completed within 15 days after detection:

(i) The date on which the leak was detected;

(ii) The date of each attempt to repair the leak;

(iii) The reasons for the delay of repair; and

(iv) The date of successful repair.

[40 CFR 63.11087(b), 40 CFR 63.11087(e), 40 CFR 63.11094, 40 CFR 63.11095(a)(1), and 40 CFR 63.11095]

{Permitting Note:  Applicant requested that the language in Condition No. B.6. be included in this section of the permit.}

{Permitting Note:  See 40 CFR 63.11095(a)(1) for storage vessels reporting requirements.}

- Minor revision of Condition C.1., shell capacity (bbl) in bold letters, combined the 2 permitting notes into one permitting note, placed rule citation before permitting note.

- C.1. Capacity.  Individual tanks are permitted as follows:

| Tank # | Primary Seal / Secondary Seal | Worst-Case Product | Shell Capacity (bbl) | Roof Type | NSPS | NESHAP |
| --- | --- | --- | --- | --- | --- | --- |
| 8 | Mechanical Shoe Rim-Mounted | Gasoline | 121,838 | IFR | Kb | BBBBBB |
| 17 | Vapor-Mounted Rim-Mounted | Gasoline | 99,388 | IFR | K | BBBBBB |
| 18 | Vapor-Mounted Rim-Mounted | Gasoline | 98,317 | IFR | K | BBBBBB |

[Rule 62-210.200, (PTE), F.A.C., and construction permit 0090029-001-AC]

{Permit Note: Worst-case product is defined as the product that is expected to result in the highest emission of volatile organic compounds. It does not limit the storage of lower vapor products (e.g. storage tanks that identify gasoline as the worst-case product are also authorized to store ethanol).

A mechanical shoe seal is a metal sheet held vertically against the tank shell by spring. It is connected by brace arms to the floating roof.  A flexible coated fabric (continuous seal) spans the annular space between the shoe plate and the rim plate of the floating roof.}

- Added “Test Method” Condition C.2.

- C.2. Test Method:  When required, tests shall be performed in accordance with the following reference methods:

| Method | Description of Method and Comments |
| --- | --- |
| 27 | Vapor Tightness of Gasoline Tank – Pressure Vacuum |

The above method is described in Appendix A of 40 CFR 60 and are adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Rule 62-204.800, F.A.C.; and Appendix A of 40 CFR 60]

- Renumbered Condition C.2. to C.3. and expanded condition (added the inspection requirements of 40 CFR 63.11092(e)(1) and 40 CFR 60.113(b)(a)(2)) and deleted obsolete language.

- C.3. The permittee must comply with the inspection requirements of 40 CFR 63.11092(e)(1) and 40 CFR 60.113(b)(a)(2).

Inspection Requirements.  The permittee shall perform inspections of the floating roof system according to the applicable requirements of §60.113b(a)(listed below) if the permittee is complying with option 2(b) in Table 1 to 40 CFR 63 Subpart BBBBBB, or according to the requirements of §63.1063(c)(1) if you are complying with option 2(d) in Table 1 to 40 CFR 63 Subpart BBBBBB.

40 CFR 60.113b(a) Requirements: For Vessels equipped with a liquid-mounted or mechanical shoe primary seal, visually inspect the internal floating roof and the primary seal or the secondary seal (if one is in service) through manholes and roof hatches on the fixed roof at least once every 12 months after initial fill. If the internal floating roof is not resting on the surface of the VOL inside the storage vessel, or there is liquid accumulated on the roof, or the seal is detached, or there are holes or tears in the seal fabric, the owner or operator shall repair the items or empty and remove the storage vessel from service within 45 days. If a failure that is detected during inspections required in this paragraph cannot be repaired within 45 days and if the vessel cannot be emptied within 45 days, a 30-day extension may be requested from the Administrator in the inspection report required in §60.115b(a)(3). Such a request for an extension must document that alternate storage capacity is unavailable and specify a schedule of actions the company will take that will assure that the control equipment will be repaired or the vessel will be emptied as soon as possible.

40 CFR 63.1063(c)(1) Requirements:  Internal floating roofing (IFR) inspections and repairs shall be performed as specified in (c), (d), and (e) below.

(c) Inspection frequency requirements for Internal floating roofs. Internal floating roofs shall be inspected as specified in paragraph (d)(1) of this section before the initial filling of the storage vessel. Subsequent inspections shall be performed as specified in paragraph (c)(1)(i) or (c)(1)(ii) below.

(i) Internal floating roofs shall be inspected as specified in paragraphs (c)(1)(i)(A) and (c)(1)(i)(B) of this section.

(A) At least once per year the IFR shall be inspected as specified in paragraph (d)(2) of this section.

(B) Each time the storage vessel is completely emptied and degassed, or every 10 years, whichever occurs first, the IFR shall be inspected as specified in paragraph (d)(1) below.

(ii) Instead of the inspection frequency specified in paragraph (c)(1)(i) of this section, internal floating roofs with two rim seals may be inspected as specified in paragraph (d)(1) of this section each time the storage vessel is completely emptied and degassed, or every 5 years, whichever occurs first.

(d) Inspection procedure requirements. Floating roof inspections shall be conducted as specified in paragraphs (d)(1), as applicable. If a floating roof fails an inspection, the owner or operator shall comply with the repair requirements of paragraph (e) of this section.

(1) Floating roof (IFR and EFR) inspections shall be conducted by visually inspecting the floating roof deck, deck fittings, and rim seals from within the storage vessel. The inspection may be performed entirely from the top side of the floating roof, as long as there is visual access to all deck components specified in paragraph (a) of this section. Any of the conditions described in paragraphs (d)(1)(i) through (d)(1)(v) of this section constitutes inspection failure.

(i) Stored liquid on the floating roof.

(ii) Holes or tears in the primary or secondary seal (if one is present).

(iii) Floating roof deck, deck fittings, or rim seals that are not functioning as designed (as specified in paragraph (a) of this section).

(iv) Failure to comply with the operational requirements of paragraph (b) of this section.

(v) Gaps of more than 0.32 centimeters (1⁄8 inch) between any deck fitting gasket, seal, or wiper (required by paragraph (a) of this section) and any surface that it is intended to seal.

(e) Repair requirements. Conditions causing inspection failures under paragraph (d) of this section shall be repaired as specified in paragraph (e)(1) or (e)(2) of this section.

(1) If the inspection is performed while the storage vessel is not storing liquid, repairs shall be completed before the refilling of the storage vessel with liquid.

(2) If the inspection is performed while the storage vessel is storing liquid, repairs shall be completed or the vessel removed from service within 45 days. If a repair cannot be completed and the vessel cannot be emptied within 45 days, the owner or operator may use up to 2 extensions of up to 30 additional days each. Documentation of a decision to use an extension shall include a description of the failure, shall document that alternate storage capacity is unavailable, and shall specify a schedule of actions that will ensure that the control equipment will be repaired or the vessel will be completely emptied as soon as practical.40 CFR 63.1063(c)(1) Requirements: For Vessels equipped with a liquid-mounted or mechanical shoe primary seal, visually inspect the internal floating roof and the primary seal or the secondary seal (if one is in service) through manholes and roof hatches on the fixed roof at least once every 12 months after initial fill. If the internal floating roof is not resting on the surface of the VOL inside the storage vessel, or there is liquid accumulated on the roof, or the seal is detached, or there are holes or tears in the seal fabric, the owner or operator shall repair the items or empty and remove the storage vessel from service within 45 days. If a failure that is detected during inspections required in this paragraph cannot be repaired within 45 days and if the vessel cannot be emptied within 45 days, a 30-day extension may be requested from the Administrator in the inspection report required in §60.115b(a)(3). Such a request for an extension must document that alternate storage capacity is unavailable and specify a schedule of actions the company will take that will assure that the control equipment will be repaired or the vessel will be emptied as soon as possible. 		   [40 CFR 63.11087(c) and 40 CFR 63.11092(e)]

- Renumbered Condition C.3. and expanded condition (added the leak inspection requirements of 40 CFR 63.11089).

- C.4. Leak Inspection Requirements:  The permittee must comply with the leak inspection requirements of 40 CFR 63.11089.

- The permittee shall perform a monthly leak inspection of all equipment in gasoline service, as defined in §63.11100. For this inspection, detection methods incorporating sight, sound, and smell are acceptable.

- A log book shall be used and shall be signed by the owner or operator at the completion of each inspection. A section of the log book shall contain a list, summary description, or diagram(s) showing the location of all equipment in gasoline service at the facility.

- Each detection of a liquid or vapor leak shall be recorded in the log book. When a leak is detected, an initial attempt at repair shall be made as soon as practicable, but no later than 5 calendar days after the leak is detected. Repair or replacement of leaking equipment shall be completed within 15 calendar days after detection of each leak, except as provided in 5d. below.

- Delay of repair of leaking equipment will be allowed if the repair is not feasible within 15 days. The owner or operator shall provide in the semiannual report specified in §63.11095(b), the reason(s) why the repair was not feasible and the date each repair was completed.

- Submit applicable notifications as required under 40 CFR 63.11093 and keep records and submit reports as specified in 40 CFR 63.11094 and 40 CFR 63.11095.

[40 CFR 63.11089]

- Renumbered Condition C.4. and revised permitting note.

- C.5. Recordkeeping. In order to demonstrate compliance with Condition No. C.1., the permittee shall maintain records at the facility for a period of at least 5 years from the date the data is recorded. The records shall contain the following:

Monthly

- Facility Name, Facility ID No. (i.e., 0090029);

- Month and year of record;

- Petroleum type and tank capacity;

- Most recent monthly total of petroleum throughput; and

- Most recent consecutive 12-month total of petroleum throughput.

The monthly logs shall be completed by the end of the following month.

[Rules 62 4.070(3) and 62 213.440(1)(b)2., F.A.C.]

{Permitting Note:  Throughput is needed for EPA’s TANKS 4.09 D Program Trinity Consultants Tank ESP software to calculate emissions.}

- Expanded Condition C.6. (adding the recordkeeping requirements of 40 CFR 63.11094 and the reporting requirements of 40 CFR 63.11095).

- Recordkeeping Requirements of 40 CFR 63.11094 and Reporting Requirements of 40 CFR 63.11095:  The permittee must comply with the requirements of 40 CFR 63 Subpart BBBBBB, including the recordkeeping requirements of 40 CFR 63.11094 and the reporting requirements of 40 CFR 63.11095.

Recordkeeping Requirements of 40 CFR 63.11094:

a.	The permittee whose storage vessels are subject to the provisions of this subpart shall keep records as specified in 40 CFR 60.115b (listed below) if the permittee is complying with Options 2(a), 2(b), or 2(c) in Table 1 (options listed below) to this subpart, except records shall be kept for at least 5 years. If the permittee is complying with the requirements of Option 2(d) in Table 1 (option listed below) to this subpart, the permittee shall keep records as specified in 40 CFR 63.1065.

40 CFR 60.115b:   The owner or operator of each storage vessel as specified in §60.112b(a) shall keep records and furnish reports as required by paragraphs (a), (b), or (c) of this section depending upon the control equipment installed to meet the requirements of §60.112b. The owner or operator shall keep copies of all reports and records required by this section, except for the record required by (c)(1), for at least 2 years. The record required by (c)(1) will be kept for the life of the control equipment.

(a) 	After installing control equipment in accordance with §60.112b(a)(1) (fixed roof and internal floating roof), the owner or operator shall meet the following requirements.

(1) Furnish the Administrator with a report that describes the control equipment and certifies that the control equipment meets the specifications of §60.112b(a)(1) and §60.113b(a)(1). This report shall be an attachment to the notification required by §60.7(a)(3).

(2) Keep a record of each inspection performed as required by §60.113b (a)(1), (a)(2), (a)(3), and (a)(4). Each record shall identify the storage vessel on which the inspection was performed and shall contain the date the vessel was inspected and the observed condition of each component of the control equipment (seals, internal floating roof, and fittings).

(3) If any of the conditions described in §60.113b(a)(2) are detected during the annual visual inspection required by §60.113b(a)(2), a report shall be furnished to the Administrator within 30 days of the inspection. Each report shall identify the storage vessel, the nature of the defects, and the date the storage vessel was emptied or the nature of and date the repair was made.

(4) After each inspection required by §60.113b(a)(3) that finds holes or tears in the seal or seal fabric, or defects in the internal floating roof, or other control equipment defects listed in §60.113b(a)(3)(ii), a report shall be furnished to the Administrator within 30 days of the inspection. The report shall identify the storage vessel and the reason it did not meet the specifications of §61.112b(a)(1) or §60.113b(a)(3) and list each repair made.

(b) 	After installing control equipment in accordance with §61.112b(a)(2) (external floating roof), the owner or operator shall meet the following requirements.

(1) Furnish the Administrator with a report that describes the control equipment and certifies that the control equipment meets the specifications of §60.112b(a)(2) and §60.113b(b)(2), (b)(3), and (b)(4). This report shall be an attachment to the notification required by §60.7(a)(3).

(2) Within 60 days of performing the seal gap measurements required by §60.113b(b)(1), furnish the Administrator with a report that contains:

(i) The date of measurement.

(ii) The raw data obtained in the measurement.

(iii) The calculations described in §60.113b (b)(2) and (b)(3).

(3) Keep a record of each gap measurement performed as required by §60.113b(b). Each record shall identify the storage vessel in which the measurement was performed and shall contain:

(i) The date of measurement.

(ii) The raw data obtained in the measurement.

(iii) The calculations described in §60.113b (b)(2) and (b)(3).

(4) After each seal gap measurement that detects gaps exceeding the limitations specified by §60.113b(b)(4), submit a report to the Administrator within 30 days of the inspection. The report will identify the vessel and contain the information specified in paragraph (b)(2) of this section and the date the vessel was emptied or the repairs made and date of repair.

(c) 	After installing control equipment in accordance with §60.112b (a)(3) or (b)(1) (closed vent system and control device other than a flare), the owner or operator shall keep the following records.

(1) A copy of the operating plan.

(2) A record of the measured values of the parameters monitored in accordance with §60.113b(c)(2).

(d) 	After installing a closed vent system and flare to comply with §60.112b, the owner or operator shall meet the following requirements.

(1) A report containing the measurements required by §60.18(f) (1), (2), (3), (4), (5), and (6) shall be furnished to the Administrator as required by §60.8 of the General Provisions. This report shall be submitted within 6 months of the initial start-up date.

(2) Records shall be kept of all periods of operation during which the flare pilot flame is absent.

(3) Semiannual reports of all periods recorded under §60.115b(d)(2) in which the pilot flame was absent shall be furnished to the Administrator.

40 CFR 63.1065: The permittee shall keep the records required in paragraph (a) of this section for as long as liquid is stored. Records required in paragraphs (b), (c) and (d) of this section shall be kept for at least 5 years. Records shall be kept in such a manner that they can be readily accessed within 24 hours. Records may be kept in hard copy or computer-readable form including, but not limited to, on paper, microfilm, computer, floppy disk, magnetic tape, or microfiche.

(a) 	Vessel dimensions and capacity. A record shall be kept of the dimensions of the storage vessel, an analysis of the capacity of the storage vessel, and an identification of the liquid stored.

(b) 	Inspection results. Records of floating roof inspection results shall be kept as specified in paragraphs (b)(1) and (b)(2) of this section.

(1) If the floating roof passes inspection, a record shall be kept that includes the information specified in paragraphs (b)(1)(i) and (b)(1)(ii) of this section. If the floating roof fails inspection, a record shall be kept that includes the information specified in paragraphs (b)(1)(i) through (b)(1)(v) of this section.

(i) Identification of the storage vessel that was inspected.

(ii) The date of the inspection.

(iii) A description of all inspection failures.

(iv) A description of all repairs and the dates they were made.

(v) The date the storage vessel was removed from service, if applicable.

(2) A record shall be kept of EFR seal gap measurements, including the raw data obtained and any calculations performed.

(c) Floating Roof Landings.  The owner or operator shall keep a record of the date when a floating roof is set on its legs or other support devices. The owner or operator shall also keep a record of the date when the roof was refloated, and the record shall indicate whether the process of refloating was continuous.

(d) An owner or operator who elects to use an extension in accordance with §63.1063(e)(2) or §63.1063(c)(2)(iv)(B) shall keep the documentation required by those paragraphs.

Options listed in Table 1 of 40 CFR 63 Subpart BBBBBB:

Option 2(a) in Table 1: Reduce emissions of total organic HAP or TOC by 95 weight-percent with a closed vent system and control device, as specified in §60.112b(a)(3) of this chapter; or

Option 2(b) in Table 1: Equip each internal floating roof gasoline storage tank according to the requirements in §60.112b(a)(1) of this chapter, except for the secondary seal requirements under §60.112b(a)(1)(ii)(B) and the requirements in §60.112b(a)(1)(iv) through (ix) of this chapter; and

Option 2(c) in Table 1: Equip each external floating roof gasoline storage tank according to the requirements in §60.112b(a)(2) of this chapter, except that the requirements of §60.112b(a)(2)(ii) of this chapter shall only be required if such storage tank does not currently meet the requirements of §60.112b(a)(2)(i) of this chapter; or

Option 2(d) in Table 1: Equip and operate each internal and external floating roof gasoline storage tank according to the applicable requirements in §63.1063(a)(1) and (b), except for the secondary seal requirements under §63.1063(a)(1)(i)(C) and (D), and equip each external floating roof gasoline storage tank according to the requirements of §63.1063(a)(2) if such storage tank does not currently meet the requirements of §63.1063(a)(1).

b.	Each owner or operator of a bulk gasoline terminal subject to the provisions of this subpart shall keep records of the test results for each gasoline cargo tank loading at the facility as specified in paragraphs (b)(1) and (b)(2) below.

(1) Annual certification testing performed under §63.11092(f)(1) and periodic railcar bubble leak testing performed under §63.11092(f)(2).

(2) The documentation file shall be kept up-to-date for each gasoline cargo tank loading at the facility. The documentation for each test shall include, as a minimum, the following information:

(i) Name of test: Annual Certification Test—Method 27 or Periodic Railcar Bubble Leak Test Procedure.

(ii) Cargo tank owner's name and address.

(iii) Cargo tank identification number.

(iv) Test location and date.

(v) Tester name and signature.

(vi) Witnessing inspector, if any: Name, signature, and affiliation.

(vii) Vapor tightness repair: Nature of repair work and when performed in relation to vapor tightness testing.

(viii) Test results: Test pressure; pressure or vacuum change, mm of water; time period of test; number of leaks found with instrument; and leak definition.

Reporting Requirements of 40 CFR 63.11095:

c.	The permittee shall include in a semiannual compliance report to the Administrator the following information, as applicable:

(1) For storage vessels, if you are complying with options 2(a), 2(b), or 2(c) in Table 1 to this subpart, the information specified in §60.115b(a), §60.115b(b), or §60.115b(c) of this chapter, depending upon the control equipment installed, or, if you are complying with option 2(d) in Table 1 to this subpart, the information specified in §63.1066.

(2) For loading racks, each loading of a gasoline cargo tank for which vapor tightness documentation had not been previously obtained by the facility.

(3) For equipment leak inspections, the number of equipment leaks not repaired within 15 days after detection.

(4) For storage vessels complying with §63.11087(b) after January 10, 2011, the storage vessel's Notice of Compliance Status information can be included in the next semi-annual compliance report in lieu of filing a separate Notification of Compliance Status report under §63.11093.

d.	The permittee shall submit an excess emissions report to the Administrator at the time the semiannual compliance report is submitted. Excess emissions events under this subpart, and the information to be included in the excess emissions report, are specified in paragraphs (b)(1) through (5) below:

(1) Each instance of a non-vapor-tight gasoline cargo tank loading at the facility in which the owner or operator failed to take steps to assure that such cargo tank would not be reloaded at the facility before vapor tightness documentation for that cargo tank was obtained.

(2) Each reloading of a non-vapor-tight gasoline cargo tank at the facility before vapor tightness documentation for that cargo tank is obtained by the facility in accordance with §63.11094(b).

(3) Each exceedance or failure to maintain, as appropriate, the monitored operating parameter value determined under §63.11092(b). The report shall include the monitoring data for the days on which exceedances or failures to maintain have occurred, and a description and timing of the steps taken to repair or perform maintenance on the vapor collection and processing systems or the CMS.

(4) Each instance in which malfunctions discovered during the monitoring and inspections required under §63.11092(b)(1)(i)(B)(2) and (b)(1)(iii)(B)(2) were not resolved according to the necessary corrective actions described in the monitoring and inspection plan. The report shall include a description of the malfunction and the timing of the steps taken to correct the malfunction.

(5) For each occurrence of an equipment leak for which no repair attempt was made within 5 days or for which repair was not completed within 15 days after detection:

(i) The date on which the leak was detected;

(ii) The date of each attempt to repair the leak;

(iii) The reasons for the delay of repair; and

(iv) The date of successful repair.

[40 CFR 63.11087(b), 40 CFR 63.11087(e), 40 CFR 63.11094, 40 CFR 63.11095(a)(1), and 40 CFR 63.11095]

{Permitting Note:  See 40 CFR 63.11095(a)(1) for storage vessels reporting requirements.}

- Combined and reorganized Conditions C.7. and C.8. into Condition C.7.

- C.7. Tank 8 is subject to Rule 62 204.800(8)(b)18., F.A.C., and 40 CFR Part 60, Subpart Kb, for Volatile Organic Liquid Storage Vessels.  Tanks 17 and 18 are subject to Rule 62-204.800(8)(b)16., F.A.C., and 40 CFR Part 60, Subpart K, for Petroleum Liquid Storage Vessels.  Tanks #8, #17, and #18 are subject to 40 CFR Part 60, Subpart A, General Provisions. [Rule 62-204.800(8), F.A.C. and 40 CFR Part 60, Subparts A, Kb and K]

{Permitting Note: 40 CFR Part 60, Subpart K applies to storage vessels for petroleum liquids for which construction, reconstruction, or modification commenced after June 11, 1973, and prior to May 19, 1978.  This regulation applies to Tanks 17 and 18, because both tanks were built in 1974.  40 CFR Part 60 Subpart Kb applies volatile organic liquid storage vessels (including petroleum liquid storage vessels) for which construction, reconstruction, or modification commenced after July 23, 1984.  This regulation applies to Tank 8, because it was built in 1992.}

- Reformatted Condition D.1.

- D.1. Capacity:  The gasoline and diesel throughput rates at the South Rack are limited to the following maximum throughput rates:

| Petroleum Product | Location | Maximum Throughput Rate (gallons per consecutive twelve months) |
| --- | --- | --- |
| Gasoline | South Rack | 315,000,000 |
| Diesel | South Rack | 100,800,000 |

[Rule 62-210.200, (PTE), F.A.C., and Permit No. 0090029-001-AC as revised 10/30/98]

- Reformatted Condition D.3.

- D.3. Emission Limit:  Emissions to the atmosphere from the vapor collection and processing systems due to loading of gasoline cargo tanks shall not exceed the following limit:

| Pollutant | Maximum Emissions Rate (milligrams per liter (mg/L) of gasoline loaded) |
| --- | --- |
| Total Organic Compound (TOC) Emissions | 35 |

[Permit No. 0090029-001-AC; 40 CFR 60.502(b), and Rule 62-204.800(8)(b)57., F.A.C.]

{Permitting Note: 1 U.S. gallon equals 3.7854 liters}

- Expanded Condition D.5.

- Testing Requirements of 40 CFR 60.503.  The permittee shall comply with Testing Requirements and procedures in 40 CFR 60.503 (listed below).  See attached Appendix NSPS, Subpart XX, attached to this permit.  The testing shall be conducted prior to the expiration date of this permit.  The testing frequency is every five years, but compliance testing shall be conducted prior to the permit expiration date (see permitting note at the end of this condition).

40 CFR 60.503 (Test and Procedures):

- In conducting the performance tests required in §60.8, the owner or operator shall use as reference methods and procedures the test methods in appendix A of this part or other methods and procedures as specified in this section, except as provided in §60.8(b). The three-run requirement of §60.8(f) does not apply to this subpart.

- Immediately before the performance test required to determine compliance with §60.502 (b), (c), and (h), the owner or operator shall use Method 21 to monitor for leakage of vapor all potential sources in the terminal's vapor collection system equipment while a gasoline tank truck is being loaded. The owner or operator shall repair all leaks with readings of 10,000 ppm (as methane) or greater before conducting the performance test.

- The owner or operator shall determine compliance with the standards in §60.502 (b) and (c) as follows:

1) The performance test shall be 6 hours long during which at least 300,000 liters of gasoline is loaded. If this is not possible, the test may be continued the same day until 300,000 liters of gasoline is loaded or the test may be resumed the next day with another complete 6-hour period. In the latter case, the 300,000-liter criterion need not be met. However, as much as possible, testing should be conducted during the 6-hour period in which the highest throughput normally occurs.

(2) If the vapor processing system is intermittent in operation, the performance test shall begin at a reference vapor holder level and shall end at the same reference point. The test shall include at least two startups and shutdowns of the vapor processor. If this does not occur under automatically controlled operations, the system shall be manually controlled.

(3) The emission rate (E) of total organic compounds shall be computed using the following equation:

where:

E = emission rate of total organic compounds, mg/liter of gasoline loaded.

Vesi = volume of air-vapor mixture exhausted at each interval “i”, scm.

Cei = concentration of total organic compounds at each interval “i”, ppm.

L = total volume of gasoline loaded, liters.

n = number of testing intervals.

i = emission testing interval of 5 minutes.

K = density of calibration gas, 1.83 × 106 for propane and 2.41 × 106 for butane, mg/scm.

(4) The performance test shall be conducted in intervals of 5 minutes. For each interval “i”, readings from each measurement shall be recorded, and the volume exhausted (Vesi) and the corresponding average total organic compounds concentration (Cei) shall be determined. The sampling system response time shall be considered in determining the average total organic compounds concentration corresponding to the volume exhausted.

(5) The following methods shall be used to determine the volume (Vesi) air-vapor mixture exhausted at each interval:

(i) Method 2B shall be used for combustion vapor processing systems.

(ii) Method 2A shall be used for all other vapor processing systems.

(6) Method 25A or 25B shall be used for determining the total organic compounds concentration (Cei) at each interval. The calibration gas shall be either propane or butane. The owner or operator may exclude the methane and ethane content in the exhaust vent by any method (e.g., Method 18) approved by the Administrator.

(7) To determine the volume (L) of gasoline dispensed during the performance test period at all loading racks whose vapor emissions are controlled by the processing system being tested, terminal records or readings from gasoline dispensing meters at each loading rack shall be used.

- The owner or operator shall determine compliance with the standard in §60.502(h) as follows:

(1) A pressure measurement device (liquid manometer, magnehelic gauge, or equivalent instrument), capable of measuring up to 500 mm of water gauge pressure with ±2.5 mm of water precision, shall be calibrated and installed on the terminal's vapor collection system at a pressure tap located as close as possible to the connection with the gasoline tank truck.

(2) During the performance test, the pressure shall be recorded every 5 minutes while a gasoline truck is being loaded; the highest instantaneous pressure that occurs during each loading shall also be recorded. Every loading position must be tested at least once during the performance test.

- The performance test requirements of paragraph (c) of this section do not apply to flares defined in §60.501 and meeting the requirements in §60.18(b) through (f). The owner or operator shall demonstrate that the flare and associated vapor collection system is in compliance with the requirements in §§60.18(b) through (f) and 60.503(a), (b), and (d).

[40 CFR 60.503; and Rules 62-204.800(8)(b)56., 62-204.800(8)(d), and 62 297.310(6), F.A.C.]

{Permitting Note:  Tests which are only required once during the term of a permit prior to obtaining a renewed permit should be performed roughly five years from the previous test.}

- Condition D.9. Test Reports. Replaced language in the condition with Title V permitting template language.  The testing requirements previously listed in the condition can be found in Appendix TR, Facility-Wide Testing Requirements.

- D.9.  Test Reports.

a.	The owner or operator of an emissions unit for which a compliance test is required (Condition D.5.) to meet an emission limitation (Condition D.3.) shall file a report with the Department on the results of each such test.   All documents related to compliance activities such as reports, tests, and notifications shall be submitted to the Central District Compliance Assurance Program. (Use the email address DEP_CD@dep.state.fl.us)  In each document, clearly identify the Air Permit Project No. 0090029-013-AV and specific emission unit (EU 006).

b.	The required test report shall be filed with the Department as soon as practical but no later than 45 days after the last sampling run of each test is completed.

c.	The test report shall provide sufficient detail on the emissions unit tested and the test procedures used to allow the Department to determine if the test was properly conducted and the test results properly computed.  As a minimum, the test report, other than for an EPA or DEP Method 9 test, shall provide the following information.

(1)	The type, location, and designation of the emissions unit tested.

(2)	The facility at which the emissions unit is located.

(3)	The owner or operator of the emissions unit.

(4)	The normal type and amount of fuels used and materials processed, and the types and amounts of  fuels used and material processed during each test run.

(5)	The means, raw data and computations used to determine the amount of fuels used and materials  processed, if necessary to determine compliance with an applicable emission limiting standard.

(6)	The type of air pollution control devices installed on the emissions unit, their general condition, their normal operating parameters (pressure drops, total operating current and GPM scrubber water), and their operating parameters during each test run.

(7)	A sketch of the duct within 8 stack diameters upstream and 2 stack diameters downstream of the sampling ports, including the distance to any upstream and downstream bends or other flow disturbances.

(8)	The date, starting time and duration of each sampling run.

(9)	The test procedures used, including any alternative procedures authorized pursuant to Rule 62-297.620, F.A.C.  Where optional procedures are authorized in this chapter, indicate which option was used.

(10) The number of points sampled and configuration and location of the sampling plane.

(11) For each sampling point for each run, the dry gas meter reading, velocity head, pressure drop across the stack, temperatures, average meter temperatures and sample time per point.

(12) The type, manufacturer and configuration of the sampling equipment used.

(13) Data related to the required calibration of the test equipment.

(14) Data on the identification, processing and weights of all filters used.

(15) Data on the types and amounts of any chemical solutions used.

(16) Data on the amount of pollutant collected from each sampling probe, the filters, and the impingers, are reported separately for the compliance test.

(17) The names of individuals who furnished the process variable data, conducted the test, analyzed the samples and prepared the report.

(18) All measured and calculated data required to be determined by each applicable test procedure for each run.

(19) The detailed calculations for one run that relate the collected data to the calculated emission rate.

(20) The applicable emission standard and the resulting maximum allowable emission rate for the emissions unit plus the test result in the same form and unit of measure.

(21) A certification that, to the knowledge of the owner or his authorized agent, all data submitted are true and correct.  When a compliance test is conducted for the Department or its agent, the person who conducts the test shall provide the certification with respect to the test procedures used.  The owner or his authorized agent shall certify that all data required and provided to the person conducting the test are true and correct to his knowledge.

[Rule 62-297.310(8), F.A.C.; Appendix TR, Testing Requirement TR8]

D.9. Common Test Requirements. Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310(8)(10), F.A.C.; Appendix TR, Testing Requirement TR9]

- Reformatted Condition E.2.

- Capacity:  Asphalt Loading at the North Rack and Marine Loading of Diesel or Lower Vapor Pressure Petroleum Product is limited to the following Maximum Loading Rates (gallons per consecutive twelve months):

| Petroleum Product | Location | Maximum Loading Rate (gallons per consecutive twelve months) |
| --- | --- | --- |
| Asphalt | North Rack | 100,800,000 |
| Marine Loading of Diesel or Lower Vapor Pressure Petroleum Product | Marine Dock | 500,000,000 |

[Rule 62-210.200, (PTE), F.A.C. and Permit No. 0090029-001-AC]

{Permitting Note: Emissions are accounted for as diesel under South Rack (EU 006).}

- Deleted Section F., Back-Up Generator, because it is a mobile source.

68.	F1. Restricted Operation:  The hours of operation of the back-up generator at this facility shall not exceed 500 hours per consecutive twelve months.  [Rules 62-4.070(3) and 62-210.200(PTE), F.A.C.]

F2.	Methods of Operation:  The sulfur content of the fuel shall not exceed 0.0015 percent, by weight.  The sulfur content shall be determined using one of the ASTM methods listed in Specific Condition F8. of this permit. [Rules 62-4.070(3) and 62-210.200, (PTE), F.A.C.; and 40 CFR 80, Subpart I]

F3.	Visible Emissions. Visible emissions from the back-up generator shall not exceed 20 percent opacity. [Rule 62-296.320(4)(b)1., F.A.C.]

F4.	Performance Standards: The Back-Up generator is not subject to 40 CFR 60, Subpart IIII or 40 CFR 63 Subpart ZZZZ.

[Rule 62-4.070(3), F.A.C.; and 40 CFR 1068.30]

{Permitting Note: This is a portable, emergency generator that is moved around between TransMontaigne’s Florida Terminals.  As it is portable, it is not subject to 40 CFR 60 Subpart IIII or 40 CFR 63 Subpart ZZZZ.}

F5.	Test Requirements:  There is no test requirement for the back-up generator unless the Department, after investigation, has good reason to believe that any applicable emission standard contained in a Department rule or in a permit issued pursuant to those rules is being violated.  [Rules 62-4.070(3)  and  62-297.310(7), F.A.C.]

F6.	Maintenance Log:  Maintain a log recording maintenance activity performed on the back-up generator according to the manufacturer’s written instructions or procedures over the life of the engine.  A copy of the manufacturer’s written instructions or procedures must be on site and available upon request by a DEP Inspector.

F7.	Sulfur Dioxide - Sulfur Content.  The permittee shall demonstrate compliance with the liquid fuel sulfur limit by providing a fuel analysis upon each fuel delivery to the fuel supply tank.  [Rules 62-213.440 and 62-296.406(3), F.A.C.]

F8.	The fuel sulfur content, percent by weight, for liquid fuels shall be evaluated using one of ASTM D2622-94, ASTM D4294-90(95), ASTM 1552-95, ASTM D1266-91, or both ASTM D4057-88 and ASTM D129-91 or latest editions.

[Rules 62-213.440, 62-296.406(3) and 62-297.440(1), F.A.C.]

F9.	Operational Data:  In order to demonstrate compliance with Specific Conditions No. F1. and F2., the permittee shall maintain records at the facility for a period of at least 5 years from the date the data is recorded. The records shall contain the following:

- Facility Name, Facility ID No. (i.e., 0090029);

- Month and year of record;

- Most recent monthly total of operational hours at this facility;

- Most recent consecutive 12 month total of operational hours at this facility; and

- Certification from the fuel supplier of the fuel’s sulfur content.

The monthly logs shall be completed by the end of the following month.

[Rules 62-4.070(3) and 62-213.440(1)(b)2., F.A.C.]

Brief Discussion of Emissions

The emissions from the facility operations are expected to remain below the following values:

| Pollutant | Potential to Emit Emissions (tpy) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | EU 028- Steam Boiler #3 | EU 024- Asphalt Heaters #5 & #6 | EU 025- Thirteen Petroleum Storage Tanks | EU 026-Three Petroleum Storage Tanks | EU 006-South Rack with Thermal Oxidizer | EU 019-North Dock and Marine Dock | Total Site-Wide Emissions (tpy) |
| PM10 | 0.26 | 1.32 | 0.00 | 0.00 | 0.00 | 0.00 | 1.58 |
| CO | 1.51 | 7.60 | 0.00 | 0.00 | 13.15 | 0.00 | 22.26 |
| SO2 | 0.03 | 0.14 | 0.00 | 0.00 | 0.00 | 0.00 | 0.17 |
| NOx | 2.63 | 13.18 | 0.00 | 0.00 | 5.26 | 0.00 | 21.07 |
| VOC | 0.10 | 0.50 | 30.73 | 50.28 | 63.81 | 3.87 | 149.28* |
| Total HAP | 0.00 | 0.00 | 1.59 | 2.29 | 1.94 | 0.41 | 6.24 |

*Note: The total site-wide VOC emissions amount (tpy) is 149.6 if the back-up generator’s emissions are included.

Emission Factors and Calculations for Potential to Emit (PTE) Emissions

- EU 028	Calculations above are for one heater (using natural gas).  Emission factors are based on AP-42 v.5.0, Section 1.4, 7/98.  Natural Gas Heating Value: 1,020 Btu/scf.  	Pollutant Emission Rate (lb/hr) = (Emission Factor, lb/MMSCF or lb/103 gal) x (Rating, MMbtu/hr) /Emissions (tons per year) = (Pollutant Emission Rate, lb/hr) x (Actual Annual Operating Time, hr/yr) / (2000 lb/ton).   Use 8,760 hrs. per year.

| Pollutant | Emission Factors (lb/MMSCF) | Emission Rates (lb/hr) | Emissions (tons per year) |
| --- | --- | --- | --- |
| PM10 | 7.6 lb/MMSCF | 0.031 | 0.14 |
| CO | 84.0 lb/MMSCF | 0.346 | 1.51 |
| SO2 | 0.60 lb/MMSCF | 0.002 | 0.01 |
| NOx | 100.0 lb/MMSCF | 0.412 | 1.80 |
| VOC (nonmethane) | 5.5 lb/MMSCF | 0.023 | 0.10 |

- EU 024 	Calculations above are for one heater (using natural gas). Emission factors are based on AP-42 v.5.0, Section 1.4, 7/98.  Natural Gas Heating Value: 1,020 Btu/scf. Emissions (tons per year) = (Pollutant Emission Rate, lb/hr) x (Actual Annual Operating Time, hr/yr) / (2000 lb/ton). Use 8,760 hours per year.

| Pollutant | Emission Factors (lb/MMSCF) | Emission Rates (lb/hr) | Emissions (tons per year) |
| --- | --- | --- | --- |
| PM10 | 7.6 lb/MMSCF | 0.078 | 0.34 |
| CO | 84.0 lb/MMSCF | 0.867 | 3.80 |
| SO2 | 0.60 lb/MMSCF | 0.006 | 0.03 |
| NOx | 100.0 lb/MMSCF | 1.032 | 4.52 |
| VOC (nonmethane) | 5.5 lb/MMSCF | 0.057 | 0.25 |

- EU 025 	Tank emissions (VOCs and HAPs) are calculated using Trinity Consultants Tank ESP software.  For Fixed Roof Tanks, HAP emissions calculated as species vapor weight fraction times working and standing (breathing) losses [AP-42 Section 7.1.4, equation 4-1]. For Floating Roof Tanks, Tank HAPs calculated as species liquid weight fraction times working losses plus vapor weight fraction times standing (breathing) losses [AP-42 Section 7.1.4, equation 4-2].

- EU 026	Tank emissions (VOCs and HAPs) are calculated using Trinity Consultants Tank ESP software.  For Fixed Roof Tanks, HAP emissions calculated as species vapor weight fraction times working and standing (breathing) losses [AP-42 Section 7.1.4, equation 4-1]. For Floating Roof Tanks, Tank HAPs calculated as species liquid weight fraction times working losses plus vapor weight fraction times standing (breathing) losses [AP-42 Section 7.1.4, equation 4-2].

- EU 006	Gasoline: Multiply throughput (i.e. 315,000,000 gal/yr. of gasoline) by emission factor (0.29 lb/1000 gal or 35 mg/l) to calculate potential VOC emissions. Gasoline throughput based on proposed permit limitation and gasoline loading rack emission factor based on proposed limitations.

Distillate: Multiply throughput (i.e. 100,800,000 gal/yr. of distillate for loading rack) by emission factor (0.0155 lb/1000 gal or 1.853 mg/l) to calculate potential VOC emissions. Distillate throughput based on proposed permit limitation and distillate loading emission factors based on AP-42, Section 5.2.

Loading Rack HAPs calculated as species vapor weight fraction times VOC emissions.

Cargo Leaks represent collection efficiency of the vapor control system. A collection efficiency of 98.7% is assumed for cargo tanks passing the annual NSPS-level testing (AP-42 Chapter 5.2). Tank trucks are assumed to be in vapor balance service (Stage I Vapor Recovery) with an uncontrolled emissions of 980 mg/L gasoline loaded (AP-42 Table 5.2-5).  Cargo leaks are then 12.74 mg/L.

Cargo Leaks HAPs calculated as species vapor weight fraction times loading rack gasoline VOC emissions.

Regarding calculating fugitive emissions, for each component type (i.e. valves – light liquid), multiply the number of components for a particular component type at the facility times the appropriate leak factor (i.e. 9.48E-05 lb/hr/component) times the number of hours (8,760) to calculate potential annual VOC emissions for that particular component type. Add all of the potential VOC emissions together for all component types to calculate the facility fugitive emissions. Leak factors are based on “Fugitive Emissions from Equipment Leaks II: Calculation Procedures for Petroleum Industry Facilities API Publication No. 343, May 1998”.  Fugitive HAPs calculated as species liquid weigh fraction times gasoline VOC emissions.

- EU 019 	Distillate: Multiply throughput (i.e. 500,000,000 gal/yr. for barge loading) by emission factor (0.0155 lb/1000 gal or 1.853 mg/l) to calculate potential VOC emissions. Distillate throughput based on proposed permit limitation and distillate loading emission factors based on AP-42, Section 5.2.

Loading Rack HAPs calculated as species vapor weight fraction times VOC emissions.

Conclusion

This project renews and revises Title V air operation permit No. 0090029-013-AV, which was effective on March 6, 2014. This Title V air operation permit renewal and revision is issued under the provisions of Chapter 403, Florida Statues (F.S.), and Chapters 62-4, 62-210, and 62-213, F.A.C.