# Miami-Dade Water and Sewer Department

# Alexander Orr Water Treatment Plant

# Facility ID No. 0250314

# Miami-Dade County

# Title V Air Operation Permit Revision/Renewal

# Permit No. 0250314-021-AV

(Renewal/Revision of Title V Air Operation Permit No. 0250314-017-AV)

# Permitting Authority:

State of Florida Department of Environmental Protection

Southeast District Office

3301 Gun Club Road, MSC 7210-1

West Palm Beach, Florida, 33416

# Telephone:  (561) 681-6600

# Email:  sed.air@dep.state.fl.us

# Compliance Authority:

State of Florida Department of Environmental Protection

Southeast District Office

3301 Gun Club Road, MSC 7210-1

West Palm Beach, Florida, 33416

# Telephone:  (561) 681-6600

# Email:  sed.air@dep.state.fl.us

# January XX, 2016

Title V Air Operation Permit Revision/Renewal

Permit No. 0250314-021-AV

Table of Contents

Section	Page Number

Placard Page 	 1

- Facility Information.

- Facility Description. 	 2

- Summary of Emissions Units. 	 2

- Applicable Regulations. 	 2

- Facility-wide Conditions. 	 4

- Emissions Units and Conditions.

- EU007.Lime Kiln 	 7

- EUs 009, 010, 011, 012, 024, and 025. Standby Diesel Generators Nos. 1-5	 9

- EU023 Pump Room Emergency Diesel Generator 	18

- EUs 018, 019, and 020 Natural Gas Pump Engines 	24

- EUs 021, 026, and 028 Existing Small Emergency Diesel Generators	29

- EU027 Emergency Kiln Rotation Engine	34

- EU025 Standby Diesel Generator No. 6	37

- Appendices. 	42

Appendix A, Glossary.

Appendix I, List of Insignificant Emissions Units and/or Activities.

Appendix NSPS, Subpart A – General Provisions.

Appendix NSPS, Subpart IIII – Standards of Performance for Stationary Compression Ignition Internal Combustion Engines

Appendix NESHAP, Subpart A – General Provisions.

Appendix NESHAP, Subpart ZZZZ – National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines

Appendix RR, Facility-wide Reporting Requirements.

Appendix TR, Facility-wide Testing Requirements.

Appendix TV, Title V General Conditions.

Appendix U, List of Unregulated Emissions Units and/or Activities.

Referenced Attachments.

Table H, Permit History.

Permittee:	Permit No. 0250314-021-AV

Miami Dade Water and Sewer Department	Alexander Orr Water Treatment Plant

3071 SW 38 Avenue	Facility ID No. 0250314

Miami, Florida 33146	Title V Air Operation Permit Renewal/Revision

The purpose of this permit is to revise/renew the Title V air operation permit for the above referenced facility.  The existing Alexander Orr Water Treatment Plant is located in Miami-Dade County at 6800 SW 87th Avenue, Miami, Florida 33173.  UTM Coordinates are:  Zone 17, 565.92 km East, 2843.33 km North.  Latitude is:  25 42’ 28” North; and, Longitude is:  80 20’ 11” West.

The Title V air operation permit is issued under the provisions of Chapter 403, Florida Statutes (F.S.), and Florida Administrative Code (F.A.C.) Chapters 62-4, 62-210, and 62-213.  The above named permittee is hereby authorized to operate the facility in accordance with the terms and conditions of this permit.

0250314-021-AV Effective Date:  January XX, 2015

Renewal Application Due Date:  Month XX, 2020

Expiration Date:  January XX, 2021

____________________________    __________

Jason R. Andreotta			     Date

Permitting Program Administrator

Southeast District

JRA/lch/sdt

Subsection A.  Facility Description.

This existing facility consists of a publicly-owned regional water treatment plant that processes up to 241.7 million gallons per day of raw water for public water supply using a lime softening process, which includes softening, recarbonation, disinfection, and filtration.  Electrical power necessary for continuous plant operations is provided by a bank of diesel-driven generators. Engine-driven high service pumps convey water to the consumer via the County wide distribution system and provide redundancy and standby capacity to electric motor-driven units.

A rotary kiln recovers the water softening process solids for conversion back to quick lime for process reuse on site.  An emergency generator at the kiln and an emergency kiln rotation engine provide redundancy to standby generators for critical functions.

Also included in this permit are miscellaneous unregulated/insignificant emissions units and/or activities.

Subsection B.  Summary of Emissions Units.

| Facility ID No. 0250314 |  |
| --- | --- |
| ID No. | Emission Unit Description |  |
| Regulated Emissions Units |  |  |
| 007 | Rotary Lime Recalcining Kiln, designed to produce 150 TPD of calcium Oxide fired by natural gas |  |
| 009 | Standby Diesel Engine Generator # 1, EMD Model 20-645F4B |  |
| 010 | Standby Diesel Engine Generator # 2, EMD Model 20-645F4B |  |
| 011 | Standby Diesel Engine Generator # 3, EMD Model 20-645F4B |  |
| 012 | Standby Diesel Engine Generator # 4, EMD Model 20-645F4B |  |
| 018 | New Pump Engine # 3, Natural Gas Fueled Caterpillar G3512 LE-130 |  |
| 019 | New Pump Engine # 4, Natural Gas Fueled Caterpillar G3512 LE-130 |  |
| 020 | New Pump Engine # 5, 2090 BHP, Natural Gas Fueled Engine |  |
| 021 | Emergency Generator for Lime Kiln, rated at 250 kW |  |
| 023 | Pump Room Emergency Diesel Engine Generator, CAT Model 3508TA-130, 900kW |  |
| 024 | Standby Diesel Engine Generator # 5, EMD Model 20-645F4B |  |
| 025 | Standby Diesel Engine Generator # 6, EMD Model L16-710-G4C-T2 |  |
| 026 | LISTER 18 HP Diesel Engine Driven Starting Air Compressor |  |
| 027 | PERKINS 83 HP Emergency Kiln Rotation Engine |  |
| 028 | HATZ 37 HP Diesel Engine Driven Starting Air Compressor |  |
| Unregulated Emissions Units and Activities (see Appendix U, List of Unregulated Emissions Units and/or Activities) |  |  |
| 022 | Railcar Lime Unloading Rack |  |

Also included in this permit are miscellaneous insignificant emissions units and/or activities (see Appendix I, List of Insignificant Emissions Units and/or Activities).

Subsection C.  Applicable Regulations.

Based on the Title V air operation permit renewal/revision application received June 29, 2015, this facility is not a major source of hazardous air pollutants (HAP).  The existing facility is a prevention of significant deterioration (PSD) major source of air pollutants in accordance with Rule 62-212.400, F.A.C.  A summary of applicable regulations is shown in the following table.

| Regulation | ## EU No(s). |
| --- | --- |
| Federal Rule Citations |  |
| 40 CFR 60, Subpart A, NSPS General Provisions |  |
| 40 CFR 60, Subpart IIII | 025, 027 |
| 40 CFR 63, Subpart A, NSPS General Provisions | 007, 009, 010, 011, 012, 018, 019 020, 021, 023, 025, 026, 027, 028 |
| 40 CFR 63, Subpart ZZZZ | 007, 009, 010, 011, 012, 018, 019 020, 021, 023, 026, 028 |
| State Rule Citations |  |
| 62-4, 62-204, 62-210, 62-213, 62-296 | Facility |

The following conditions apply facility-wide to all emission units and activities:

- Appendices.  The permittee shall comply with all documents identified in Section IV., Appendices, listed in the Table of Contents.  Each document is an enforceable part of this permit unless otherwise indicated.  [Rule 62-213.440, F.A.C.]

Emissions and Controls

- Objectionable Odor Prohibited.  No person shall cause, suffer, allow or permit the discharge of air pollutants, which cause or contribute to an objectionable odor.  An “objectionable odor” means any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance.  [Rule 62-296.320(2) and 62-210.200(Definitions), F.A.C.]

- General Volatile Organic Compounds (VOC) Emissions or Organic Solvents (OS) Emissions.  The permittee shall allow no person to store, pump, handle, process, load, unload or use in any process or installation, volatile organic compounds or organic solvents without applying known and existing vapor emission control devices or systems deemed necessary and ordered by the Department.  [Rule 62-296.320(1), F.A.C.]

{Permitting Note:  Nothing is deemed necessary and ordered at this time.}

- General Visible Emissions.  No person shall cause, let, permit, suffer or allow to be discharged into the atmosphere the emissions of air pollutants from any activity equal to or greater than 20% opacity.  This regulation does not impose a specific testing requirement.  [Rule 62-296.320(4)(b), F.A.C.]

- Unconfined Particulate Matter.  No person shall cause, let, permit, suffer or allow the emissions of unconfined particulate matter from any activity, including vehicular movement; transportation of materials; construction; alteration; demolition or wrecking; or industrially related activities such as loading, unloading, storing or handling; without taking reasonable precautions to prevent such emissions.  Reasonable precautions to prevent emissions of unconfined particulate matter at this facility include:

  - Paving and maintenance of roads, parking areas, and yards.

  - Application of water or chemicals to control emissions from such activities as demolition of buildings, grading roads, construction, and land clearing.

  - Application of asphalt, water, oil, chemicals, or other dust suppressants to unpaved roads, yards, open stock piles, and similar sources.

  - Removal of particulate matter from buildings or work area to prevent particulate from becoming airborne.

  - Landscaping or planting of vegetation

  - Use of hoods, fans, filters, and similar equipment to contain and or vent particulate matter

  - Confining abrasive blasting, where possible

  - Enclosure or covering of conveyor systems

[Rule 62-296.320(4)(c), F.A.C.; and, proposed by applicant in Title V air operation permit renewal application received June 29, 2015.]

Annual Reports and Fees

See Appendix RR, Facility-wide Reporting Requirements for additional details.

- Electronic Annual Operating Report and Title V Annual Emissions Fees.  The information required by the Annual Operating Report for Air Pollutant Emitting Facility [Including Title V Source Emissions Fee Calculation] (DEP Form No. 62-210.900(5)) shall be submitted by April 1 of each year, for the previous calendar year, to the Department of Environmental Protection’s (DEP) Division of Air Resource Management.  Each Title V source shall submit the annual operating report using the DEP’s Electronic Annual Operating Report (EAOR) software, unless the Title V source claims a technical or financial hardship by submitting DEP Form No. 62-210.900(5) to the DEP Division of Air Resource Management instead of using the reporting software.  Emissions shall be computed in accordance with the provisions of subsection 62-210.370(2), F.A.C.  Each Title V source must pay between January 15 and April 1 of each year an annual emissions fee in an amount determined as set forth in subsection 62-213.205(1), F.A.C.  The annual fee shall only apply to those regulated pollutants, except carbon monoxide and greenhouse gases, for which an allowable numeric emission-limiting standard is specified in the source’s most recent construction permit or operation permit.  Upon completing the required EAOR entries, the EAOR Title V Fee Invoice can be printed by the source showing which of the reported emissions are subject to the fee and the total Title V Annual Emissions Fee that is due.  The submission of the annual Title V emissions fee payment is also due (postmarked) by April 1st of each year.  A copy of the system-generated EAOR Title V Annual Emissions Fee Invoice and the indicated total fee shall be submitted to:  Major Air Pollution Source Annual Emissions Fee, Post Office Box 3070, Tallahassee, Florida 32315-3070.  Additional information is available by accessing the Title V Annual Emissions Fee On-line Information Center at the following Internet web site:  http://www.dep.state.fl.us/air/emission/tvfee.htm.  [Rules 62-210.370(3), 62-210.900 & 62-213.205, F.A.C.; and, §403.0872(11), Florida Statutes (2013)]

{Permitting Note:  Resources to help you complete your AOR are available on the electronic AOR (EAOR) website at:  http://www.dep.state.fl.us/air/emission/eaor.  If you have questions or need assistance after reviewing the information posted on the EAOR website, please contact the Department by phone at (850) 717-9000 or email at eaor@dep.state.fl.us.}

{Permitting Note:  The Title V Annual Emissions Fee form (DEP Form No. 62-213.900(1)) has been repealed.  A separate Annual Emissions Fee form is no longer required to be submitted by March 1st each year.}

- Annual Statement of Compliance.  The permittee shall submit an annual statement of compliance to the compliance authority at the address shown on the cover of this permit within 60 days after the end of each calendar year during which the Title V permit was effective.  [Rules 62-213.440(3)(a)2. & 3. and (b), F.A.C.]

- Prevention of Accidental Releases (Section 112(r) of CAA).

  - As required by Section 112(r)(7)(B)(iii) of the CAA and 40 CFR 68, the owner or operator shall submit an updated Risk Management Plan (RMP) to the Chemical Emergency Preparedness and Prevention Office (CEPPO) RMP Reporting Center.  (See paragraph e., below.)

  - As required under Section 252.941(1)(c), F.S., the owner or operator shall report to the appropriate representative of the Division of Emergency Management, as established by department rule, within one working day of discovery of an accidental release of a regulated substance from the stationary source, if the owner or operator is required to report the release to the United States Environmental Protection Agency under Section 112(r)(6) of the CAA.

  - The owner or operator shall submit the required annual registration fee to the Division of Emergency Management on or before April 1, in accordance with Part IV, Chapter 252, F.S., and Rule 27P-21, F.A.C.

  - Any required written reports, notifications, certifications, and data required to be sent to the Division of Emergency Management, should be sent to:  Division of Emergency Management, 2555 Shumard Oak Boulevard, Tallahassee, FL  32399-2100, Telephone:  (850) 413-9970, Fax:  (850) 488-1739.

  - Any Risk Management Plans, original submittals, revisions, or updates to submittals, should be sent electronically through EPA’s Central Data Exchange system at the following address:  https://cdx.epa.gov.  Information on electronically submitting risk management plans using the Central Data Exchange system is available at:  http://www2.epa.gov/rmp.  The RMP Reporting Center can be contacted at:  RMP Reporting Center, Post Office Box 10162, Fairfax, VA  22038, Telephone:  (703) 227-7650.

  - Any required reports to be sent to the National Response Center, should be sent to:  U.S. Environmental Protection Agency, Office of Solid Waste and Emergency Response, 1200 Pennsylvania Ave. NW, Mail Code:  US EPA (5101T), Washington, DC 20460, Telephone:  (800) 424-8802.

  - Send the required annual registration fee using approved forms made payable to:  Cashier, Division of Emergency Management, State Emergency Response Commission, 2555 Shumard Oak Boulevard, Tallahassee, FL  32399-2149

[Part IV, Chapter 252, F.S.; and, Rule 27P-21, F.A.C.]

The specific conditions in this section apply to the following emissions unit:

| EU No. | Brief Description |
| --- | --- |
| 007 | Rotary Lime Recalcining Kiln, designed to produce 150 TPD of Calcium Oxide (CaO) fired by Natural Gas |

# Calcium carbonate from the plant’s water treatment process is fed to the lime kiln where it is converted into lime products and carbon dioxide (CO2). The CO2 is recycled into the recarbonation basins at the water treatment plant where it is used to stabilize the water chemically, after the softening process.  A venture scrubber at the feed end of the kiln is used to recover lime solids that would otherwise be lost to the atmosphere and also serves to reduce particulate matter emissions from the exhaust.  Lime solids are discharged into an integral tube cooler at the firing end of the kiln.

This emission unit is not subject to Compliance Assurance Monitoring (CAM) because the wet scrubber installed at this emission unit meets the definition of inherent process equipment in accordance with the Subpart 40 CFR 64.1.  The primary purpose of this control devise is product recovery.  Furthermore, the efficiency at which the control equipment is operated by design for purposes other than compliance with the applicable emission limits is more than sufficient to assure compliance with the emissions limit specified in Rule 62-296.320(4)(a), F.A.C.

{Permitting note: This emission unit is regulated under Prevention of Significant Deterioration (PSD) and Best Available Control Technology (BACT) Determination dated August 1, 1980}

Essential Potential to Emit (PTE) Parameters

- Methods of Operation - (i.e., Fuels). The only fuel allowed to be burned is natural gas.  [Rule 62-213.410, F.A.C.]

- Hours of Operation.  This emissions unit(s) may operate continuously (8,760 hours/year).  [Rule 62-210.200(PTE), F.A.C.]

Emission Limitations and Standards

Unless otherwise specified, the averaging times for Specific Conditions A.3. - A.4 are based on the specified averaging time of the applicable test method.

- NOX Emissions.  NOx emissions shall not exceed 3.0 lb. /ton product and 18.8 pounds per hour as determined by EPA Method 7 or 7E stack testing.  [BACT Determination dated August 1, 1980]

{Permitting note: The tons of product from the recalcining kiln is indirectly determined by the lime mud feed input (dry) divided by 1.785 (the ratio of the molecular weight of CaCO3 and CaO), assuming that the lime mud feed consists entirely of Calcium Carbonate (CaCO3) and is converted entirely to Calcium Oxide (CaO).

- Particulate Matter (PM): PM emissions shall not exceed 0.85 lb. /ton input (dry) and 9.8 pounds per hour as determined by EPA Method 5 stack testing.  [BACT Determination dated August 1, 1980]

{Permitting note: The recalcining kiln input (dry) is indirectly determined by flow measurement and specific gravity of the lime mud feed}

Test Methods and Procedures

{Permitting Note:  The attached Table 2, Summary of Compliance Requirements, summarizes information for convenience purposes only.  This table does not supersede any of the terms or conditions of this permit.}

- Test Methods.  When required, tests shall be performed in accordance with the following reference methods:

| Method | Description of Method and Comments |
| --- | --- |
| 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| 5B | Method for Determining Particulate Matter Emissions (All PM is assumed to be PM10.) |
| 7E | Determination of Nitrogen Oxide Emissions from Stationary Sources |

The above methods are described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Rule 62-297.401, F.A.C.]

- PM Testing: Compliance with PM shall be demonstrated each calendar year (January 1 – December 31) by using EPA Method 5 as described in 40 CFR 60, Appendix A.  [BACT Determination dated August 1, 1980]

- Nitrogen Oxide (NOx) Emissions Tests: Compliance with the emissions limits for NOx of this permit shall be demonstrated each calendar year (January 1 – December 31) by using EPA Method 7 or 7E, as described in 40 CFR 60, Appendix A (1997 version), adopted by reference in Rule 62-204.800, F.A.C., and adopted in Rule 62-297.401, F.A.C.  [BACT Determination dated August 1, 1980]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- Annual Compliance Tests Required.  During each calendar year (January 1 – December 31), each EU shall be tested to demonstrate compliance with the emissions standards for PM and NOx.  [BACT Determination dated August 1, 1980]

Recordkeeping and Reporting Requirements

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440(1)(b), F.A.C.]

- The owner or operator shall make and keep the following records at the facility:

  - Tons per day of lime produced

  - Fuel Use..

[Rule 62-4.070(3), F.A.C.]

- All records shall be prepared no later than fifteen calendar days after the end of each month.  [Rule 62-4.070(3), F.A.C.]

The specific conditions in this section apply to the following emissions units:

| EU No. | Brief Description |
| --- | --- |
| 009 | Standby Diesel Engine Generator # 1, EMD model No. 20-645F4B |
| 010 | Standby Diesel Engine Generator # 2, EMD model No. 20-645F4B |
| 011 | Standby Diesel Engine Generator # 3, EMD model No. 20-645F4B |
| 012 | Standby Diesel Engine Generator # 4, EMD model No. 20-645F4B |
| 024 | Standby Diesel Engine Generator # 5, EMD model No. 20-645F4B |

These five diesel-driven 2.865 MW generators are part of a bank of six generators that provide standby power for the continuous plant operation.  Specific conditions for the sixth engine (EU025) are provided in Subsection G.

These emissions units are subject to regulation under Rule 62-212.400, F.A.C. Prevention of Significant Deterioration (PSD) and are subject to the requirements of the state rules as indicated in the Tile V operation permit renewal.

Emissions units 009-012, are regulated under Prevention of Significant Deterioration (PSD-FL-249); Rule 62-212.400(6), F.A.C., (dated 2/5/98), and Best Available Control Technology (BACT) Determination, dated May 19, 1998. Emissions Unit 024 is regulated under construction permit 0250314-009-AC.

These emissions units are also subject to 40 CFR 63, Subpart ZZZZ.  In 2015, oxidation catalysts with Continuous Parameter Monitoring Systems (CPMS) for temperature were installed on all of the engines.  Subsequent initial performance testing was successfully conducted to confirm that the catalysts met the CO reduction requirements of Subpart ZZZZ on all engines except EU024 pending completion of testing.

| E.U. ID No. | Engine Brake HP | Date of Initial Startup | Primary Fuel | Type of Engine | Displacement liters/cylinder (l/c) | Manufacturer |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Model # |
| 009 | 4,000 | 7-1-1987 | Ultra Low Diesel No. 2 | Non-Emergency* | 10.6 | EMD |
|  |  |  |  |  |  | 20-645F4B |
| 010 | 4,000 | 7-1-1987 | Ultra Low Diesel No. 2 | Non-Emergency* | 10.6 | EMD |
|  |  |  |  |  |  | 20-645F4B |
| 011 | 4,000 | 7-1-1987 | Ultra Low Diesel No. 2 | Non-Emergency* | 10.6 | EMD |
|  |  |  |  |  |  | 20-645F4B |
| 012 | 4,000 | 7-1-1987 | Ultra Low Diesel No. 2 | Non-Emergency* | 10.6 | EMD |
|  |  |  |  |  |  | 20-645F4B |
| 024 | 4,000 | 8-14-2007 | Ultra Low Diesel No. 2 | Non-Emergency* | 10.6 | EMD |
|  |  |  |  |  |  | 20-645F4B |

*Load Sharing Contract with Electric Utility precludes generators from qualifying as an emergency engine per 40 CFR63 Subpart ZZZZ.

Essential Potential to Emit (PTE) Parameters

- Permitted Capacity.  The maximum heat input rate for each unit is 27 MMBtu per hour (approximately 197 gallons per hour).

{Permitting Note: The maximum heat input rate is based on a higher heating value of 19,640 Btu/lb. and density of 7.034 pounds per gallon of diesel}

[Rule 62-210.200(PTE), F.A.C., and Permit 0250314-009-AC]

- Emissions Unit Operating Rate Limitation After Testing.  See the related testing provisions in Appendix TR, Facility-wide Testing Requirements.  [Rule 62-297.310(3), F.A.C.]

- Methods of Operation.

  - Fuels.

      - Sulfur Content.  The sulfur content shall not exceed 15 ppm (0.0015% by weight) for non-road diesel fuel.

      - Cetane and Aromatic.  The fuel must have a minimum cetane index of 40 or must have a maximum aromatic content of 35 volume percent.

[40 CFR 60.4207(b), and 80.510(b)]

  - Fuel limitation.  Consumption of all six generator emission units (EUs 009, 010, 011, 012, 024, and 025) combined shall not exceed 1,200,000 gallons of diesel fuel in any consecutive 12-month period. [Permit No. 0250314-014-AC]

  - Hours of Operation.  The hours of operation of all six generator emission units (EUs 009, 010, 011, 012, 024, and 025) are only restricted by the fuel consumption limit given in Condition B.2.b. [Rule 62-210.200(PTE), F.A.C.; and, Permit No. 0250314-014-AC]

{Permitting Note:  Based on a total fuel consumption and fuel flow rate of approximately 197 gallons per hour, it equates to 6091 hours per year for all six units combined.}

[Rule 62-213.410, F.A.C.; Applicant’s request in Title V permit renewal application received June 29, 2015; Permit No. 0250314-009-AC and, 0250314-014-AC.]

Emission Limitations and Standards

{Permitting Note:  The attached Table 1, Summary of Air Pollutant Standards, summarizes information for convenience purposes only.  This table does not supersede any of the terms or conditions of this permit.}

Unless otherwise specified, the averaging times for Specific Conditions B.4 through B.6 are based on the specified averaging time of the applicable test method if not otherwise specified by rule.

- Visible Emissions.  Visible emissions shall not exceed 20 percent opacity as measured using EPA Method 9 per Facility-Wide Condition FW4.  Compliance with the visible emissions shall be demonstrated each calendar year (January 1 – December 31).  [Rule 62-296.320(4)(b), F.A.C.]

- NOX Emissions.  Nitrogen oxide (NOX) emissions shall not exceed 3.40 lb/MMBtu as determined by the average of three 1-hour compliance test runs conducted in accordance with EPA Method 7 or 7E.  [Rule 62-212.400, F.A.C. and BACT Determination for PSD-FL-249 in Permit No. 0250314-014-AC]

- CO Emissions.  The owner or operator must reduce carbon monoxide (CO) emissions by 70 percent or more; or limit concentration of CO in the stationary RICE exhaust to 23 parts per million by volume, dry (ppmvd) or less at 15 percent O2. [40 CFR 63.6600(d) Table 2c]

Excess Emissions

- Excess Emissions Allowed.  Excess emissions resulting from startup, shutdown or malfunction of any emissions unit shall be permitted provided that best operational practices to minimize emissions are adhered to and the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C.]

Monitoring of Operations

- Fuel Sulfur Content Tests: For each load of fuel delivered to the facility, the permittee shall either:

  - Obtain a copy of the fuel analysis from the supplier.  Methods for determining the fuel sulfur content of the distillate oil shall be ASTM Method D 129-91, ASTM D 2622-94, ASTM D 4294-98 or comparable Department approved method.  Records shall specify the test method used.

  - Collect a fuel sample to be sent for laboratory analysis based on one of the following methods: ASTM Method D 129-91, ASTM D 2622-94, ASTM D 4294-98 or comparable Department approved method.

  - Records from the fuel supplier that indicates the fuel delivered is Ultra Low Sulfur No. 2 Diesel fuel oil by ASTM Method 975-98b, or current version.  Specification for Diesel Fuel Oils provides for this classification of diesel fuel oils as having no more than 0.0015 percent sulfur content by weight.

[Rules 62-4.070(3), 62-297.440, F.A.C. and PSD-FL-249, and Permit 0250314-009-AC]

- Fuel Consumption: The owner or operator shall monitor fuel consumption by metering the fuel between the storage tank and the bank of generators on a daily basis.  [Rule 62-4.070(3), F.A.C.]

- Monitors:  The owner or operator shall install, calibrate, operate and maintain monitoring devices to monitor and record the fuel flow and hours of operation.  [Rule 62-4.070(3), F.A.C., and Permit 0250314-009-AC]

- Fuel Meter Calibration:  Calibration of the fuel meter shall be conducted in accordance with manufacturer’s schedule and recommendation.  [Rule 62-4.070(3), F.A.C.]

- Operating Procedures:  These emission units shall be properly operated and maintained at all times in a condition to minimize emissions of air pollutants.  The owner and operator shall ensure that all facility staff responsible for these emissions units is trained in their operation and maintenance in accordance with the guidelines and procedures as established by the equipment manufacturers.  [Rule 62-4.070(3), F.A.C. and PSD-FL-249]

- Operation and Maintenance of Equipment.  At all times the owner or operator must operate and maintain, any affected source, including associated air pollution control equipment and monitoring equipment, in a manner consistent with safety and good air pollution control practices for minimizing emissions.  Determination of whether such operation and maintenance procedures are being used will be based on information available to the compliance authority which may include, but is not limited to, monitoring results, review of operation and maintenance procedures, review of operation and maintenance records, and inspection of the source.  [40 CFR 63.6605(b)]

Continuous Compliance

- At all times, this unit:

  - Must be in compliance with the operating limitations in this section.

  - Must be operated and maintained in a manner consistent with safety and good air pollution control practices for minimizing emissions.  The general duty to minimize emissions does not require you to make any further efforts to reduce emissions if levels required by this standard have been achieved.  Determination of whether such operation and maintenance procedures are being used will be based on information available to the Administrator which may include, but is not limited to, monitoring results, review of operation and maintenance procedures, review of operation and maintenance records, and inspection of the source.

[40 CFR 63.6605]

- Monitoring and Data.  If the owner or operator must comply with emission and operating limitations, they must monitor and collect data according to this section.

  - Except for monitor malfunctions, associated repairs, and required quality assurance or control activities (including, as applicable, calibration checks and required zero and span adjustments), they must monitor continuously at all times that the stationary RICE is operating.

  - The owner or operator may not use data recorded during monitoring malfunctions, associated repairs, and required quality assurance or control activities in data averages and calculations used to report emission or operating levels.  They must, however, use all the valid data collected during all other periods.

[40 CFR 63.6635(a)]

- The owner or operator must demonstrate continuous compliance by:

  - Conducting performance tests every 8,760 hours or 3 years, whichever comes first, for CO to demonstrate that the required CO percent reduction is achieved or that emissions remain at or below the CO concentration limit; and,

  - Collecting the approved operating parameter (if any) data according to 40 CFR 63.6625(b); and

  - Reducing these data to 4-hour rolling averages; and,

  - Maintaining the 4-hour rolling averages within the operating limitations for the operating parameters established during the performance test.

  - Measuring the pressure drop across the catalyst once per month and demonstrating that the pressure drop across the catalyst is within the operating limitation established during the performance test.

[40 CFR 63.6640(a) Table 6 10.i.-v.]

- CEMS.  If the owner or operator elects to install a CEMS as specified in Table 5 of 40 CFR 63, Subpart ZZZZ, they must install, operate, and maintain a CEMS to monitor CO and either oxygen or carbon dioxide (CO2) at both the inlet and the outlet of the control device according to the requirements in 40 CFR 63.6625(a)(1) through (4).  [40 CFR 63.6625(a).]

- Oxidation Catalyst and CPMS.  Facility shall install oxidation catalysts on the generators with Continuous Parameter Monitoring Systems (CPMS) to monitor the catalyst inlet temperatures.  The oxidation catalysts shall be capable of reducing the exhaust CO concentration to 23 ppmvd at 15 percent O2, or by 70 percent or more If the catalyst is changed, permittee must reestablish the values of the operating parameters measured during the initial performance test.  When re-establishing the values of the operating parameters, the permittee must also conduct a performance test to demonstrate that the emissions unit is meeting the required emission limitation applicable to the stationary RICE.  [Rule 40 CFR 63.6630, 40 CFR 63.6640]

{Note:  Facility has installed Oxidation Catalysts and CPMS units on all of these Emission Units, and has successfully completed initial performance tests on all Emission Units except EU024 which is pending}

- Oxidation Catalyst Operation.  Facility shall:

  - maintain the oxidation catalyst so that the pressure drop across the catalyst does not change by more than 2 inches of water from the pressure drop the catalyst that was measured during the initial performance; and

  - maintain the temperature of the exhaust so that the catalyst inlet temperature is greater than or equal to 450 degrees Fahrenheit and less than or equal to 1350 degrees Fahrenheit.

- CPMS Temperature Measurement Device.  Permittee must operate, and maintain each CPMS according to the requirements in paragraphs (a) through (f) of this section.

  - You must prepare a site-specific monitoring plan that addresses the monitoring system design, data collection, and the quality assurance and quality control elements outlined in paragraphs (i) through (v) of this section and in 40 CFR 63.8(d).  As specified in 40 CFR 63.8(f)(4), you may request approval of monitoring system quality assurance and quality control procedures alternative to those specified in paragraphs (a) through (e) of this section in your site-specific monitoring plan.

(i) 	The performance criteria and design specifications for the monitoring system equipment, including the sample interface, detector signal analyzer, and data acquisition and calculations;

(ii)	Sampling interface ( e.g., thermocouple) location such that the monitoring system will provide representative measurements;

(iii)	Equipment performance evaluations, system accuracy audits, or other audit procedures;

(iv)	Ongoing operation and maintenance procedures in accordance with provisions in 40 CFR 63.8(c)(1)(ii) and (c)(3); and

(v) 	Ongoing reporting and recordkeeping procedures in accordance with provisions in 40 CFR 63.10(c), (e)(1), and (e)(2)(i).

  - You must install, operate, and maintain each CPMS in continuous operation according to the procedures in your site-specific monitoring plan.

  - The CPMS must collect data at least once every 15 minutes (see also 40 CFR 63.6635).

  - For a CPMS for measuring temperature range, the temperature sensor must have a minimum tolerance of 2.8 degrees Celsius (5 degrees Fahrenheit) or 1 percent of the measurement range, whichever is larger.

  - You must conduct the CPMS equipment performance evaluation, system accuracy audits, or other audit procedures specified in your site-specific monitoring plan at least annually.

  - You must conduct a performance evaluation of each CPMS in accordance with your site-specific monitoring plan.

[40 CFR 63.6625(b)]

- Crankcase Ventilation System.  If the emissions units are not equipped with a closed crankcase ventilation system, the permittee must comply with either (a) or (b) of this section:

  - Install a closed crankcase ventilation system that prevents crankcase emissions from being emitted to the atmosphere.  [40 CFR 63.6625(g)(1)]

  - Install an open crankcase filtration emission control system that reduces emissions from the crankcase by filtering the exhaust stream to remove oil mist, particulates, and metals.  [40 CFR 63.6625(g)(2)]

Owners and operators must follow the manufacturer's specified maintenance requirements for operating and maintaining the open or closed crankcase ventilation systems and replacing the crankcase filters, or can request the Administrator to approve different maintenance requirements that are as protective as manufacturer requirements.  [40 CFR 63.6625(g)]

Test Methods and Procedures

- Test Methods.  When required, tests shall be performed in accordance with the following reference methods:

| Method | Description of Method and Comments |
| --- | --- |
| 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| 7 | Determination of Nitrogen Oxide Emissions from Stationary Sources |
| 7E | Determination of Nitrogen Oxide Emissions from Stationary Sources (Instrumental Analyzer Procedure) |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |
| 10 | Determination of Carbon Monoxide Emissions from Stationary Sources {Note: The method shall be based on a continuous sampling train.} |

The above methods are described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Rule 62-297.401, F.A.C.]

- Annual Compliance Tests Required:

  - Visible Emissions:  Compliance with the visible emissions limits of this permit shall be demonstrated each calendar year (January 1 – December 31) by an annual compliance test using EPA Method 9.  [Rule 62-296.320(4)(b), F.A.C.]

  - NOx Emissions:  Compliance with the emissions limits for NOx of this permit shall be demonstrated each calendar year (January 1 – December 31) by an annual compliance test using EPA Method 7 or 7E.  Sampling of the exhaust gas shall be via a rake probe placed into the engine exhaust outlet.  Annual compliance testing while firing diesel fuel oil is unnecessary for units operating on diesel fuel oil for less than 400 hours in the current calendar year.  [Rules 62-4.070(3), 62-204.800, 62-297.310]

  - CO Emissions:  Compliance with the emissions limits for CO of this permit shall be demonstrated every 8,760 hours or 3 years, whichever comes first according to the test procedures specified in 40 CFR 63.6620 and 40 CFR 63 Subpart ZZZZ Table 4.3.a.i-iii.  [40 CFR 63.6615, 40 CFR 63.6620, and 40 CFR 63 Subpart ZZZZ Table 3 and Table 4]

- NOx Emissions Cap:  To demonstrate compliance with the projected actual NOx emissions cap of 282 tons per year for Units 1-6, the permittee shall do the following:

- The permittee shall monitor NOx emissions; and, using the most reliable information available, calculate and maintain a record of the annual emissions, in tons per year on a calendar year basis, for a period of 5 years following resumption of regular operations.  Emissions shall be computed in accordance with Rule 62-210.370, F.A.C.

- The permittee shall report to the Department within 60 days after the end of each year during which records must be generated under subparagraph 62-212.300(1)(e)1., F.A.C., setting out the units annual emissions during the calendar year that preceded submission of the report.  The report shall contain the following:

- The name, address and telephone number of the owner or operator of the major stationary source;

- The annual emissions as calculated pursuant to subparagraph 62-212.300(1)(e)1., F.A.C.;

- If the emissions differ from the preconstruction projection, an explanation as to why there is a difference; and

- Any other information that the owner or operator wishes to include in the report.

- The information required to be documented and maintained pursuant to subparagraphs 62-212.300(1)(e)1. and 2., F.A.C., shall be submitted to the Department, which shall make it available for review to the general public.

[Rule 62-212.300 F.A.C. and Permit No. 0250314-014-AC]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

Recordkeeping and Reporting Requirements

- Diesel Fuel Consumption Records: The permittee shall record and maintain fuel usage records for the bank of generators, including operation for repairs or maintenance, on a daily basis.  The diesel fuel usage records for the generators shall be based on daily fuel meter readings.  Within ten days of the end of each month, the owner or operator shall make records of monthly diesel fuel consumption from the daily records, and shall make records of consecutive 12 month diesel fuel consumption to demonstrate compliance with the fuel consumption limit of specific condition B.2 of this permit.  [Rule 62-4.070(3), F.A.C. and PSD-FL-249, and Permit 0250314-009-AC]

- Fuel Sulfur Content Records. The owner or operator shall maintain records of sulfur content of each delivery of diesel fuel received for these emissions units. [Rule 62-4.070(3), F.A.C. and PSD-FL-249]

- Notification, Performance and Compliance Records.

- The owner or operator must keep a copy of each notification and report that the owner or operator submitted to comply with this section, including all documentation supporting any Initial Notification or Notification of Compliance Status that the owner or operator submitted.

- The owner or operator must keep the records required in 40 CFR 63.6625(e) of this section to show continuous compliance with each emission limitation or operating requirement.

- The owner or operator must keep records of the hours of operation of the engine that is recorded through the non-resettable hour meter.  The owner or operator must document how many hours are spent for emergency operation including what classified the operation as emergency and how many hours are spent for non-emergency operation.  If the engines are used for demand response operation, the owner or operator must keep records of the notification of the emergency situation, and the time the engine was operated as part of demand response.

[40 CFR 63.6655]

- Malfunction Records.

- The owner or operator must keep records of the occurrence and duration of each malfunction of operation (i.e. process equipment) or the air pollution control and monitoring equipment.

- The owner or operator must keep records of actions taken during periods of malfunction to minimize emissions in accordance with 40 CFR 63.6605(b) of this section including corrective actions to restore malfunctioning process and air pollution control and monitoring equipment to its normal or usual manner of operation.

[40 CFR 63.6655]

- Maintenance Records.

- The owner or operator must keep records of all required maintenance performed on the air pollution control and monitoring equipment.

- The owner or operator must keep records of the maintenance conducted on the stationary RICE in order to demonstrate that the stationary RICE and after-treatment control device (if any) are operated and maintained according to its own maintenance plan.

[Rule 62-4.070(3), F.A.C. and PSD-FL-249, 40 CFR 63.6655, and Permit 0250314-009-AC]

- Record Retention.

- The owner or operator must keep records in a suitable and readily available form for expeditious reviews.

- The owner or operator must keep each record readily accessible in hard copy or electronic form for at least 5 years after the date of each occurrence, measurement, maintenance, corrective action, report, or record.

[40 CFR 63.6660 and 40 CFR 63.10(b)(1)]

- Annual Operating Report (AOR).

- The permittee shall submit to the Compliance Authority, each calendar year, on or before April 1st, a completed DEP Form No. 62-210.900(5), “Annual Operating Report for Air Pollutant Emitting Facility”, for the preceding calendar year.

- Emissions shall be computed in accordance with the provisions of Rule 62-210.370(2), F.A.C.

[Rules 62-210.370(2) & (3) and 62-213.440(3)(a)2., F.A.C.; and, Permit No. 0250314-AC, Specific Condition 19]

- AOR Supplemental Information: Annual operating reports shall include the following supplemental information that was recorded in the previous calendar year:

  - The highest consecutive 12 months total diesel fuel usage for the standby generators

  - Records of the fuel meter calibration

  - A statement by the permittee that the fuel sulfur limitation was or was not exceeded during the previous calendar year

  - A statement by the permittee whether or not the records of fuel supplier certifications maintained by the permittee represent all fuel oil burned during the previous calendar year.

[Rule 62-4.070(3), F.A.C.]

- Notification Requirements.  The owner or operator must submit all of the notifications in 40 CFR 63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), 63.9(b) through (e), and (g) and (h) that apply to you by the dates specified.  [40 CFR 63.6645(a)]

- Notification of Intent to Conduct a Performance Test.  The owner or operator is required to conduct a performance test, they must submit a Notification of Intent to conduct a performance test at least 60 days before the performance test is scheduled to begin as required in 40 CFR 63.7(b)(1).  [40 CFR 63.6645(g)]

- Notification of Compliance Status.  The owner or operator is required to conduct a performance test as specified in Tables 4 and 5 of 40 CFR 63, Subpart ZZZZ, they must submit a Notification of Compliance Status according to 40 CFR 63.9(h)(2)(ii).

  - For each compliance demonstration required in Table 5 of 40 CFR 63, Subpart ZZZZ that does not include a performance test, the owner or operator must submit the Notification of Compliance Status before the close of business on the 30th day following the completion of the initial compliance demonstration.

  - For each compliance demonstration required in Table 5 of 40 CFR 63, Subpart ZZZZ that includes a performance test conducted according to the requirements in Table 3 of 40 CFR 63, Subpart ZZZZ, the owner or operator must submit the Notification of Compliance Status, including the performance test results, before the close of business on the 60th day following the completion of the performance test according to 40 CFR 63.10(d)(2).

[40 CFR 63.6645(h)]

- Semiannual Compliance Report.  The owner or operator must submit a Semiannual Compliance Report. The Report must contain:

  - If there are no deviations from any emission limitations or operating limitations that apply to the owner or operator, a statement that there were no deviations from the emission limitations or operating limitations during the reporting period.  If there were no periods during which the CMS, including CEMS and CPMS, was out-of-control, as specified in 40 CFR 63.8(c)(7), a statement that there were not periods during which the CMS was out-of-control during the reporting period; or

  - If the owner or operator had a deviation from any emission limitation or operating limitation during the reporting period, the information in 40 CFR 63.6650(d).  If there were periods during which the CMS, including CEMS and CPMS, was out-of-control, as specified in 40 CFR 63.8(c)(7), the information in 40 CFR 63.6650(e); or

  - If the owner or operator had a malfunction during the reporting period, the information in 40 CFR 63.6650(c)(4).  The owner or operator must submit the report semiannually according to the requirements in 40 CFR 63.6650(b).

[40 CFR 63.6650 (except 63.6650(g)) Table 7]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440, F.A.C.]

Other Requirements

- 40 CFR 63 Requirements - Subpart A.  These emissions units shall comply with all applicable requirements of 40 CFR 63, Subpart A, General Provisions, which have been adopted by reference in Rule 62-204.800(11)(d)1., F.A.C., except that the Secretary is not the Administrator for purposes of 40 CFR 63.5(e), 40 CFR 63.5(f), 40 CFR 63.6(g), 40 CFR 63.6(h)(9), 40 CFR 63.6(j), 40 CFR 63.13, and 40 CFR 63.14.  The applicable 40 CFR 63, Subpart A, General Provisions to which these emissions are subject to are found at 40 CFR 63.6665 and are included in Appendix 40 CFR 63 Subpart A.  [Rule 62-204.800(11)(d)1., F.A.C.]

| General Provisions Citation | Subject of Citation |
| --- | --- |
| §63.1 | General applicability of the General Provisions |
| §63.2 | Definitions |
| §63.3 | Units and abbreviations |
| §63.4 | Prohibited activities and circumvention |
| §63.5 | Construction and reconstruction |
| §63.6(a) | Applicability |
| §63.9(i) | Adjustment of submittal deadlines |
| §63.9(j) | Change in previous information |
| §63.10(a) | Administrative provisions for recordkeeping/reporting |
| §63.10(b)(1) | Record retention |
| §63.10(b)(2)(vi)–(xi) | Records |
| §63.10(b)(2)(xii) | Record when under waiver |
| §63.10(b)(2)(xiv) | Records of supporting documentation |
| §63.10(b)(3) | Records of applicability determination |
| §63.10(d)(1) | General reporting requirements |
| §63.10(d)(4) | Progress Reports |
| §63.10(f) | Waiver for recordkeeping/reporting |
| §63.12 | State authority and delegations |
| §63.13 | Addresses |
| §63.14 | Incorporation by reference |
| §63.15 | Availability of information |

- 40 CFR 63 Requirements - Subpart ZZZZ [Generally Applicable Requirements].  These emissions units shall comply with all applicable requirements of 40 CFR 63, Subpart ZZZZ, National Emission Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines (RICE), which have been adopted by reference in Rule 62-204.800(11)(b), F.A.C.  These emissions units shall comply with Appendix 40 CFR 63 Subpart ZZZZ “Generally Applicable Requirements,” included with this permit, which includes applicable requirements that apply in general to all engines regulated under 40 CFR 63 Subpart ZZZZ.  This appendix also contains useful information like provisions that are not delegated to state or local agencies (see 40 CFR 63.6670) and contains definitions (see 40 CFR 63.6675) that are specific to engines regulated under 40 CFR 63 Subpart ZZZZ.  [Rule 62-204.800(11)(b), F.A.C.]

The specific conditions in this section apply to the following emissions unit:

| EU No. | Brief Description |
| --- | --- |
| 023 | Pump Room Emergency Diesel Engine Generator, Caterpillar Model 3508 TA-130, 900 kW |

{This emissions unit is subject to the Reasonable Available Control Technology (RACT) requirements of Rule 62-296.570(4)(b)7, F.A.C. which limits the emissions of NOx to 4.75 lb/MMBtu from this diesel fired generator.  The unit supplies emergency electrical power for the operation of the plant’s north pump room in the event of a power loss.  The engine is limited to running 500 hours per 12-month period.}

| E.U. ID No. | Engine Brake HP | Date of Initial Startup | Primary Fuel | Type of Engine | Displacement liters/cylinder (l/c) | Manufacturer |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Model # |
| 023 | 1,332 max | 6-11-2007 | Ultra Low Diesel No. 2 | Emergency | 4.32 | CAT |
|  |  |  |  |  |  | 3508 TA-130 |

{The diesel engine is also subject to the provisions of 40 CFR 63 Subpart ZZZZ as an existing emergency Compression Ignition (CI) engine greater than 500 hp, operating at an area source.}

Essential Potential to Emit (PTE) Parameters

- Permitted Capacity.  The maximum heat input rate for this unit is 9.18 MMBtu per hour (approximately 66.5 gallons per hour).

{Permitting note: At 100% engine load a Model 3508 engine fuel consumption is 66.5 gallons per hour, based on a 35-degree API diesel fuel with a higher heating value of 18,390 Btu/lb.  On this basis, the fuel consumption for 500 hours of operation at 100 percent engine load is approximately 33,250 gallons.}

[Rule 62-210.200(PTE), F.A.C., and Permit 0250314-005-AC, Application 0250314-021-AV]

- Emissions Unit Operating Rate Limitation After Testing.  See the related testing provisions in Appendix TR, Facility-wide Testing Requirements.  [Rule 62-297.310(3), F.A.C.]

- Methods of Operation.

  - Fuels.  Sulfur Content.  The sulfur content shall not exceed 500 ppm (0.05% by weight) for non-road diesel fuel. [Rule 62-210,200, F.A.C., and Permit 0250314-005-AC]

  - Operational Restrictions.  This emissions unit shall be properly operated and maintained at all times in a condition to minimize emissions of air pollutants.  The owner and operator shall ensure that all facility staff responsible for this emissions unit is trained in the operation and maintenance in accordance with the guidelines and procedures as established by the equipment manufacturer(s).  [Rule 62-4.070(3), F.A.C. and PSD-FL-249, Permits 0250314-005-AC & 0250314-007-AC]

- Hours of Operation:

- The hours of operation for this emission unit shall not exceed 500 hours in any consecutive 12-month period.  [Rule 62-210.200, F.A.C., Definitions-Potential to emit (PTE), 0250314-005-AC, & 0250314-007-AC]]

- Emergency Situations.  There is no time limit on the use of emergency stationary RICE in emergency situations except per Specific Condition C.4.a. above.  [40 CFR 63.6640(f)(1)]

- Maintenance and Testing.  The emissions unit is authorized to operate for the purpose of maintenance checks and readiness testing, provided that the tests are recommended by federal, state or local government, the manufacturer, the vendor, or the insurance company associated with the engine. Maintenance checks and readiness testing of such units is limited to 100 hours per year. [40 CFR 63.6640(f)(2)]

- Non-emergency Situations.  Each RICE is authorized to operate up to 50 hours per year in non-emergency situations, but those 50 hours are counted towards the 100 hours per year provided for maintenance and testing.  [40 CFR 63.6640(f)(4)]

- Engine Startup.  During periods of startup the owner or operator must minimize the engine's time spent at idle and minimize the engine's startup time to a period needed for the appropriate and safe loading of the engine, not to exceed 30 minutes, after which time the non-startup emission limitations apply.  [40 CFR 63.6625(h)]

Emission Limitations and Standards

Unless otherwise specified, the averaging times for Specific Conditions C.5 and C.6 are based on the specified averaging time of the applicable test method if not otherwise specified by rule.

- Visible Emissions.  Visible emissions shall not exceed 20 percent opacity as measured using EPA Method 9 per Facility-Wide Condition FW4.  [Rules 62-296.320(4)b, F.A.C., 0250314-005-AC, & 0250314-007-AC]

- NOX Emissions.  Emissions of NOx shall not exceed 4.75 lb/MMBtu.  [Rule 62-296.570(4)(b)7, F.A.C., 0250314-005-AC]

- Work or Management Practice Standards.

- Oil.  Change oil and filter every 500 hours of operation or annually, whichever comes first.  [40 CFR 63 Table 2d(4)(a)]

- Air Cleaner.  Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first.  [40 CFR 63 Table 2d(4)(b)]

- Hoses and Belts.  Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary.  [40 CFR 63 Table 2d(4)(c)]

- Operation and Maintenance.  Operate and maintain the stationary RICE according to the manufacturer's emission-related operation and maintenance instructions or develop and follow your own maintenance plan which must provide, to the extent practicable for the maintenance and operation of the engine in a manner consistent with good air pollution, control practice for minimizing emissions.  [40 CFR 63.6625(e)]

- Oil Analysis.  The owner or operator has the option of using oil analysis to extend the change requirement.  The oil analysis must be performed at the same frequency specified for changing the oil.  The analysis program must at a minimum analyze the following three parameters: Total Base Number, viscosity, and percent of water content.  The condemning limits for these parameters are as follows: Total Base Number is less than 30 percent of the Total Base Number of the oil when new; viscosity of the oil has changed by more than 20 percent from the viscosity of the oil when new; or percent of water content (by volume) is greater than 0.5.  If all of these condemning limits are not exceeded, the engine owner or operator is not required to change the oil.  If any of the limits are exceeded, the engine owner or operator must change the oil within 2 days of receiving the results of the analysis; if the engine is not in operation when the results of the analysis are received, the engine owner or operator must change the oil within 2 days or before commencing operation, whichever is later.  The owner or operator must keep records of the parameters that are analyzed as part of the program, the results of the analysis, and the oil changes for the engine. The analysis program must be part of the maintenance plan for the engine.  [40 CFR 63.6625(i)]

Excess Emissions

- Excess Emissions Allowed.  Excess emissions resulting from startup, shutdown or malfunction of any emissions unit shall be permitted provided that best operational practices to minimize emissions are adhered to and the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C. 0250314-005-AC, & 0250314-007-AC]

Monitoring of Operations

- Fuel Sulfur Content Tests: For each load of fuel delivered to the facility, the permittee shall either:

  - Obtain a copy of the fuel analysis from the supplier.  Methods for determining the fuel sulfur content of the distillate oil shall be ASTM Method D 129-91, ASTM D 2622-94, ASTM D 4294-98 or comparable Department approved method.  Records shall specify the test method used.

  - Collect a fuel sample to be sent for laboratory analysis based on one of the following methods: ASTM Method D 129-91, ASTM D 2622-94, ASTM D 4294-98 or comparable Department approved method.

  - Records from the fuel supplier that indicates the fuel delivered is Low Sulfur No. 2 Diesel fuel oil by ASTM Method 975-98b, or current version.  Specification for Diesel Fuel Oils provides for this classification of diesel fuel oils as having no more than 0.05 percent sulfur content by weight.

[Rules 62-4.070(3), 62-297.440, F.A.C. and PSD-FL-249, and Permit 0250314-005-AC]

- Monitors:  The owner or operator shall install, calibrate, operate and maintain monitoring devices to monitor and record the fuel flow and hours of operation.  [Rule 62-4.070(3), F.A.C., and Permit 0250314-005-AC]

- Fuel Meter Calibration:  Calibration of the fuel meter shall be conducted in accordance with manufacturer’s schedule and recommendation.  [Rule 62-4.070(3), F.A.C.]

- Operating Procedures:  These emission units shall be properly operated and maintained at all times in a condition to minimize emissions of air pollutants.  The owner and operator shall ensure that all facility staff responsible for these emissions units is trained in their operation and maintenance in accordance with the guidelines and procedures as established by the equipment manufacturers.  [Rule 62-4.070(3), F.A.C. and PSD-FL-249]

Continuous Compliance

- At all times, this unit:

  - Must be in compliance with the operating limitations in this section.

  - Must be operated and maintained in a manner consistent with safety and good air pollution control practices for minimizing emissions.  The general duty to minimize emissions does not require you to make any further efforts to reduce emissions if levels required by this standard have been achieved.  Determination of whether such operation and maintenance procedures are being used will be based on information available to the Administrator which may include, but is not limited to, monitoring results, review of operation and maintenance procedures, review of operation and maintenance records, and inspection of the source.

[40 CFR 63.6605]

- Owner or operator must demonstrate continuous compliance with the work or management practice standards listed in Specific Condition C.7 above by operating and maintaining the stationary RICE according to the manufacturer's emission-related operation and maintenance instructions; or by developing and following the facility’s own maintenance plan which must provide to the extent practicable for the maintenance and operation of the engine in a manner consistent with good air pollution control practice for minimizing emissions. [40 CFR 63.6640(a) and Table 6.9(a) of 40 CFR 63 Subpart ZZZZ]

Test Methods and Procedures

- Test Methods.  When required, tests shall be performed in accordance with the following reference methods:

| Method | Description of Method and Comments |
| --- | --- |
| 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| 7 | Determination of Nitrogen Oxide Emissions from Stationary Sources |
| 7E | Determination of Nitrogen Oxide Emissions from Stationary Sources (Instrumental Analyzer Procedure) |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |
| 10 | Determination of Carbon Monoxide Emissions from Stationary Sources {Note: The method shall be based on a continuous sampling train.} |

The above methods are described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Rule 62-297.401, F.A.C.]

- Annual Compliance Tests Required:

  - Visible Emissions:  Compliance with the visible emissions limits of this permit shall be demonstrated each calendar year (January 1 – December 31) by an annual compliance test using EPA Method 9.  [Rule 62-296.320(4)(b), F.A.C. and Permit No. 0250314-005-AC]

  - NOx Emissions:  Compliance with the emissions limits for NOx of this permit shall be demonstrated each calendar year (January 1 – December 31)  by an annual compliance test using EPA Method 7 or 7E.  Sampling of the exhaust gas shall be via a rake probe placed into the engine exhaust outlet.  [Rules 62-4.070(3), 62-204.800, 62-297.310, 62-297.401, F.A.C., and 63.6620(a) and Permit No. 0250314-005-AC]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

Recordkeeping and Reporting Requirements

- Diesel Fuel Consumption Records: The permittee shall record and maintain fuel usage records for the emission unit, including operation for repairs or maintenance, on a daily basis.  The diesel fuel usage records for the generator shall be based on daily fuel meter readings.  Within ten days of the end of each month, the owner or operator shall make records of monthly diesel fuel consumption from the daily records, and shall make records of consecutive 12 month diesel fuel consumption.  [Rule 62-4.070(3), F.A.C.]

- Fuel Sulfur Content Records. The owner or operator shall maintain records of sulfur content of each delivery of diesel fuel received for these emissions units. [Rule 62-4.070(3), F.A.C. and PSD-FL-249]

- Notification, Performance and Compliance Records.

  - The owner or operator must keep a copy of each notification and report that the owner or operator submitted to comply with this section, including all documentation supporting any Initial Notification or Notification of Compliance Status that the owner or operator submitted.

  - The owner or operator must keep records of the hours of operation of the engine that is recorded through the non-resettable hour meter.  The owner or operator must document how many hours are spent for emergency operation including what classified the operation as emergency and how many hours are spent for non-emergency operation.  If the engines are used for demand response operation, the owner or operator must keep records of the notification of the emergency situation.  The hourly operation records for the emissions unit shall be based on daily hour meter readings.  Within ten days of the end of each month, the owner or operator shall make records of monthly operation from the daily records, and shall make records of consecutive 12 month hourly operation.

[40 CFR 63.6655 and Rule 62-4.070(3), F.A.C.]

- The owner or operator must report each instance in which it did not satisfy the work or management practice standards specified in Specific Condition C.7 above. [40 CFR 63.6640(b)]

- Maintenance Records.  The owner or operator must keep records of the maintenance conducted on the stationary RICE in order to demonstrate that the stationary RICE and after-treatment control device (if any) are operated and maintained according to its own maintenance plan.  [Rule 62-4.070(3), F.A.C. and PSD-FL-249, 40 CFR 63.6655, and Permit 0250314-005-AC]

- Record Retention.

  - The owner or operator must keep records in a suitable and readily available form for expeditious reviews.

  - The owner or operator must keep each record readily accessible in hard copy or electronic form for at least 5 years after the date of each occurrence, measurement, maintenance, corrective action, report, or record.

[40 CFR 63.6660 and 40 CFR 63.10(b)(1)]

- AOR Supplemental Information: Annual operating reports shall include the following supplemental information that was recorded in the previous calendar year:

  - The highest consecutive 12 months total diesel fuel usage for the standby generator.

  - Records of the fuel meter calibration

  - A statement by the permittee that the fuel sulfur limitation was or was not exceeded during the previous calendar year

  - A statement by the permittee whether or not the records of fuel supplier certifications maintained by the permittee represent all fuel oil burned during the previous calendar year.

[Rule 62-4.070(3), F.A.C.]

- Notification Requirements.  The owner or operator must submit all of the notifications in 40 CFR 63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), 63.9(b) through (e), and (g) and (h) that apply to you by the dates specified.  [40 CFR 63.6645(a)]

- Notification of Intent to Conduct a Performance Test.  The owner or operator is required to conduct a performance test, they must submit a Notification of Intent to conduct a performance test at least 60 days before the performance test is scheduled to begin as required in 40 CFR 63.7(b)(1).  [40 CFR 63.6645(g)]

- Semiannual Compliance Report.  The owner or operator must include in its Semiannual Compliance Report:

  - If there are no deviations from any emission limitations or operating limitations that apply to the owner or operator, a statement that there were no deviations from the emission limitations or operating limitations during the reporting period; or

  - If the owner or operator had a deviation from any emission limitation or operating limitation during the reporting period, the information in 40 CFR 63.6650(f).

[40 CFR 63.6640, and 40 CFR 63.6650]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440, F.A.C.]

Other Requirements

- 40 CFR 63 Requirements - Subpart A.  These emissions units shall comply with all applicable requirements of 40 CFR 63, Subpart A, General Provisions, which have been adopted by reference in Rule 62-204.800(11)(d)1., F.A.C., except that the Secretary is not the Administrator for purposes of 40 CFR 63.5(e), 40 CFR 63.5(f), 40 CFR 63.6(g), 40 CFR 63.6(h)(9), 40 CFR 63.6(j), 40 CFR 63.13, and 40 CFR 63.14.  The applicable 40 CFR 63, Subpart A, General Provisions to which these emissions are subject to are found at 40 CFR 63.6665 and are included in Appendix 40 CFR 63 Subpart A.

[Rule 62-204.800(11)(d)1., F.A.C.]

| General Provisions Citation | Subject of Citation |
| --- | --- |
| §63.1 | General applicability of the General Provisions |
| §63.2 | Definitions |
| §63.3 | Units and abbreviations |
| §63.4 | Prohibited activities and circumvention |
| §63.5 | Construction and reconstruction |
| §63.6(a) | Applicability |
| §63.9(i) | Adjustment of submittal deadlines |
| §63.9(j) | Change in previous information |
| §63.10(a) | Administrative provisions for recordkeeping/reporting |
| §63.10(b)(1) | Record retention |
| §63.10(b)(2)(vi)–(xi) | Records |
| §63.10(b)(2)(xii) | Record when under waiver |
| §63.10(b)(2)(xiv) | Records of supporting documentation |
| §63.10(b)(3) | Records of applicability determination |
| §63.10(d)(1) | General reporting requirements |
| §63.10(d)(4) | Progress Reports |
| §63.10(f) | Waiver for recordkeeping/reporting |
| §63.12 | State authority and delegations |
| §63.13 | Addresses |
| §63.14 | Incorporation by reference |
| §63.15 | Availability of information |

- 40 CFR 63 Requirements - Subpart ZZZZ   These emissions units shall comply with all applicable requirements of 40 CFR 63, Subpart ZZZZ, National Emission Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines (RICE), which have been adopted by reference in Rule 62-204.800(11)(b), F.A.C.  [Rule 62-204.800(11)(b), F.A.C.]

Subsection D.  The specific conditions in this section apply to the following emissions units:

| EU No. | Brief Description |
| --- | --- |
| 018 | New pump engine # 3; Nat. gas fueled Caterpillar G3512 LE-130 |
| 019 | New pump engine # 4; Nat. gas fueled Caterpillar G3512 LE-130 |
| 020 | New pump engine # 5; 2225 BHP Nat. gas fueled Caterpillar G3608 LE TA-130 |

| E.U. ID No. | Engine Brake HP | Date of Initial Startup | Primary Fuel | Type of Engine | Displacement liters/cylinder (l/c) | Manufacturer |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Model # |
| 018 | 738 | 6-11-2005 | Natural Gas | Non-Emergency | 4.3 | CAT |
|  |  |  |  |  |  | G3512 LE-130 |
| 019 | 738 | 6-14-2005 | Natural Gas | Non-Emergency | 4.3 | CAT |
|  |  |  |  |  |  | G3512 LE-130 |
| 020 | 2,225 | 3-1-2014* | Natural Gas | Non-Emergency | 21.2 | CAT |
|  |  |  |  |  |  | G3608 LE TA-130 |

*Purchase and construction process for EU020 began before 2006, therefore the engine is considered “existing” per 40 CFR Subpart ZZZZ

These natural gas fueled engines are existing non-emergency, non-black start four stroke lean burn stationary Reciprocal Internal Combustion Engines (RICE) greater than 500 hp located at an area source of HAP that are not remote stationary RICE and that operate more than 24 hours per calendar year per 40 CFR 63 Subpart ZZZZ.

These RICE have had oxidation catalysts installed with Continuous Parameter Monitoring Systems to continuously monitor catalyst inlet temperature.  The emissions units have also successfully undergone initial performance testing on the oxidation catalysts to demonstrate that they are meeting the requirements of 40 CFR 63.6612.

Essential Potential to Emit (PTE) Parameters

- Permitted Capacity.  The maximum allowable heat input rate is as follows:

| Unit No. | MMBtu/hr Heat Input | Fuel Type |
| --- | --- | --- |
| 018 | 5.26 | Natural Gas |
| 019 | 5.26 | Natural Gas |
| 020 | 13.70 | Natural Gas |

[Rules 62-4.160(2), 62-204.800, 62-210.200(PTE), F.A.C.; and, Permit No. 0250314-005-AC.]

- Emissions Unit Operating Rate Limitation After Testing.  See the related testing provisions in Appendix TR, Facility-wide Testing Requirements.  [Rule 62-297.310(2), F.A.C.]

- Methods of Operation.

  - Fuels.  The only fuel that is allowed to be used in these units is natural gas. [Rule 62-213.410, F.A.C.; Applicant’s request in Title V permit renewal application received August 15, 2015; and, Permit No. 0250314-005-AC.]

  - Fuel Limitation.  Fuel consumption shall not exceed 88 million standard cubic feet (MMscf) in any consecutive 12-month period for Emission Units EU018 and EU019 combined.  Annual fuel consumption shall not exceed 111 MMscf in any consecutive 12-month period for Emission Unit EU020.  [Rule 62-4.070(3), F.A.C. and Permit No. 0250314-005-AC]

- Hours of Operation.  These emissions units may operate continuously (8,760 hours/year).  [Rule 62-210.200(PTE), F.A.C.; and, Permit No. 0250314-005-AC]

Control and Monitoring Technology

- Oxidation Catalyst:  Facility is required to install an oxidation catalyst on the emissions units to reduce HAP emissions.  [40 CFR 63.6630(a) and Table 2d.9. of 40 CFR 63 Subpart ZZZZ]

- Continuous Parameter Monitoring System (CPMS).  The facility is required to install a CPMS to continuously monitor catalyst inlet temperature according to requirements (a) – (f) below, or to install equipment to automatically shut down the engine if the catalyst inlet temperature exceeds 1350 degrees F.

{Note:  Facility has installed CPMS systems.}

- Facility must prepare a site-specific monitoring plan that addresses the monitoring system design, data collection, and the quality assurance and quality control elements outlined in paragraphs (i) through (v) of this section and in 40 CFR 63.8(d).  As specified in 40 CFR 63.8(f)(4), you may request approval of monitoring system quality assurance and quality control procedures alternative to those specified in paragraphs (a) through (f) of this section in your site-specific monitoring plan.

(i) 	The performance criteria and design specifications for the monitoring system equipment, including the sample interface, detector signal analyzer, and data acquisition and calculations;

(ii)	Sampling interface ( e.g., thermocouple) location such that the monitoring system will provide representative measurements;

(iii)	Equipment performance evaluations, system accuracy audits, or other audit procedures;

(iv)	Ongoing operation and maintenance procedures in accordance with provisions in § 63.8(c)(1)(ii) and (c)(3); and

(v) 	Ongoing reporting and recordkeeping procedures in accordance with provisions in § 63.10(c), (e)(1), and (e)(2)(i).

- You must install, operate, and maintain each CPMS in continuous operation according to the procedures in your site-specific monitoring plan.

- The CPMS must collect data at least once every 15 minutes (see also 40 CFR 63.6635).

- For a CPMS for measuring temperature range, the temperature sensor must have a minimum tolerance of 2.8 degrees Celsius (5 degrees Fahrenheit) or 1 percent of the measurement range, whichever is larger.

- You must conduct the CPMS equipment performance evaluation, system accuracy audits, or other audit procedures specified in your site-specific monitoring plan at least annually.

- You must conduct a performance evaluation of each CPMS in accordance with your site-specific monitoring plan.

[Rule 40 CFR 63.6625(b)]

Emission Limitations and Standards

Unless otherwise specified, the averaging time for Specific Condition D.7 is based on the specified averaging time of the applicable test method.

- Visible Emissions.  Visible emissions shall not exceed 20 percent opacity using EPA Method 9 per Facility-Wide Condition FW4.  .  [Rule 62-296.320(4)(b), F.A.C.]

- General Compliance Requirements:

- The facility must be in compliance with the emission limitations, operating limitations, and other requirements in 40 CFR Subpart ZZZZ that applies to it at all times.

- At all times the facility  must operate and maintain the emissions unit, including associated air pollution control equipment and monitoring equipment, in a manner consistent with safety and good air pollution control practices for minimizing emissions

[Rule 40 CFR 63.6605]

Continuous Compliance

- Annual Compliance Demonstration.  These emissions units must demonstrate continuous compliance by conducting annual compliance demonstrations according to the conditions below to show that the average reduction of the emissions of CO is 93 percent or more, or the average emissions CO concentration is less than or equal to 47 ppmvd at 15 percent O2, and also by either collecting the catalyst inlet temperature data according to Condition D.6, reducing these data to 4-hour rolling averages,; and maintaining the 4-hour rolling averages without the limitation of greater than 450 degrees F and less than or equal to 1350 degrees F for the catalyst inlet temperature, or immediately shutting down the engine if the catalyst inlet temperature exceeds 350 degrees F.

- The compliance demonstration must consist of at least one test run.

- Each test run must be of at least 15 minute duration, except that each test conducted using the method in 40 CFR 63 Subpart ZZZZ Appendix A to this subpart must consist of at least one measurement cycle and include at least 2 minutes of test data phase measurement.

- The facility must measure CO emissions using one of the CO measurement methods specified below, or using 40 CFR 63 Subpart ZZZZ Appendix A to this subpart.  O2 measurements must be made at the same time as the CO measurements, and the CO concentration must be at 15% O2, dry basis as calculated using the method described in 40 CFR 63.6620(e).

(i)	ASTM D6522-00 (Reapproved 2005) or

(ii)	Method 10 of 40 CFR Part 60, Appendix A

- The facility must measure O2 using one of the O2 measurement methods specified below.  Measurements to determine O2 concentration must be made at the same time as the measurements for CO or THC concentration.

(i)	Method 3 or 3A or 3B of 40 CFR part 60, appendix A, or

(ii)	ASTM Method D6522-00 (Reapproved 2005)

- If you are demonstrating compliance with the CO percent reduction requirement, you must measure CO emissions and O2 emissions simultaneously at the inlet and outlet of the control device and calculate the percent reduction using the method described in 40 CFR 63.6620(e).

- If the results of the annual compliance demonstration show that the emissions exceed the levels specified above, the stationary RICE must be shut down as soon as safely possible, and appropriate corrective action must be taken (e.g., repairs, catalyst cleaning, catalyst replacement).  The stationary RICE must be retested within 7 days of being restarted and the emissions must meet the levels specified above.  If the retest shows that the emissions continue to exceed the specified levels, the stationary RICE must again be shut down as soon as safely possible, and the stationary RICE may not operate, except for purposes of startup and testing, until the owner/operator demonstrates through testing that the emissions do not exceed the levels specified above.

[40 CFR 63.6640(c) and Table 4 and Table 6 to 40 CFR 63 Subpart ZZZZ]

- The facility must minimize the engine's time spent at idle during startup and minimize the engine's startup time to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes, after which time the emission standards applicable to all times other than startup apply.  [40 CFR 6625(h)]

Test Methods and Procedures

- Test Methods.  When required, tests shall be performed in accordance with the following reference methods:

| Method | Description of Method and Comments |
| --- | --- |
| 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |
| 10 | Determination of Carbon Monoxide Emissions from Stationary Sources {Note: The method shall be based on a continuous sampling train.} |
| 18 | Measurement of Gaseous Organic Compound Emissions by Gas Chromatography |
| 19 | Determination of Sulfur Dioxide Removal Efficiency and Particulate Matter, Sulfur Dioxide, and Nitrogen Oxides Emission Rates (Optional F-factor method may be used to determine flow rate and gas analysis to calculate mass emissions in lieu of Methods 1-4.) |
| 20 | Determination of Nitrogen Oxides, Sulfur Dioxide and Diluent Emissions from Stationary Gas Turbines |
| 25A | Method for Determining Gaseous Organic Concentrations (Flame Ionization) |

The above methods are described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Rule 62-297.401, F.A.C., and, 40 CFR 63 Subpart ZZZZ]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

Recordkeeping and Reporting Requirements

- Fuel Use.  Owner or operator shall keep monthly records of total fuel consumption for these emission units and keep a running 12-month total of fuel use for each emission unit to ensure compliance with Specific Condition D.3 above.  [Rule 62-4.070(3), F.A.C. and Permit No. 0250314-005-AC]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440(1)(b), F.A.C.]

- You must submit all of the notifications in 40 CFR 63.7(b) and (c), 40 CFR 63.8(e), (f)(4) and (f)(6), 40 CFR 63.9(b) through (e), and (g) and (h) that apply to you.

- Notification of Intent.  If you are required to conduct a performance test, you must submit a Notification of Intent to conduct a performance test at least 60 days before the performance test is scheduled to begin as required in 40 CFR 63.7(b)(1).

- Notification of Compliance Status.  For each performance test, you must submit the Notification of Compliance Status, including the performance test results, before the close of business on the 60th day following the completion of the performance test according to 40 CFR 63.10(d)(2)

- Compliance Report.  Submit the results of the annual compliance demonstration, if conducted during the reporting period, with the Semiannual Compliance Report.

- Facility must report each instance in which you did not meet each emission limitation or operating limitation to 40 CFR 63 Subpart 63 that applies to these emissions units.  These instances are deviations from the emission and operating limitations in this subpart.  These deviations must be reported according to the requirements in 40 CFR 63.6650.  If the facility changes the catalyst, the facility must reestablish the values of the operating parameters measured during the initial performance test.  When the facility reestablishes the values of your operating parameters, the facility must also conduct a performance test to demonstrate that the facility is meeting the required emission limitation applicable to the stationary RICE.

- Record Retention.

- The owner or operator must keep records in a suitable and readily available form for expeditious reviews.

- The owner or operator must keep each record readily accessible in hard copy or electronic form for at least 5 years after the date of each occurrence, measurement, maintenance, corrective action, report, or record.

[40 CFR 63.6660 and 40 CFR 63.10(b)(1)]

Other Requirements

## Applicability of General Provisions to Subpart ZZZZ.

- As stated in § 63.6665, the facility must comply with the following applicable general provisions.

| General Provisions Citation | Subject of Citation |
| --- | --- |
| §63.1 | General applicability of the General Provisions |
| §63.2 | Definitions |
| §63.3 | Units and abbreviations |
| §63.4 | Prohibited activities and circumvention |
| §63.5 | Construction and reconstruction |
| §63.6(a) | Applicability |
| §63.9(i) | Adjustment of submittal deadlines |
| §63.9(j) | Change in previous information |
| §63.10(a) | Administrative provisions for recordkeeping/reporting |
| §63.10(b)(1) | Record retention |
| §63.10(b)(2)(vi)–(xi) | Records |
| §63.10(b)(2)(xii) | Record when under waiver |
| §63.10(b)(2)(xiv) | Records of supporting documentation |
| §63.10(b)(3) | Records of applicability determination |
| §63.10(d)(1) | General reporting requirements |
| §63.10(d)(4) | Progress Reports |
| §63.10(f) | Waiver for recordkeeping/reporting |
| §63.12 | State authority and delegations |
| §63.13 | Addresses |
| §63.14 | Incorporation by reference |
| §63.15 | Availability of information |

Subsection E.  The specific conditions in this section apply to the following emissions units:

| 021 | Allis-Chalmers Emergency Generator for Lime Kiln, rated at 250 kW |
| --- | --- |
| 026 | LISTER 18 HP Diesel Engine Driven Starting Air Compressor |
| 028 | HATZ 37 HP Diesel Engine Driven Starting Air Compressor |

{Permitting Note:  This emissions units is regulated under NESHAP 40 CFR 63 Subpart ZZZZ as existing (constructed or reconstructed prior to June 12, 2006) emergency diesel engines under 500 hp operating at an area source of HAPs.}

| E.U. ID No. | Engine Brake HP | Date of Initial Startup | Primary Fuel | Type of Engine | Displacement liters/cylinder (l/c) | Manufacturer |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Model # |
| 021 | Approx. 400 | 2-1-1982 | Ultra Low Diesel No. 2 | Emergency | <30 | Allis-Chalmers |
|  |  |  |  |  |  | 6138T |
| 026 | 18 | 1991 | Ultra Low Diesel No. 2 | Emergency | <30 | LISTER |
|  |  |  |  |  |  | ST2 |
|  |  |  |  |  |  | 804D-T |
| 028 | 37 | 1997 | Ultra Low Diesel No. 2 | Emergency | <30 | HATZ |
|  |  |  |  |  |  | 2M40LZ |

These previously unregulated diesel engines are considered existing emergency diesel stationary Reciprocal Internal Combustion Engines (RICE) less than 500 hp located at an area source of HAP per 40 CFR 63 Subpart ZZZZ.

Essential Potential to Emit (PTE) Parameters

- Permitted Capacity.  The maximum allowable heat input rate is as follows:

| Unit No. | MMBtu/hr Heat Input | Fuel Type |
| --- | --- | --- |
| 021 | 3.7 | Ultra Low Diesel No. 2 |
| 026 | 0.17 | Ultra Low Diesel No. 2 |
| 028 | 0.30 | Ultra Low Diesel No. 2 |

[Rules 62-4.160(2), 62-210.200(PTE), F.A.C.; and, Permit Application No. 0250314-021-AV.]

- Emissions Unit Operating Rate Limitation After Testing.  See the related testing provisions in Appendix TR, Facility-wide Testing Requirements.  [Rule 62-297.310(3), F.A.C.]

Methods of Operation

- Hours of Operation.

- Emergency Situations.  There is no time limit on the use of emergency stationary RICE in emergency situations.  [40 CFR 63.6640(f)(1)]

- Maintenance and Testing.  Each RICE is authorized to operate for the purpose of maintenance checks and readiness testing, provided that the tests are recommended by federal, state or local government, the manufacturer, the vendor, or the insurance company associated with the engine. Maintenance checks and readiness testing of such units is limited to 100 hours per year. [40 CFR 63.6640(f)(2)]

- Non-emergency Situations.  Each RICE is authorized to operate up to 50 hours per year in non-emergency situations, but those 50 hours are counted towards the 100 hours per year provided for maintenance and testing.  [40 CFR 63.6640(f)(4)]

- Other Situations.  Each RICE cannot be used for peak shaving or to generate income for a facility to supply power to an electric grid or otherwise supply power as part of a financial arrangement with another entity; except that owners and operators may operate the emergency engine for a maximum of 15 hours per year as part of a demand response program if the regional transmission organization or equivalent balancing authority and transmission operator has determined there are emergency conditions that could lead to a potential electrical blackout, such as unusually low frequency, equipment overload, capacity or energy deficiency, or unacceptable voltage level. The engine may not be operated for more than 30 minutes prior to the time when the emergency condition is expected to occur, and the engine operation must be terminated immediately after the facility is notified that the emergency condition is no longer imminent. The 15 hours per year of demand response operation are counted as part of the 50 hours of operation per year provided for non-emergency situations. The supply of emergency power to another entity or entities pursuant to financial arrangement is not limited by this paragraph, as long as the power provided by the financial arrangement is limited to emergency power.  [40 CFR 63.6640(f)(4)]

- Engine Startup.  During periods of startup the owner or operator must minimize the engine's time spent at idle and minimize the engine's startup time to a period needed for the appropriate and safe loading of the engine, not to exceed 30 minutes, after which time the non-startup emission limitations apply.  [40 CFR 63.6625(h)]

Emission Limitations and Standards

{Permitting note:  These “existing” stationary CI engines with < 500 HP do not have specific numerical emission limitations and standards.}

- Work or Management Practice Standards.

- Oil.  Change oil and filter every 500 hours of operation or annually, whichever comes first.  [40 CFR 63 Table 2d(4)(a)]

- Air Cleaner.  Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first.  [40 CFR 63 Table 2d(4)(b)]

- Hoses and Belts.  Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary.  [40 CFR 63 Table 2d(4)(c)]

- Operation and Maintenance.  Operate and maintain the stationary RICE according to the manufacturer's emission-related operation and maintenance instructions or develop and follow your own maintenance plan which must provide, to the extent practicable for the maintenance and operation of the engine in a manner consistent with good air pollution, control practice for minimizing emissions.  [40 CFR 63.6625(e)]

- Oil Analysis.  The owner or operator has the option of using oil analysis to extend the change requirement.  The oil analysis must be performed at the same frequency specified for changing the oil.  The analysis program must at a minimum analyze the following three parameters: Total Base Number, viscosity, and percent of water content.  The condemning limits for these parameters are as follows: Total Base Number is less than 30 percent of the Total Base Number of the oil when new; viscosity of the oil has changed by more than 20 percent from the viscosity of the oil when new; or percent of water content (by volume) is greater than 0.5.  If all of these condemning limits are not exceeded, the engine owner or operator is not required to change the oil.  If any of the limits are exceeded, the engine owner or operator must change the oil within 2 days of receiving the results of the analysis; if the engine is not in operation when the results of the analysis are received, the engine owner or operator must change the oil within 2 days or before commencing operation, whichever is later.  The owner or operator must keep records of the parameters that are analyzed as part of the program, the results of the analysis, and the oil changes for the engine. The analysis program must be part of the maintenance plan for the engine.  [40 CFR 63.6625(i)]

Monitoring of Operations

- Hour Meter.  The owner or operator must install a non-resettable hour meter if one is not already installed.  [40 CFR 63.6625(f)]

Continuous Compliance

- Continuous Compliance.  Each unit shall be in compliance with the emission limitations and operating standards in this section at all times.  [40 CFR 63.6605(a)]

- Operation and Maintenance of Equipment.  At all times the owner or operator must operate and maintain, any affected source, including associated air pollution control equipment and monitoring equipment, in a manner consistent with safety and good air pollution control practices for minimizing emissions.  Determination of whether such operation and maintenance procedures are being used will be based on information available to the compliance authority which may include, but is not limited to, monitoring results, review of operation and maintenance procedures, review of operation and maintenance records, and inspection of the source.  [40 CFR 63.6605(b)]

Recordkeeping and Reporting Requirements

- Hours of Operation.  The owner or operator must keep records of the hours of operation of the engine that is recorded through the non-resettable hour meter.  The owner or operator must document how many hours are spent for emergency operation, including what classified the operation as emergency and how many hours are spent for non-emergency operation.  [40 CFR 63.6655(f)]

- Notifications.  The owner or operator must keep the records of each notification and report that was submitted to comply with 40 CFR 63 Subpart ZZZZ, including all documentation supporting any Initial Notification or Notification of Compliance Status that was submitted, according to the requirement in 40 CFR 63.10(b)(2)(xiv). [40 CFR 63.6655]

- Fuel Use.  From the daily records of diesel fuel usage the permittee shall record and maintain a rolling 365-day total of the amount of fuel consumed by the generators.  This rolling 365-day total record shall be updated each day.  These records shall be used for the annual operating report.  [Rule 62-4.070(3)]

- Malfunction Records.

- Records of the occurrence and duration of each malfunction of operation (i.e. process equipment) or the air pollution control and monitoring equipment.

- Records of actions taken during periods of malfunction to minimize emissions in accordance with 40 CFR 63.6605(b) of this section including corrective actions to restore malfunctioning process and air pollution control and monitoring equipment to its normal or usual manner of operation.

[40 CFR 63.6655]

- Maintenance Records.

- Records of all required maintenance performed on the air pollution control and monitoring equipment.

- The owner or operator must keep records of the maintenance conducted on the stationary RICE in order to demonstrate that the stationary RICE and after-treatment control device (if any) are operated and maintained according to its own maintenance plan.

[40 CFR 63.6655]

- Record Retention.

- The owner or operator must keep records in a suitable and readily available form for expeditious reviews.

- The owner or operator must keep each record readily accessible in hard copy or electronic form for at least 5 years after the date of each occurrence, measurement, maintenance, corrective action, report, or record.

[40 CFR 63.6660 and 40 CFR 63.10(b)(1)]

- Emergency Situation.  If an emergency engine is operating during an emergency and it is not possible to shut down the engine in order to perform the work practice requirements on the schedule required of this section, or if performing the work practice on the required schedule would otherwise pose an unacceptable risk under federal, state, or local law, the work practice can be delayed until the emergency is over or the unacceptable risk under federal, state, or local law has abated.  The work practice should be performed as soon as practicable after the emergency has ended or the unacceptable risk under federal, state, or local law has abated.  Sources must report any failure to perform the work practice on the schedule required and the federal, state or local law under which the risk was deemed unacceptable.  [40 CFR 63.6602 Table 2c, footnote 1]

- The owner or operator must report each instance in which the owner or operator did not meet each emission limitation or operating limitation in this section.  [40 CFR 63.6640(b)]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440(1)(b), F.A.C.]

NESHAP 40 CFR 63, Subpart A & ZZZZ Requirements

- 40 CFR 63 Requirements - Subpart A.  These emissions units shall comply with all applicable requirements of 40 CFR 63, Subpart A, General Provisions, which have been adopted by reference in Rule 62-204.800(11)(d)1., F.A.C., except that the Secretary is not the Administrator for purposes of 40 CFR 63.5(e), 40 CFR 63.5(f), 40 CFR 63.6(g), 40 CFR 63.6(h)(9), 40 CFR 63.6(j), 40 CFR 63.13, and 40 CFR 63.14.  The applicable 40 CFR 63, Subpart A, General Provisions to which these emissions are subject to are found at 40 CFR 63.6665 and are included in Appendix 40 CFR 63 Subpart A.  [Rule 62-204.800(11)(d)1., F.A.C.]

| General Provisions Citation | Subject of Citation |
| --- | --- |
| §63.1 | General applicability of the General Provisions |
| §63.2 | Definitions |
| §63.3 | Units and abbreviations |
| §63.4 | Prohibited activities and circumvention |
| §63.5 | Construction and reconstruction |
| §63.6(a) | Applicability |
| §63.9(i) | Adjustment of submittal deadlines |
| §63.9(j) | Change in previous information |
| §63.10(a) | Administrative provisions for recordkeeping/reporting |
| §63.10(b)(1) | Record retention |
| §63.10(b)(2)(vi)–(xi) | Records |
| §63.10(b)(2)(xii) | Record when under waiver |
| §63.10(b)(2)(xiv) | Records of supporting documentation |
| §63.10(b)(3) | Records of applicability determination |
| §63.10(d)(1) | General reporting requirements |
| §63.10(d)(4) | Progress Reports |
| §63.10(f) | Waiver for recordkeeping/reporting |
| §63.12 | State authority and delegations |
| §63.13 | Addresses |
| §63.14 | Incorporation by reference |
| §63.15 | Availability of information |

- 40 CFR 63 Requirements - Subpart ZZZZ [Generally Applicable Requirements].  These emissions units shall comply with all applicable requirements of 40 CFR 63, Subpart ZZZZ, National Emission Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines (RICE), which have been adopted by reference in Rule 62-204.800(11)(b), F.A.C.  These emissions units shall comply with Appendix 40 CFR 63 Subpart ZZZZ “Generally Applicable Requirements,” included with this permit, which includes applicable requirements that apply in general to all engines regulated under 40 CFR 63 Subpart ZZZZ.  This appendix also contains useful information like provisions that are not delegated to state or local agencies (see 40 CFR 63.6670) and contains definitions (see 40 CFR 63.6675) that are specific to engines regulated under 40 CFR 63 Subpart ZZZZ.  [Rule 62-204.800(11)(b), F.A.C.]

The specific conditions in this section apply to the following emissions unit:

| EU No. | Brief Description |
| --- | --- |
| 027 | PERKINS 83 HP Emergency Kiln Rotation Engine |

{Permitting note:  This part of the subsection addresses new stationary emergency constant speed CI RICE greater than 37 kw and less than 75 kw that are located at a major source of HAP and that have been constructed or reconstructed after 2008.  This RICE is not used as a fire pump.

This emission unit is subject to the requirements of 40 CFR part 60 subpart IIII standards of performance for stationary compression ignition internal combustion engines (CI). By meeting the requirements for 40 CFR part 60 subpart IIII the emission unit also meets the requirements of 40 CFR part 63 subpart ZZZZ “National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocation Internal Combustion Engines” (CFr 63.6590}

| E.U. ID No. | Engine Brake HP/kw | Date of Initial Startup | Primary Fuel | Type of Engine | Displacement liters/cylinder (l/c) | Manufacturer |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Model # |
| 027 | 83/62 | 2012 | Ultra Low Diesel No. 2 | Emergency | <30 | PERKINS |
|  |  |  |  |  |  | 804D-T |

Essential Potential to Emit (PTE) Parameters

- Permitted Capacity.  The maximum allowable heat input rate is as follows:

| Unit No. | MMBtu/hr Heat Input | Fuel Type |
| --- | --- | --- |
| 027 | 0.77 | Ultra Low Diesel No. 2 |

[Rules 62-4.160(2), 62-204.800, 62-210.200(PTE)]

- Allowable Fuel.   The Stationary RICE must use diesel fuel that meets the following requirements for non-road diesel fuel:

- Sulfur Content.  The sulfur content shall not exceed 15 ppm 0.0015% weight for Non-Road fuel.

- Cetane and Aromatic.  The fuel must have a minimum cetane index of 40 or must have a maximum aromatic content of 35 volume percent.

[40 CFR 60.4207(b) and 80.510(b)]

- Hours of Operation.

- Emergency Situations.  There is no time limit on the use of emergency stationary RICE in emergency situations.  [40 CFR 60.4211(e)]

- Maintenance and Testing.  Each RICE is authorized to operate for the purpose of maintenance checks and readiness testing, provided that the tests are recommended by federal, state, or local government, the manufacturer, the vendor, or the insurance company associated with the engine. Maintenance checks and readiness testing of such units is limited to 100 hours per year.  [40 CFR 60.4211(e)]

- Other Situations.  Each RICE cannot be used for peak shaving or to generate income for a facility to supply power to an electric grid or otherwise supply power as part of a financial arrangement with another entity.  [40 CFR 60.4219]

Emission Limitations and Standards

- NMHC + NOX Emissions.  Non-Methane Hydrocarbons and Nitrogen oxide emissions shall not exceed 4.7 g/KW-hr.  [40 CFR 60.4205(b) & 40 CFR 89.112 Table 1]

- CO Emissions.  Carbon monoxide emissions shall not exceed 5.0 g/KW-hr.  [40 CFR 60.4205(b) & 40 CFR 89.112 Table 1

- PM emissions.  Particulate matter emissions shall not exceed 0.4 g/KW-hr.  [40 CFR 60.4205(b) & 40 CFR 89.112 Table 1]

- Operation and Maintenance.  The owner or operator must operate and maintain the stationary CI internal combustion engine according to the manufacturer's written instructions or procedures developed by the owner or operator that are approved by the engine manufacturer.  In addition, owners and operators may only change those settings that are permitted by the manufacturer. The owner or operator must meet the requirements of 40 CFR parts 89, 94 and/or 1068, as they apply.  [40 CFR 60.4211(a)]

Monitoring of Operations

- Fuel Use.  The fuel use shall be monitored and recorded.  [62-4.070(3), F.A.C.]

Recordkeeping and Reporting Requirements

- Required Records.  Owner or operator must keep records of the operation of the engine in emergency and non-emergency service.  The owner or operator must record the time of operation of the engine and the reason the engine was in operation during that time.  [40 CFR 60.4214]

- Fuel Use:  The owner or operator shall make and maintain daily records of diesel fuel consumption for this emission unit at the end of each day. Within ten days of the end of each month, the owner or operator shall make records of monthly diesel fuel consumption from the daily records.  [Rule 62-4.070(3)]

- Records Retention.

- The owner or operator must keep records in a suitable and readily available form for expeditious reviews.

- The owner or operator must keep each record readily accessible in hard copy or electronic form for at least 5 years after the date of each occurrence, measurement, maintenance, corrective action, report, or record.

[62-4.070(3), F.A.C.]

General Provisions

- 40 CFR 60 Subpart A, General Provisions.  This engine shall comply with all applicable requirements of 40 CFR 60 Subpart A, General Provisions, which have been adopted by reference in Rule 62-204.800(11)(d)1., F.A.C.  This engine shall comply with the applicable portions of Appendix 40 NSPS Subpart A included with this permit, as specified below.

| General Provisions Citation | Subject of Citation |
| --- | --- |
| § 60.1 | General applicability of the General Provisions |
| § 60.2 | Definitions (see also § 60.4219) |
| § 60.3 | Units and abbreviations |
| § 60.4 | Address |
| § 60.5 | Determination of construction or modification |
| § 60.6 | Review of plans |
| § 60.7 | Notification and Recordkeeping (as specified in § 60.4214(a) |
| § 60.8 | Performance tests (if required) |
| § 60.9 | Availability of information |
| § 60.10 | State Authority |
| § 60.12 | Circumvention |
| § 60.14 | Modification |
| § 60.15 | Reconstruction |
| § 60.16 | Priority list |
| § 60.17 | Incorporations by reference |
| § 60.19 | General notification and reporting requirements |

[40 CFR 60.4218]

The specific conditions in this section apply to the following emissions unit:

| EU No. | Brief Description |
| --- | --- |
| 025 | Standby Diesel Engine Generator # 6, EMD model No. L16-710-G4C-T2 |

This diesel-driven generator is the sixth of a bank of six generators that provide standby power for the continuous plant operation.  Specific conditions for the other five engines (EUs 009, 010, 011, 012, and 024) are provided in Subsection B.

This emissions units is subject to regulation under Rule 62-212.400, F.A.C. Prevention of Significant Deterioration (PSD) and is subject to the requirements of the state rules as indicated in the Tile V operation permit renewal.

This engine is also regulated under 40 CFR 63, Subpart ZZZZ, National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines (RICE) adopted in Rule 62.204.800(11)(b), F.A.C. and 40 CFR 60, Subpart IIII, Standards of Performance for Stationary Compression Ignition Internal Combustion Engines.  Compliance with the requirements of 40 CFR 63, Subpart ZZZZ is met by meeting the requirements of 40 CFR 60, Subpart IIII.  No further requirements of 40 CFR 63, Subpart ZZZZ apply for this engine.  This permit section addresses a stationary CI RICE with a displacement greater than 10 liters per cylinder and less than 15 liters per cylinder, that is located at an area source of HAP and that has been constructed on or after 6/12/2006.  This engine certified by the manufacturer to meet the Tier 2 standards for a 2007 model year marine engine.

| E.U. ID No. | Engine Brake HP | Date of Initial Startup | Primary Fuel | Type of Engine | Displacement liters/cylinder (l/c) | Manufacturer |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Model # |
| 025 | 4000 | 2015 | Ultra Low Diesel No. 2 | Non-Emergency* | 11.6 | EMD |
|  |  |  |  |  |  | L16-710-G4C-T2 |

*Load Sharing Contract with Electric Utility precludes generators from qualifying as an emergency engine per 40 CFR63 Subpart ZZZZ.

Essential Potential to Emit (PTE) Parameters

- Permitted Capacity.  The maximum heat input rate for each unit is 27 MMBtu per hour (approximately 197 gallons per hour).

[Rule 62-210.200(PTE), F.A.C., and Permit 0250314-014-AC]

{Permitting Note:  27 MMBtu/hr is approximately equal to 197 gallons per hour based on a higher heating value of 19,640 btu/lb and a density of 7.034 pounds per gallon of diesel}

- Methods of Operation:

- Fuels.

- Sulfur Content.  The sulfur content shall not exceed 15 ppm (0.0015% by weight) for non-road diesel fuel.

- Cetane and Aromatic.  The fuel must have a minimum cetane index of 40 or must have a maximum aromatic content of 35 volume percent.

[40 CFR 60.4207(b), and 80.510(b)]

- Fuel consumption of all six generator emission units (EUs 009, 010, 011, 012, 024, and 025) combined shall not exceed 1,200,000 gallons of diesel fuel in any consecutive 12-month period. [Permit No. 0250314-014-AC]

- [40 CFR 60.4207(b), and 80.510(b), Permit No. 0250314-014-AC]  Hours of Operation.  The hours of operation of all six generator emission units (EUs 009, 010, 011, 012, 024, and 025) are contingent upon fuel consumption per Condition G.2 b. above.  [Rule 62-210.200(PTE), F.A.C.; and, Permit No. 0250314-014-AC]

{Permitting Note:  Based on a total fuel consumption and fuel flow rate of approximately 197 gallons per hour, it equates to 6091 hours per year for all six units combined.}

- Operation and Maintenance.  The owner or operator must operate and maintain the stationary CI internal combustion engine according to the manufacturer's written instructions or procedures developed by the owner or operator that are approved by the engine manufacturer.  In addition, owners and operators may only change those settings that are permitted by the manufacturer. The owner or operator must meet the requirements of 40 CFR parts 89, 94 and/or 1068, as they apply. [40 CFR 60.4211(a)]

Emission Limitations and Standards

- NOX Emissions.  Nitrogen oxide (NOX) emissions shall not exceed 3.40 lb/MMBtu as determined by the average of three 1-hour compliance test runs conducted in accordance with EPA Method 7 or 7E.  (Equivalent to a NOx emission rate of approximately 92.5 pounds per hour at 100% engine load for each unit.)  NOx emissions from the bank of the six standby generators are limited to 282 tons per year.  [Rule 62-212.400, F.A.C. and BACT Determination for PSD-FL-249 in Permit No. 0250314-014-AC]

- NMHC + NOX Emissions.  Non-Methane Hydrocarbons and Nitrogen oxide emissions shall not exceed 7.8 g/KW-hr (or 10.5 g/hp-hr).  [40 CFR 60.4204(b), 60.4205(b) 60.4201(d)(1) & 40 CFR 94.8(a)(2)(i) Table A-1]

- CO Emissions.  Carbon monoxide emissions shall not exceed 5.0 g/KW-hr (or 6.7 g/hp-hr).  [40 CFR 60.4204(b), 60.4205(b) 60.4201(d)(1) & 40 CFR 94.8(a)(2)(i) Table A-1]

- PM emissions.  Particulate matter emissions shall not exceed 0.27 g/KW-hr (or 0.36 g/hp-hr).  [40 CFR 60.4204(b), 60.4205(b) 60.4201(d)(1) & 40 CFR 94.8(a)(2)(i) Table A-1]

{Permitting Note:  The engine is certified by the manufacturer to meet the 2007 Tier 2 Standards for NMHC+NOx, CO, and PM emissions above.}

Monitoring and Testing of Operations

- Test Methods:  Any required tests shall be performed in accordance with the following reference methods or any other test Method approved by the Department.

| Method | Description of Method and Comments |
| --- | --- |
| 5 | Determination of PM Emissions from Stationary Sources |
| 7 or 7E | Determination of Nitrogen Oxide Emissions from Stationary Sources |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |
| 10 | Determination of Carbon Monoxide Emissions from Stationary Sources {Notes: The method shall be based on a continuous sampling train.} |
| 201 | Determination of PM with a Mean Diameter of 10 Microns or Less (PM10) |

- Hour Meter.  The owner or operator must install, maintain and operate a non-resettable hour meter.  [Permit No. 0250314-014-AC, Specific Condition A.12]

- Fuel Meter.  The owner or operator must install, maintain and operate a monitoring device to record the fuel flow for the emissions unit. [62.4.070(3), F.A.C., and Permit No. 0250314-014-AC]

- Fuel Sulfur Content Tests:  The owner or operator shall determine the sulfur content of each delivery of diesel fuel received for these emissions units using ASTM D 4057-88, Standard Practice for Manual Sampling of Petroleum and Petroleum Products; and one of the following test methods for sulfur in petroleum products:  ASTM D 129-91, ASTM D 2622-94, or ASTM D 4294-90.  These methods are adopted by Rule 62-297.440, F.A.C.  The owner or operator may comply with this requirement by receiving records from the fuel supplier that indicate the sulfur content of the fuel delivered complies with the sulfur limit specified in this permit.  [Rules 62-4.070(3) and 62-297.440, F.A.C.]

- Annual NOx Compliance Tests:  During each calendar year (January 1 – December 31), the unit shall be tested to demonstrate compliance with the 3.40 lb/MMBtu NOx emission standard if the unit operated more than 400 hours during the previous 12 months.  [Rules 62-4.070(3), 62-297.310(7)(a), 62-212.400(12)b, F.A.C., and 40 CFR 60.8

- NOx Emissions Cap:  To demonstrate compliance with the projected actual NOx emissions cap of 282 tons per year for Units 1-6, the permittee shall do the following:

- The permittee shall monitor NOx emissions; and, using the most reliable information available, calculate and maintain a record of the annual emissions, in tons per year on a calendar year basis, for a period of 5 years following resumption of regular operations.  Emissions shall be computed in accordance with Rule 62-210.370, F.A.C.

- The permittee shall report to the Department within 60 days after the end of each year during which records must be generated under subparagraph 62-212.300(1)(e)1., F.A.C., setting out the units annual emissions during the calendar year that preceded submission of the report.  The report shall contain the following:

- The name, address and telephone number of the owner or operator of the major stationary source;

- The annual emissions as calculated pursuant to subparagraph 62-212.300(1)(e)1., F.A.C.;

- If the emissions differ from the preconstruction projection, an explanation as to why there is a difference; and

- Any other information that the owner or operator wishes to include in the report.

- The information required to be documented and maintained pursuant to subparagraphs 62-212.300(1)(e)1. and 2., F.A.C., shall be submitted to the Department, which shall make it available for review to the general public.

[Rule 62-212.300 F.A.C. and Permit No. 0250314-014-AC]

- Annual Reporting:  Records required for Unit 1-6 shall be submitted to the Compliance Authority on an annual basis or upon request.  [Rule 62-4.070(3) F.A.C.]

Notifications, Records and Reports

- Test Notification:  The owner or operator shall notify the Compliance Authority, at least 15 days prior to the date on which each formal compliance test is to begin, of the date, time, and place of each such test, and the test contact person who will be responsible for coordinating and having such test conducted for the owner or operator.  [Rule 62-297.310(7)(a)9, F.A.C.]

- Test Report.  The owner or operator of an emissions unit for which a compliance test is required shall file a report with the Compliance Authority on the results of each such test. The required test report shall be filed with the Compliance Authority as soon as practical but no later than 45 days after the last sampling run of each test is completed. The test report shall provide sufficient detail on the emissions unit tested and the test procedures used to allow the Compliance Authority to determine if the test was properly conducted and the test results properly computed. As a minimum, the test report shall provide the information required in Rule 62-297.310(8), F.A.C. [See Appendix TR, Testing Requirements, Rule 62-297.310(8), F.A.C. and Permit No. 0250314-014-AC, Specific Condition A.15]

- Annual Operating Report (AOR).

- The permittee shall submit to the Compliance Authority, each calendar year, on or before April 1st, a completed DEP Form No. 62-210.900(5), “Annual Operating Report for Air Pollutant Emitting Facility”, for the preceding calendar year.

- Emissions shall be computed in accordance with the provisions of Rule 62-210.370(2), F.A.C.

[Rules 62-210.370(2) & (3) and 62-213.440(3)(a)2., F.A.C.; and, Permit No. 0250314-AC, Specific Condition 19]

- AOR Supplemental Information: Annual operating reports shall include the following supplemental information that was recorded in the previous calendar year:

- The highest consecutive 12 months total diesel fuel usage for the standby generators

- Records of the fuel meter calibration

- A statement by the permittee that the fuel sulfur limitation was or was not exceeded during the previous calendar year

- A statement by the permittee whether or not the records of fuel supplier certifications maintained by the permittee represent all fuel oil burned during the previous calendar year.  [Rule 62-4.070(3), F.A.C.]

- Notifications and Records.  The following requirements must be met:

- Initial Notification.  Submit an initial notification as required in §60.7(a)(1).  The notification must include the following information:

  - Name and address of the owner or operator;

  - The address of the affected source;

  - Engine information including make, model, engine family, serial number, model year, maximum engine power, and engine displacement;

  - Emission control equipment; and

  - Fuel used.

{Permitting Note:  Facility has submitted initial notification for this emissions unit.}

- Records.  The following records must be kept:

  - All notifications submitted to comply with this subpart and all documentation supporting any notification.

  - Maintenance conducted on the engine.

  - If the stationary CI internal combustion is a certified engine, documentation from the manufacturer that the engine is certified to meet the emission standards.

  - If the stationary CI internal combustion is not a certified engine, documentation that the engine meets the emission standards.

  - Fuel Records.  The owner or operator shall maintain records of the sulfur content of each delivery of diesel fuel received for this emission unit. The owner or operator shall make and maintain daily records of diesel fuel consumption for this emission unit at the end of each day. Within ten days of the end of each month, the owner or operator shall make records of monthly diesel fuel consumption from the daily records, and shall make records of the consecutive 12-month diesel fuel consumption to demonstrate compliance with the fuel consumption limits specified in this permit. [40 CFR 60.4214(a), Rule 62-4.070(3), F.A.C. and Permit No. 0250314-014-AC, Specific Condition No. A.17]

- Record Retention.

- The owner or operator must keep records in a suitable and readily available form for expeditious reviews.  Year-to-date hours of operation of the unit and fuel usage in gallons for the unit are to be monitored and recorded.  Records concerning maintenance conducted on the engine must also be kept, and documentation from the manufacturer that the engine is certified to meet the emission standards must be on file.

- The owner or operator must keep each record readily accessible in hard copy or electronic form for at least 5 years after the date of each occurrence, measurement, maintenance, corrective action, report, or record.

[Rule 62-4.070(3), and 62-213.440(1)(b)2.b.]

General Provisions

- NSPS 40 CFR 60, Subpart A.  The engine shall comply with the requirements of 40 CFR 60, Subpart A, General Provisions, listed below, which have been adopted by reference in Rule 62-204.800(8)(d), F.A.C.; except that the Secretary is not the Administrator for purposes of 40 CFR 60.4, 40 CFR 60.8(b)(2) and (3), 40 CFR 60.11(e)(7) and (8), 40 CFR 60.13(g), (i) and (j)(2), and 40 CFR 60.16.  See Appendix NSPS, Subpart A, General Provisions.  [Rule 62-204.800(8)(d), F.A.C.]

| General Provisions Citation | Subject of Citation |
| --- | --- |
| §60.1 | General applicability of the General Provisions |
| §60.2 | Definitions (additional terms defined in §60.4219) |
| §60.3 | Units and abbreviations |
| §60.4 | Address |
| §60.5 | Determination of construction or modification |
| §60.6 | Review of plans |
| §60.7 | Notification and Recordkeeping (only as specified in Condition 13.) |
| §60.8 | Performance tests (only if engine is not certified) |
| §60.9 | Availability of information |
| §60.10 | State Authority |
| §60.12 | Circumvention |
| §60.14 | Modification |
| §60.15 | Reconstruction |
| §60.16 | Priority list |
| §60.17 | Incorporations by reference |
| §60.19 | General notification and reporting requirements |

Appendix A, Glossary.

Appendix I, List of Insignificant Emissions Units and/or Activities.

Appendix NSPS, 40 CFR 60 Subpart A, General Provisions

Appendix NSPS 40 CFR 60 Subpart IIII, Standards of Performance for Stationary Compression Ignition Internal Combustion Engines

Appendix NESHAP, 40 CFR 63 Subpart A, General Provisions

Appendix NESHAP, 40 CFR 63 Subpart ZZZZ, National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines

Appendix RR, Facility-wide Reporting Requirements.

Appendix TR, Facility-wide Testing Requirements.

Appendix TV, Title V General Conditions.

Appendix U, List of Unregulated Emissions Units and/or Activities.

Attachments

Figure 1, Summary Report - Gaseous and Opacity Excess Emission and Monitoring System Performance

Table H, Permit History