Miami-Dade Water and Sewer Department

North District Wastewater Treatment Plant

Facility ID No.: 0250600

Miami-Dade County

### Title V Air Operation Permit Renewal

PROPOSED Permit Project No.:  0250600-007-AV

Permitting & Compliance Authority:

Florida Department of Environmental Protection

Southeast District Office, Air Program

400 North Congress Avenue, Suite 200

West Palm Beach, Florida, 33401

Telephone:  561-681-6600

Fax:  561-681-6790

#### Title V Air Operation Permit Renewal

PROPOSED Permit No.:  0250600-007-AV

### Table of Contents

Section									Page Number

Placard Page ............................................................................................................... 1

I. Facility Information ................................................................................................2

A. Facility Description.

B. Summary of Emissions Unit ID No(s). and Brief Description(s).

C. Relevant Documents.

II. Facility-wide Conditions .......................................................................................4

III. Emissions Unit(s) and Conditions

Emissions Units Brief Descriptions ...........................................................................8

| 001 | Wastewater Liquid Process (Entire Plant) |
| --- | --- |
| 002 | Diesel Engine Generator EMD model No. 20-645E4B (Unit # 1) |
| 003 | Diesel Engine Generator EMD model No. 20-645E4B (Unit # 2) |
| 004 | Diesel Engine Generator EMD model No. 20-645E4B (Unit # 3) |
| 005 | Diesel Engine Generator EMD model No. 20-645E4B (Unit # 4) |
| 007 | Diesel Engine Generator EMD model No. 16-710G4A (Unit # 6) |
| 008 | Diesel Engine Generator CAT model No. 3612 (Unit # 5) |

Page i

Permittee:					PROPOSED Permit No.:  0250600-007-AV

Miami-Dade Water and Sewer Department	Facility ID No.:  0250600

PO Box 330316					SIC No.:  4952

Miami, FL. 33233-0316				Project: Title V Air Operation Permit 									  Renewal

The purpose of this permit is to renew the Title V Air Operation Permit No. 0250600-005-AV.  This existing facility is located at 2575 NE 156 Street, North Miami, Miami-Dade County; UTM Coordinates:  Zone 17,  584.45 km East,  2866.97 km North and; and, Latitude:  25 55’ 13” North, Longitude: 80 08’ 54” West

This Title V Air Operation Permit Renewal is issued under the provisions of Chapter 403, Florida Statutes (F.S.), and Florida Administrative Code (F.A.C.) Chapters 62-4, 62-210 and 62-213.  The above named permittee is hereby authorized to operate the facility shown on the application and approved drawing(s), plans, and other documents, attached hereto or on file with the permitting authority, in accordance with the terms and conditions of this permit.

Referenced attachments made a part of this permit:

Appendix U-1, List of Unregulated Emissions Units and/or Activities

Appendix I-1, List of Insignificant Emissions Units and/or Activities

APPENDIX TV-6, TITLE V CONDITIONS version dated 06/23/06

Effective Date:  [ARMS Day 55]

Renewal Application Due Date:  Pending

Expiration Date:  Pending

PROPOSED

___________________________    _____________

Jack Long	Date

District Director

Southeast District

# JL/LA/md

Section I.  Facility Information.

Subsection A.  Facility Description.

This facility is a Publicly Owned Treatment Works (POTW), and consists of a wastewater treatment plant for commercial and residential sewage.  The wastewater processes (emissions unit 001), includes primary clarification, oxygenation tanks, and secondary clarifiers.  All liquid process units are covered and vented to an odor control scrubber units for reduction of hydrogen sulfide (H2S), and odors.  The scrubbers do not constitute an air pollution control device; their design is not to reduce VOCs.

The maximum process rate of 49,275 million gallons per year is based on a design treatment capacity of 135 million gallons per day on an annual average basis.  The facility is currently permitted for 112.5 million gallons per day on an annual average basis, and an increase to 120 million gallons per day on annual average basis has been applied for.

Six standby diesel generators supply electricity to the plant in the event of power loss or power curtailment from the Florida Power and Light Co.  Five of these emissions units are manufactured by General Motors Electro-Motive Diesel Division; four of them are model 20-645E4B, and the fifth one is a model 16-710G4A.  Emissions unit 005 according to the applicant is out of service.  The sixth generator is a Caterpillar unit, model 3612.

Also included in this permit are miscellaneous unregulated/insignificant emissions units and/or activities.

Based on the Title V Air Operation Permit Renewal application received April 13, 2009, this facility is a major source of hazardous air pollutants (HAPs).

Subsection B.  Summary of Emissions Unit ID Nos. and Brief Descriptions.

| E.U. ID No. | ## Brief Description |
| --- | --- |
| 002 | Diesel Engine Generator EMD model No. 20-645E4B (Unit # 1) |
| 003 | Diesel Engine Generator EMD model No. 20-645E4B (Unit # 2) |
| 004 | Diesel Engine Generator EMD model No. 20-645E4B (Unit # 3) |
| 005 | Diesel Engine Generator EMD model No. 20-645E4B (Unit # 4) (Out of Service) |
| 007 | Diesel Engine Generator EMD model No. 16-710G4A (Unit # 6) |
| 008 | Diesel Engine Generator CAT model No. 3612 (Unit # 5) |

Unregulated Emissions Units and/or Activities

| E.U. ID No. | Brief Description |
| --- | --- |
| 001 | Wastewater Liquid Process (Entire Plant) |

Please reference the Permit No., Facility ID No., and appropriate Emissions Unit(s) ID No(s). on all correspondence, test report submittals, applications, etc.

Subsection C.  Relevant Documents.

The documents listed below are not a part of this permit; however, they are specifically related to this permitting action.

These documents are provided to the permittee for information purposes only:

Appendix A-1, Abbreviations, Acronyms, Citations, and Identification Numbers

Appendix H-1, Permit History

Statement of Basis

These documents are on file with the permitting authority:

Federal Enforceable Operation Permit issued October 29, 1996

Air Construction Permit issue December 10, 1998

Initial Title V Air Operation Permit issued: September 20, 1999

Administrative Permit Correction issue February 25, 2003

Title V Air Operation Permit Renewal issued March 23, 2004

Administrative Permit Correction issued May 10, 2006

Section II.  Facility-wide Conditions.

The following conditions apply facility-wide:

1.  APPENDIX TV-6, TITLE V CONDITIONS, is a part of this permit.

2.   General Pollutant Emission Limiting Standards.  Objectionable Odor Prohibited.  No person shall cause, suffer, allow, or permit the discharge of air pollutants which cause or contribute to an objectionable odor.

[Rule 62-296.320(2), F.A.C.]

3.  General Particulate Emission Limiting Standards.  General Visible Emissions Standard.

Except for emissions units that are subject to a particulate matter or opacity limit set forth or established by rule and reflected by conditions in this permit, no person shall cause, let, permit, suffer or allow to be discharged into the atmosphere the emissions of air pollutants from any activity, the density of which is equal to or greater than that designated as Number 1 on the Ringelmann Chart (20 percent opacity).  EPA Method 9 is the method of compliance pursuant to Chapter 62-297, F.A.C.

[Rule 62-296.320(4)(b)1. & 4., F.A.C.]

4.  Prevention of Accidental Releases (Section 112(r) of CAA).

a.  As required by Section 112(r)(7)(B)(iii) of the CAA and 40 CFR 68, the owner or operator shall submit an updated Risk Management Plan (RMP) to the Chemical Emergency Preparedness and Prevention Office (CEPPO) RMP Reporting Center.

b. As required under Section 252.941(1)(c), F.S., the owner or operator shall report to the appropriate representative of the Department of Community Affairs (DCA), as established by department rule, within one working day of discovery of an accidental release of a regulated substance from the stationary source, if the owner or operator is required to report the release to the United States Environmental Protection Agency under Section 112(r)(6) of the CAA.

c. The owner or operator shall submit the required annual registration fee to the DCA on or before April 1, in accordance with Part IV, Chapter 252, F.S., and Rule 9G-21, F.A.C.

Any required written reports, notifications, certifications, and data required to be sent to the DCA, should be sent to:

Department of Community Affairs

Division of Emergency Management

2555 Shumard Oak Boulevard

Tallahassee, FL  32399-2100

Telephone:  850/413-9921, Fax:  850/488-1739

Any Risk Management Plans, original submittals, revisions or updates to submittals, should be sent to:

RMP Reporting Center

Post Office Box 1515

Lanham-Seabrook, MD  20703-1515

Telephone:  301/429-5018

Any required reports to be sent to the National Response Center, should be sent to:

National Response Center

EPA Office of Solid Waste and Emergency Response

USEPA (5305 W)

401 M Street, SW

Washington, D.C.  20460

Telephone:  1/800/424-8802

Send the required annual registration fee using approved forms made payable to:

Cashier

Department of Community Affairs

State Emergency Response Commission

2555 Shumard Oak Boulevard

Tallahassee, FL  32399-2149

[Part IV, Chapter 252, F.S.; and, Rule 9G-21, F.A.C.]

5.  Unregulated Emissions Units and/or Activities.  Appendix U-1, List of Unregulated Emissions Units and/or Activities, is a part of this permit.

[Rule 62-213.440(1), F.A.C.]

6.  Insignificant Emissions Units and/or Activities.  Appendix I-1, List of Insignificant Emissions Units and/or Activities, is a part of this permit.

[Rules 62-213.440(1), 62-213.430(6) and 62-4.040(1)(b), F.A.C.]

7.  Compliance Plan.  Based on the application submitted April 13, 2009 emissions unit 005 is out of service and pending an overhaul, the emissions unit 005 was not in compliance at the time of application.  Compliance Plan for this unit is a part of the application.

[Rule 62-213.440(2), F.A.C.]

8.  General Pollutant Emission Limiting Standards. Volatile Organic Compounds (VOC) or Organic Solvents (OS) Emissions.  The permittee shall allow no person to store, pump, handle, process, load, unload or use in any process or installation, volatile organic compounds (VOC) or

organic solvents (OS) without applying known and existing vapor emission control devices or systems deemed necessary and ordered by the Department.

9.  Emissions of Unconfined Particulate Matter.  Pursuant to Rules 62-296.320(4)(c)1., 3. & 4., F.A.C., reasonable precautions to prevent emissions of unconfined particulate matter at this facility include the following requirements (see Condition 57. of APPENDIX TV-6, TITLE V CONDITIONS):

The following requirements are “not federally enforceable”:

- Paving and maintenance of roads, parking areas and yards.

- Application of water or other dust suppressants to control emissions from such activities as demolition of buildings, grading roads, construction, and land clearing.

- Application of asphalt, water, or other dust suppressants to unpaved roads, yards, open stock piles and similar activities.

- Removal of particulate matter from roads and other paved areas under the control of the owner or operator of the facility to prevent reentrainment, and from buildings or work areas to prevent particulate from becoming airborne.

- Landscaping or planting of vegetation.

- Use of hoods, fans, filters, and similar equipment to contain, capture and/or vent particulate matter.

- Confining abrasive blasting where possible.

[Rule 62-296.320(4)(c), F.A.C.]

10.  When appropriate, any recording, monitoring, or reporting requirements that are time-specific shall be in accordance with the effective date of the permit, which defines day one.

[Rule 62-213.440, F.A.C.]

11.  Statement of Compliance.  The annual statement of compliance pursuant to Rule 62-213.440(3)(a)2., F.A.C., shall be submitted to the Department and EPA within 60 (sixty) days after the end of the calendar year using DEP Form No. 62-213.900(7), F.A.C.

[Rules 62-213.440(3) and 62-213.900, F.A.C.]

{Permitting Note:  This condition implements the requirements of Rules 62-213.440(3)(a)2. & 3. F.A.C. (see Condition 51. of APPENDIX TV-6, TITLE V CONDITIONS)}

12.  The permittee shall submit all compliance related notifications and reports required of this permit to the Department’s Southeast District Office.

Department of Environmental Protection

Southeast District Office

400 North Congress Ave, Suite 200

West Palm Beach, Florida 33401

Telephone:  561/681-6600; Fax:  561/681-6790

Local Program:

Miami-Dade County Department of Environmental

Resources Management

Air Section

33 SW 2nd Avenue Suite 9-223

Miami, FL  33130

Telephone: (305) 372-6925

Fax: (305) 372-6954

13.  Any reports, data, notifications, certifications, and requests required to be sent to the United States Environmental Protection Agency, Region 4, should be sent to:

United States Environmental Protection Agency

Region 4

Air, Pesticides & Toxics Management Division

Air and EPCRA Enforcement Branch

Air Enforcement Section

61 Forsyth Street

Atlanta, Georgia  30303-8960

Telephone:  404/562-9155; Fax:  404/562-9163

14.  Certification by Responsible Official (RO).  In addition to the professional engineering certification required for applications by Rule 62-4.050(3), F.A.C., any application form, report, compliance statement, compliance plan and compliance schedule submitted pursuant to Chapter 62-213, F.A.C., shall contain a certification signed by a responsible official that, based on information and belief formed after reasonable inquiry, the statements and information in the document are true, accurate, and complete.  Any responsible official who fails to submit any required information or who has submitted incorrect information shall, upon becoming aware of such failure or incorrect submittal, promptly submit such supplementary information or correct information.

[Rule 62-213.420(4), F.A.C.]

15. Annual Operating Report Required:  A completed DEP Form 62-210.900(5), Annual Operating Report for Air Pollution Emitting Facility, shall be submitted to the Department of Environmental Protection, Southeast District Office Air Program. The report shall be submitted by April 1st.  Included with this report shall be additional reports, if any, required by this permit in Part III -- Emission Unit Specific Conditions.

[Rule 62-210.370(3), F.A.C.]

Section III.  Emissions Units and Conditions.

Subsection A.  This section addresses the following emissions units.

| E.U. ID No. |  | Brief Description |
| --- | --- | --- |
| 002 | Diesel Engine Generator EMD model No. 20-645E4B (Unit # 1) |  |  |
| 003 | Diesel Engine Generator EMD model No. 20-645E4B (Unit # 2) |  |  |
| 004 | Diesel Engine Generator EMD model No. 20-645E4B (Unit # 3) |  |  |
| 005 | Diesel Engine Generator EMD model No. 20-645E4B (Unit # 4) (Out of Service) |  |  |
| 007 | Diesel Engine Generator EMD model No. 16-710G4A (Unit # 6) |  |  |
| 008 | Diesel Engine Generator CAT model No. 3612 (Unit # 5) |  |  |

All EMD Model 20-645E4 are prime movers manufactured by General Motors Electro Motive Division, each coupled to a 2,500 kW generator.  These prime movers are turbocharged diesel-fueled reciprocating internal combustion engines that operate at 900 rpm.  These units began commercial operation on January 1, 1979.

The Model No. 16-710G4A is a prime mover turbocharged diesel fueled reciprocating internal combustion engine manufactured by General Motors Electro Motive Division that operates at 900 rpm and is coupled to a 2,700 kW generator.  Commercial operation for this unit began January 5, 1995.

The CAT Model 3612 is a prime mover turbocharged diesel fueled reciprocating internal combustion engine manufactured by Caterpillar that operates at 900 rpm and is coupled to a 3,300 kW generator.  This unit began operation January 6, 1997.

The power output for all generators is 16 Megawatts.  These emissions units are regulated as a group and they shared a fuel limit of 7000,000 gallons diesel fuel per year.

The following specific conditions apply to the emissions units listed above:

Essential Potential to Emit (PTE) Parameters

A.1. Methods of Operation - (i.e., Fuels). These emissions units shall burn only No. 2 diesel fuel oil with sulfur content not to exceed 0.05 percent by weight.  The consumption of diesel fuel for the above reference emissions units combined shall not exceed 700,000 gallons per year in any consecutive 365-day period.

[Rule 62-213.410, F.A.C., and requested by applicant on the Initial and renewal application to escape PSD applicability based on NOx emission of 229.43 tpy]

A.2. Hours of Operation.  These emissions units are allowed to operate continuously, i.e., 8,760 hours/year.

[Rule 62-210.200(PTE), F.A.C.]

Emission Limitations and Standards

A.3. Nitrogen Oxide (NOx) Emissions. NOx emissions from each of the emission units 002-005 and 007-008 shall not exceed 4.75 lbs/MMBtu heat input, and NOx emissions for all generators combined shall not exceed 229.43 ton per year.

[Rule 62-296.570(4)(b)7, F.A.C., and requested in the renewal application dated April 13, 2009]

Test Methods and Procedures

A.4.  Nitrogen Oxide (NOx) Emission Tests: Compliance with the emission limits for NOx shall be demonstrated each federal fiscal year (Oct.1-Sept. 30) by using EPA Method 7 or 7E, as described in 40 CFR 60, Appendix A, adopted by reference in Rule 62-297.401, F.A.C.

[Rule 62-297.401, F.A.C]

A.5. Annual compliance testing while firing diesel fuel oil is unnecessary for units operating on diesel fuel oil for less than 400 hours in the current federal fiscal year.

[Rule 62-296.570(4)3, F.A.C.]

Monitoring of Operations

A.6. Fuel Consumption: The owner or operator shall monitor fuel consumption for the above referenced emissions units by metering the fuel between the storage tank and the bank of generators, and at the fuel return line between the emissions units and the main storage tanks whenever any one of these emissions units are in operation.

[Rule 62-4.070(3), F.A.C., and Permit No. 0250600-003-AC]

A.7. Meter Fuel Calibration: Calibration of the fuel meters shall be conducted in accordance with manufacturer’s schedule and recommendation.  All calibration data shall be maintained at the facility physical location for inspection.

[Rule 62-4.070(3), F.A.C.]

A.8. Diesel Fuel Sulfur Content Certification:  For each load of fuel delivered to the facility, the permittee shall either:

a. Obtain a copy of the fuel analysis from the supplier.  Methods for determining the fuel sulfur content of the distillate oil shall be ASTM Method D 129-91, D 1552-95, D 2622-94, D 4294-98 or comparable Department approved method.  Records shall specify the test method used. Or,

b. Collect a fuel sample to be sent for laboratory analysis based on one of the following method: ASTM Method D 129-91, D 1552-95, D 2622-94, D 4294-98 or comparable Department approved method.

c. Records from the fuel supplier that indicates the fuel delivered is Low Sulfur No. 2 Diesel fuel oil by ASTM Method 975-98b, or current version.  Specification for Diesel Fuel Oils provides for this classification of diesel fuel oils as having no more than 0.05 percent (500 ppm) sulfur content by weight.

[Rule 62-4.070(3), F.A.C., and requested in the renewal application dated April 13, 2009]

Recordkeeping and Reporting Requirements

A.9.   From the daily records of diesel fuel usage the permittee shall record and maintain a rolling 365-day total of the amount of fuel consumed by the generators.  This rolling 365-day total record shall be updated each day.  These records shall be used to demonstrate compliance with the fuel limitation. If the fuel consumption of all emission units combined does not exceed 525,000 gallons of diesel fuel at the end of any consecutive 365-day period; the permittee may make and maintain records of the fuel consumption for these emission units once every seven days instead of at the end of each day.  Daily consumption recording shall resume upon the weekly 365-day total exceeding 525,000 gallons of diesel fuel.

[Rule 62-4.070(3), F.A.C., and requested in the renewal application dated April 13, 2009]

A.10. Copies of the fuel supplier certifications shall be maintained at the facility physical location for inspection.

[Rule 62-4.070(3), F.A.C.]

A.11. All records required under this section shall be maintained by the owner or operator of the affected facility for a period of five (5) years following the date of such record, and shall be available for inspection at the facility physical location.

[Rule 62-4.070(3), F.A.C.]

A.12. AOR Supplemental Information:  Annual operating reports shall include the following supplemental information that was recorded in the previous calendar year:

- The highest sulfur percentage in the fuel received.

- The highest 365-day total diesel fuel usage for the generators.

[Rule 62-4.070(3), F.A.C.]  EXAMPLES: