# JEA

# Brandy Branch Generating Station

# Facility ID No. 0310485

# Duval County

#### Title V Air Operation Permit Renewal

#### Permit No. 0310485-023-AV

(Renewal of Title V Air Operation Permit No. 0310485-020-AV)

# Permitting Authority:

State of Florida

Department of Environmental Protection

Division of Air Resource Management

Office of Permitting and Compliance

2600 Blair Stone Road

Mail Station #5505

Tallahassee, Florida  32399-2400

# Telephone:  (850) 717-9000

Email:  DARM_Permitting@dep.state.fl.us

# Compliance Authority:

Department of Environmental Protection

Northeast District Office

8800 Baymeadows Way West

Jacksonville, Florida  32256

Telephone:  (904) 256-1700

Title V Air Operation Permit Renewal

Permit No. 0310485-023-AV

Table of Contents

Section	Page Number

Placard Page 	 1

I.	Facility Information.

A.	Facility Description. 	 2

B.	Summary of Emissions Units. 	 2

C.	Applicable Regulations. 	 2

II.	Facility-wide Conditions. 	 4

III.	Emissions Units and Conditions.

A.	EU No. 001.  Simple-Cycle Combustion Turbine-Electrical Generator. 	 7

B.	EU Nos. 002 and 003.  Two Combined-Cycle Combustion Turbine Electric Generators. 	 14

C.	EU No. 008.  One Emergency Diesel-Fueled Fire Pump Engine. 	 24

IV.	Acid Rain Part. 	 28

Phase II Acid Rain Application/Compliance Plan.

V.	Appendices. 	 Attached

Appendix A, Glossary.

Appendix I, List of Insignificant Emissions Units and/or Activities.

Appendix NESHAP Subpart A, General Provisions.

Appendix NESHAP Subpart ZZZZ, NESHAP for Stationary Reciprocating Internal Combustion Engines.

Appendix NSPS Subpart A, General Provisions.

Appendix NSPS Subpart GG, Standards of Performance for Stationary Gas Turbines.

Appendix RR, Facility-wide Reporting Requirements.

Appendix TR, Facility-wide Testing Requirements.

Appendix TV, Title V General Conditions.

Appendix U, List of Unregulated Emissions Units and/or Activities.

Referenced Attachments. 	 At End of Appendices Document

Figure 1, Summary Report-Gaseous and Opacity Excess Emission and

Monitoring System Performance (40 CFR 60, July 1996).

Table H, Permit History.

| Permittee: JEA Brandy Branch Generating Station 15701 West Beaver Street Baldwin, Florida 32234 | Permit No. 0310485-023-AV Brandy Branch Generating Station Facility ID No. 0310485 Title V Air Operation Permit Renewal |
| --- | --- |

The purpose of this permit is to renew the Title V air operation permit for the above referenced facility.  The existing Brandy Branch Generating Station is in Duval County at 15701 West Beaver Street, Baldwin, Florida.  UTM Coordinates are:  Zone 17, 408.91 kilometers (km) East and 3354.64 km North.  Latitude is:  30° 19’ 15.899” North; and, Longitude is:  81° 56’ 51.176” West.

The Title V air operation permit is issued under the provisions of Chapter 403, Florida Statutes (F.S.), and Florida Administrative Code (F.A.C.) Chapters 62-4, 62-210, 62-213 and 62-214.  The above named permittee is hereby authorized to operate the facility in accordance with the terms and conditions of this permit.

Executed in Tallahassee, Florida.

0310485-020-AV Effective Date:  January 1, 2014

0310485-023-AV Effective Date:  October 29, 2018

Renewal Application Due Date:  March 18, 2023

Expiration Date:  October 29, 2023

For:  Syed Arif, P.E., Program Administrator

Office of Permitting and Compliance

Division of Air Resource Management

SA/dlr/jpd

Subsection A.  Facility Description.

This facility consists of three dual-fuel, nominal 170 megawatt (MW) General Electric model PG7241FA combustion turbine-electrical generators and two one-million-gallon capacity fuel oil storage tanks.  Two of the combustion turbines (EU Nos. 002 and 003) are configured for combined-cycle mode and one (EU 001) for simple-cycle operation.  Emissions from the units are controlled by Dry Low Nitrogen Oxides (NOX) (DLN-2.6) combustors when operating on natural gas and wet injection when firing fuel oil.  For the combined cycle units, selective catalytic reduction (SCR) systems are additionally utilized for further NOX reductions.  Inherently clean fuels and good combustion practices are employed to control all pollutants.

Subsection B.  Summary of Emissions Units.

| EU No. | ## Brief Description |
| --- | --- |
| Regulated Emissions Units |  |
| 001 | Simple-Cycle Combustion Turbine-Electrical Generator |
| 002 | Combined-Cycle Combustion Turbine-Electrical Generator with supplementary-fired Heat Recovery Steam Generator (HRSG) |
| 003 | Combined Cycle Combustion Turbine-Electrical Generator with supplementary-fired HRSG |
| 008 | Emergency Diesel-Fueled Fire Pump Engine |
| Unregulated Emissions Units |  |
| 007 | Water Cooling - One Fresh Water Mechanical Draft Cooling Tower |

Also included in this permit are miscellaneous insignificant emissions units and/or activities (see Appendix I, List of Insignificant Emissions Units and/or Activities).

Subsection C.  Applicable Regulations.

Based on the Title V air operation permit renewal application received May 17, 2018, this facility is not a major source of hazardous air pollutants (HAP).  The existing facility is a prevention of significant deterioration (PSD) major source of air pollutants in accordance with Rule 62-212.400, F.A.C.  A summary of applicable regulations is shown in the following table.

| Regulation | ## EU No(s). |
| --- | --- |
| Federal Rule Citations |  |
| 40 CFR 60, Subpart A, NSPS General Provisions | 001, 002, 003 |
| 40 CFR 60, Subpart GG, Standards of Performance for Stationary Gas Turbines | 001, 002, 003 |
| 40 CFR 63, Subpart A, General Provisions | 008 |
| 40 CFR 63, Subpart ZZZZ, NESHAP for Stationary Reciprocating Internal Combustion Engines | 008 |
| 40 CFR 75 Acid Rain Monitoring Provisions | 001, 002, 003 |

| Regulation | EU No(s). |
| --- | --- |
| State Rule Citations |  |
| Chapter 62-4, Florida Administrative Code (F.A.C.) (Permitting Requirements) | 001, 002, 003, 007, 008 |
| Chapter 62-204, F.A.C. (Ambient Air Quality Requirements, PSD Increments, and Federal Regulations Adopted by Reference) | 001, 002, 003, 007, 008 |
| Chapter 62-210, F.A.C. (Permits Required, Public Notice, Reports, Stack Height Policy, Circumvention, Excess Emissions, and Forms) | 001, 002, 003, 007, 008 |
| Chapter 62-212, F.A.C. (Preconstruction Review, PSD Review and Best Available Control Technology (BACT)) | 001, 002, 003, 007, 008 |
| Chapter 62-213, F.A.C. (Title V Air Operation Permits for Major Sources of Air Pollution) | 001, 002, 003, 007, 008 |
| Chapter 62-214, F.A.C. (Requirements For Sources Subject To The Federal Acid Rain Program) | 001, 002, 003 |
| Chapter 62-296, F.A.C. (Emission Limiting Standards) | 001, 002, 003, 008 |
| Chapter 62-297, F.A.C. (Test Methods and Procedures, Continuous Monitoring Specifications, and Alternate Sampling Procedures) | 001, 002, 003, 008 |

Table of Contents

The following conditions apply facility-wide to all emission units and activities:

- Appendices.  The permittee shall comply with all documents identified in Section V, Appendices, listed in the Table of Contents.  Each document is an enforceable part of this permit unless otherwise indicated.  [Rule 62-213.440, F.A.C.]

Emissions and Controls

- Not federally Enforceable.  Objectionable Odor Prohibited.  No person shall cause, suffer, allow or permit the discharge of air pollutants, which cause or contribute to an objectionable odor.  An “objectionable odor” means any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance.  [Rule 62-296.320(2) and 62-210.200(Definitions), F.A.C.]

- General Volatile Organic Compounds (VOC) Emissions or Organic Solvents (OS) Emissions.  The permittee shall allow no person to store, pump, handle, process, load, unload or use in any process or installation, volatile organic compounds or organic solvents without applying known and existing vapor emission control devices or systems deemed necessary and ordered by the Department.  [Rule 62-296.320(1), F.A.C.]

{Permitting Note:  Nothing is deemed necessary and ordered at this time.}

- General Visible Emissions.  No person shall cause, let, permit, suffer or allow to be discharged into the atmosphere the emissions of air pollutants from any activity equal to or greater than 20% opacity.  This regulation does not impose a specific testing requirement.  [Rule 62-296.320(4)(b), F.A.C.]

- Unconfined Particulate Matter.  No person shall cause, let, permit, suffer or allow the emissions of unconfined particulate matter from any activity, including vehicular movement; transportation of materials; construction; alteration; demolition or wrecking; or industrially related activities such as loading, unloading, storing or handling; without taking reasonable precautions to prevent such emissions.  Reasonable precautions to prevent emissions of unconfined particulate matter at this facility include:

  - Paving of roads, parking areas, and equipment yards.

  - Landscaping and planting of vegetation.

  - Maintenance of paved areas as needed.

  - Regular mowing of grass and care of vegetation.

  - Limiting access to plant property of unnecessary vehicles.

[Rule 62-296.320(4)(c), F.A.C.; and, proposed by applicant in Title V air operation permit renewal application received May 17, 2018]

Reports and Fees

See Appendix RR, Facility-wide Reporting Requirements, for additional details and requirements.

- Electronic Annual Operating Report and Title V Annual Emissions Fees.  The information required by the Annual Operating Report for Air Pollutant Emitting Facility [Including Title V Source Emissions Fee Calculation] (DEP Form No. 62-210.900(5)) shall be submitted by April 1 of each year, for the previous calendar year, to the Department of Environmental Protection’s Division of Air Resource Management.  Each Title V source shall submit the annual operating report using the DEP’s Electronic Annual Operating Report (EAOR) software, unless the Title V source claims a technical or financial hardship by submitting DEP Form No. 62-210.900(5) to the DEP Division of Air Resource Management instead of using the reporting software. Emissions shall be computed in accordance with the provisions of subsection 62-210.370(2), F.A.C.  Each Title V source must pay between January 15 and April 1 of each year an annual emissions fee in an amount determined as set forth in subsection 62-213.205(1), F.A.C.  The annual fee shall only apply to those regulated pollutants, except carbon monoxide and greenhouse gases, for which an allowable numeric emission-limiting standard is specified in the source’s most recent construction permit or operation permit.  Upon completing the required EAOR entries, the EAOR Title V Fee Invoice can be printed by the source showing which of the reported emissions are subject to the fee and the total Title V Annual Emissions Fee that is due.  The submission of the annual Title V emissions fee payment is also due (postmarked) by April 1st of each year.  A copy of the system-generated EAOR Title V Annual Emissions Fee Invoice and the indicated total fee shall be submitted to:  Major Air Pollution Source Annual Emissions Fee, P.O. Box 3070, Tallahassee, Florida  32315-3070.  Additional information is available by accessing the Title V Annual Emissions Fee On-line Information Center at the following Internet web site:  https://floridadep.gov/air/permitting-compliance/content/title-v-fees.  [Rules 62-210.370(3), 62-210.900 & 62-213.205, F.A.C.; and, §403.0872(11), Florida Statutes (2013)]

{Permitting Note:  Resources to help you complete your AOR are available on the electronic AOR (EAOR) website at:  http://www.dep.state.fl.us/air/emission/eaor.  If you have questions or need assistance after reviewing the information posted on the EAOR website, please contact the Department by phone at (850) 717-9000 or email at eaor@dep.state.fl.us.}

{Permitting Note:  The Title V Annual Emissions Fee form (DEP Form No. 62-213.900(1)) has been repealed.  A separate Annual Emissions Fee form is no longer required to be submitted by March 1st each year.}

- Annual Statement of Compliance.  The permittee shall submit an annual statement of compliance to the compliance authority at the address shown on the cover of this permit and to the US. EPA at the address shown below within 60 days after the end of each calendar year during which the Title V air operation permit was effective.  (See also Appendix RR, Conditions RR1 and RR7.)  [Rules 62-213.440(3)(a)2. & 3. and (b), F.A.C.]

U.S. Environmental Protection Agency, Region 4

Atlanta Federal Center

61 Forsyth Street, SW

Atlanta, Georgia  30303

Attn:  Air Enforcement Branch

FW9.	Prevention of Accidental Releases (Section 112(r) of CAA).  If, and when, the facility becomes subject to 112(r), the permittee shall:

a.	Submit its Risk Management Plan (RMP) to the Chemical Emergency Preparedness and Prevention Office (CEPPO) RMP Reporting Center.  Any Risk Management Plans, original submittals, revisions or updates to submittals, should be sent electronically through EPA’s Central Data Exchange system at the following address:  https://cdx.epa.gov.  Information on electronically submitting risk management plans using the Central Data Exchange system is available at:  http://www2.epa.gov/rmp.  The RMP Reporting Center can be contacted at:  RMP Reporting Center, Post Office Box 10162, Fairfax, VA  22038, Telephone:  (703) 227-7650.

b.	Submit to the permitting authority Title V certification forms or a compliance schedule in accordance with Rule 62-213.440(2), F.A.C.

[40 CFR 68]

- Semi-Annual Reports.  The permittee shall monitor compliance with the terms and conditions of this permit and shall submit reports at least every six months to the compliance office.  Each semi-annual report shall cover the 6-month periods of January 1 – June 30 and July 1 – December 31.  The reports shall be submitted by the 60th day following the end of each calendar half (i.e., March 1st and August 29th of every year).  All instances of deviations from permit requirements (including conditions in the referenced Appendices) must be clearly identified in such reports, including reference to the specific requirement and the duration of such deviation.  If there are no deviations during the reporting period, the report shall so indicate.  Any semi-annual reporting requirements contained in applicable federal NSPS or NESHAP requirements may be submitted as part of this report.  The submittal dates specified above shall replace the submittal dates specified in the federal rules.  All additional reports submitted as part of this report should be clearly identified according to the specific federal requirement.  All reports shall include a certification by a responsible official, pursuant to subsection 62-213.420(4), F.A.C.  (See also Conditions RR2. – RR4. of Appendix RR, Facility-wide Reporting Requirements, for additional reporting requirements related to deviations.)  [Rule 62-213.440(1)(b)3.a., F.A.C.; and, 40 CFR 60.19, 40 CFR 61.10 & 40 CFR 63.10]

{Permitting Note:  EPA has clarified that, pursuant to 40 CFR 70.6(a)(3), the word “monitoring” is used in a broad sense and means monitoring (i.e., paying attention to) the compliance of the source with all emissions limitations, standards, and work practices specified in the permit.}

Table of Contents

The specific conditions in this section apply to the following emissions unit:

| EU No. | Brief Description |
| --- | --- |
| 001 | Simple-Cycle Combustion Turbine-Electrical Generator |

This emissions unit is one nominal 170-MW simple-cycle combustion turbine (CT) (Make/Model: General Electric PG7241FA), with a 90-foot exhaust stack.  Natural gas is the primary fuel, with low-sulfur distillate fuel oil as the back-up fuel.  NOX emissions are controlled by dry low NOX (DLN) combustors, and a water injection system for use when firing No. 2 or superior grade distillate fuel oil.  The stationary combustion turbine, ducting, and stack is designed so as to not preclude installation of SCR equipment and/or oxidation catalyst equipment in the event of a failure to achieve the NOX limits or the carbon monoxide (CO) limits.  Compliance Assurance Monitoring (CAM) does not apply to this emissions unit.  Start-up date was April 20, 2001.

{Permitting note:  This emissions unit is regulated under:  Acid Rain-Phase II, 40 CFR 60, Subpart GG, Standards of Performance for Stationary Gas Turbines, adopted by reference in Rule 62-204.800(7)(b), F.A.C.; Rule 212.400, F.A.C., Prevention of Significant Deterioration (PSD); Best Available Control Technology (BACT); Air Construction Permit No. 0310485-001-AC/PSD-FL-267 and amendments (A thru D); and, Power Plant Siting Project No. PA 00-43.  The CT began commercial operation on April 20, 2001.  Stack height = 90 feet, exit diameter = 18.0 feet, exit temperature = 1,116 ºF, actual volumetric flow rate = 2,393,300 acfm.}

Essential Potential to Emit (PTE) Parameters

- Permitted Capacity.  The maximum allowable heat input rates, based on the lower heating value (LHV) of each fuel at ambient conditions of 59°F temperature, 60% relative humidity, 100% load, and 14.7 psi pressure shall not exceed the following when firing the corresponding type of fuel:

| Unit No. | MMBtu/hr Heat Input | Fuel Type |
| --- | --- | --- |
| 001 | 1,623 | Natural Gas |
|  | 1,822 | No. 2 or superior grade of distillate fuel oil |

These maximum heat input rates will vary depending upon ambient conditions and the combustion turbine characteristics.  Manufacturer’s curves corrected for site conditions or equations for correction to other ambient conditions have been provided to the Department and shall be re-submitted within 45 days of re-establishing the curves due to a compliance test or combustor major tuning session.

{Permitting Note:  The heat input limitations have been placed in the permit to identify the capacity of each emissions unit for purposes of confirming that emissions testing is conducted within 90 – 100 percent of the emissions unit’s rated capacity (or to limit future operation to 110 percent of the test load), to establish appropriate limits and to aid in determining future rule applicability.  Regular record keeping is not required for heat input whenever emission testing is required, to demonstrate at what percentage of the rated capacity that the unit was tested.  Rule 62-297.310(5), F.A.C., included in this permit requires measurement of the process variables for emission tests.  Such heat input determinations may be based on measurements of fuel consumption by various methods (including by not limited) fuel flow metering or tank drop measurements, using the heat value of the fuel determining by the vendor or operator to calculate average hourly heat input during the test.}

[Rules 62-4.160(2), F.A.C., 62-204.800, F.A.C., 62-210.200(Definitions - PTE), F.A.C., 62-213.440(1), F.A.C., and Permit No. PSD-FL-267/0310485-001-AC, Specific Condition 8.]

- Emissions Unit Operating Rate Limitation After Testing.  See the related testing provisions in Appendix TR, Facility-wide Testing Requirements.  [Rule 62-297.310(3), F.A.C.]

- Methods of Operation – Fuels.  Only natural gas or No. 2 or superior grade distillate fuel oil with a sulfur content no greater than 0.0015% by weight shall be fired.  [Rules 62-210.200(Definitions-PTE), F.A.C.; and Permit No. PSD-FL-267/0310485-001-AC, Specific Condition 7.; 0310485-021-AC, Specific Condition 2.]

{Permitting Note:  The limitation of this specific condition is more stringent than the NSPS sulfur dioxide limitation and thus assures compliance with 40 CFR 60.333 and 60.334.}

- Hours of Operation.  This unit may operate up to 4,750 hours during any consecutive twelve-month period, of which 750 hours of operation per combustion turbine may be while firing fuel oil.  [Rule 62-210.200(Definitions - PTE), F.A.C.; and, Permit No. PSD-FL-267/0310485-001-AC, Specific Condition 13.; 0310485-021-AC, Specific Condition 2.]

Control Technology

- Control Equipment.  Consistent with best operation and maintenance practices, the DLN systems shall each be tuned to optimize emissions reductions and shall be maintained to minimize NOX emissions and CO emissions.  Operation of the DLN systems in the diffusion-firing mode shall be minimized when firing natural gas.  A water injection system shall be installed for use when firing fuel oil for control of NOX emissions.  [Rule 62-4.070, F.A.C.; and, Permit No. PSD-FL-267/0310485-001-AC, Specific Conditions 18 and 19]

Emission Limitations and Standards

Unless otherwise specified, the averaging times for Specific Conditions A.6.-A.11. are based on the specified averaging time of the applicable test method.

- Nitrogen Oxides (NOX).

- Data Substitution.  For the sole purpose of Acid Rain reporting, when NOX monitoring data are not available, substitution for missing data shall be handled as required by Title IV (40 CFR 75).

- While firing Natural Gas.  The emission rate of NOX in the exhaust gas shall not exceed 10.5 ppmvd corrected to 15% O2 on a 24 hr block average as measured by the continuous emission monitoring system (CEMS).  In addition, NOX emissions calculated as NO2 (at ISO conditions) shall not exceed 10.5 ppmvd @ 15% O2 to be demonstrated by annual stack test.

- While firing Fuel Oil.  The concentration of NOX in the exhaust gas shall not exceed 42 ppmvd at 15% O2 on the basis of a 3-hr block average basis as measured by the continuous emission monitoring system (CEMS).  In addition, NOX emissions calculated as NO2 (at ISO conditions) shall not exceed 42 ppmvd @ 15% O2 to be demonstrated by stack test.

- After Firing Fuel Oil For 400 Hours.  After combusting fuel oil for at least 400 hours on any individual combustion turbine (CT), the permittee shall prepare and submit for the DEP’s review and acceptance an engineering report regarding the lowest NOX emission rate that can consistently be achieved when firing distillate oil.  This lowest recommended rate shall include a reasonable operating margin, taking into account long-term performance expectations and good operating and maintenance practices.  The DEP may revise the NOX emission rate based upon this report.

[Rule 62-212.400, F.A.C.; and, Permit No. PSD-FL-267/0310485-001-AC, Specific Condition 21; 0310485-021-AC, Specific Condition 2]

- Carbon Monoxide (CO).  The concentration of CO in the exhaust gas shall not exceed 15 ppmvd when firing natural gas and 20 ppmvd when firing fuel oil as measured by EPA Method 10.  CO emissions shall not exceed 48.0 lbs/hr (when firing natural gas) and 65.0 lbs/hr (when firing fuel oil) as indicated by EPA Method 10.  [Rule 62-212.400, F.A.C.; Permit No. PSD-FL-267/0310485-001-AC, Specific Condition 22]

- Sulfur Dioxide (SO2) and Sulfuric Acid Mist (SAM).  SO2 and SAM emissions shall be limited by firing natural gas (sulfur content not greater than 2 grains per 100 standard cubic feet) and 0.0015% sulfur content, by weight, fuel oil.  Compliance with this requirement in conjunction with implementation of the Custom Fuel Monitoring Schedule in Specific Conditions A.18. and A.26. will demonstrate compliance with the applicable NSPS SO2 emissions limitations from the combustion turbine.  [40 CFR 60 Subpart GG; Rules 62-4.070, 62-212.400, and 62-204.800(7), F.A.C.; BACT; and, Permit No. 0310485-004-AC, Specific Condition 23 (as revised in permit modification letter dated 4/12/01); 0310485-021-AC, Specific Condition 4]

{Permitting Note:  The fuel sulfur limitations for the three turbines effectively limit the combined SO2 emissions for EU001, EU002 and EU003 to 117 TPY.}

- Visible emissions (VE).  VE emissions shall not exceed 10 percent opacity when firing natural gas or No. 2 or superior grade of fuel oil.  [Permit No. PSD-FL-267/0310485-001-AC, Specific Condition 24]

- Particulate Matter (PM).  PM emissions shall not exceed 9.0 lbs/hr (front catch) while firing natural gas and 17.0 lbs/hr (front catch) while firing fuel oil as indicated by opacity.  [Permit No. PSD-FL-267/0310485-001-AC, Specific Condition 24]

- Volatile Organic Compounds (VOC).  The concentration of VOC in the exhaust gas shall not exceed 2 ppmvd when firing natural gas and 3.5 ppmvd when firing fuel oil as assured by EPA Methods 18 and/or 25A.  VOC emissions (at ISO conditions) shall not exceed 4.0 lb/hr (when firing natural gas) and 7.5 lb/hr (when firing fuel oil) as indicated by EPA Methods 18 and/or 25A.  (See Specific Condition A.28.)  [Permit No. PSD-FL-267/0310485-001-AC, Specific Condition 25]

- Operating Procedures.  Operating procedures shall include good operating practices and proper training of all operators and supervisors.  The good operating practices shall meet the guidelines and procedures as established by the equipment manufacturers.  All operators (including supervisors) of air pollution control devices shall be properly trained in plant specific equipment.  [Rule 62-4.070(3), F.A.C.; and, 0310485-001-AC, Specific Condition 11]

Excess Emissions

Rule 62-210.700 (Excess Emissions), F.A.C. cannot vary any requirement of an NSPS, NESHAP or Acid Rain program provision.

- Definitions. The following definitions apply:

  - Startup.  Startup is defined as the commencement of operation of any emissions unit which has shut down or ceased operation for a period of time sufficient to cause temperature, pressure, chemical or pollution control device imbalances.  [Rule 62-210.200(246), F.A.C.]

  - Shutdown.  Shutdown is defined as the cessation of the operation of an emissions unit for any purpose.  [Rule 62-210.200(233), F.A.C.]

  - Malfunction.  Malfunction is defined as any unavoidable mechanical and/or electrical failure of air pollution control equipment or process equipment or of a process resulting in operation in an abnormal or unusual manner.  [Rule 62-210.200(155), F.A.C.]

- Excess Emissions Allowed.  Excess emissions resulting from startup, shutdown or malfunction of any emissions unit shall be permitted provided:

  - Best operational practices are adhered to and the duration of excess emissions shall be minimized, but in no case exceed two hours (120 minutes) in any 24-hour period for other reasons, unless specifically authorized by the Department for longer duration.

  - Operation below 62 gross megawatts while firing fuel oil and/or natural gas shall be limited to 2 hours per unit cycle (breaker closed to breaker open).

[Rule 62-210.700(1), F.A.C.; Permit No. PSD-FL-267/0310485-001-AC, Specific Condition 26; Permit No. 0310485-010-AC (revision dated 1/18/2005); 0310485-021-AC, Specific Condition 6]

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C.]

- CEMS Data Exclusion for DLN Tuning.  NOX emissions data recorded via CEMS that is collected during initial or other major Dry-Low NOX (DLN) tuning sessions may be excluded from demonstrations of compliance with the state-issued concentration-based NOX limits, provided the tuning session is performed in accordance with the manufacturer’s specifications or industry standards. NOX emissions data recorded during DLN combustor tuning shall not be excluded from annual emissions reports and demonstrations of compliance with any NSPS provisions. A “major DLN tuning session” occurs after one or more of the following circumstances:

- Combustor change-outs

- Major repairs or maintenance to a combustor

- Other similar circumstances

Prior to performing any major tuning session, the permittee shall provide the Compliance Authority with an advance notice of at least one day, detailing the activity and proposed tuning schedule.  The notice may be by telephone or electronic mail.

[Rule 62-210.700(4), F.A.C.; Permit No. 0310485-025-AC/PSD-FL-267D]

- CEMS Data Exclusion for FSNL Testing:  As a periodic maintenance practice, the permittee may perform full-speed no-load (FSNL) tests the with CT generator in accordance with the manufacturer’s recommendations or industry standards.  NOX emissions data gathered during periods of FSNL testing may be excluded from demonstrations of compliance with the state-issued concentration-based NOX limits.  NOX emissions data recorded during FSNL testing shall not be excluded from annual emissions reports and demonstrations of compliance with any NSPS provisions.  [Rule 62-210.700(4), F.A.C.; Permit No. 0310485-025-AC/PSD-FL-267D]

Monitoring of Operations

- Natural Gas Monitoring Schedule.  The following custom monitoring schedule for natural gas is approved in lieu of the daily sampling requirements of 40 CFR 60 Subpart GG:

- Each unit shall be monitored for SO2 emissions using methods consistent with the requirements of 40 CFR 75 and certified by the US EPA.

- The owner or operator shall notify the Permitting and Compliance Authorities of any change in natural gas supply for reexamination of this monitoring schedule.  A substantial change in natural gas quality (i.e., sulfur content variation of greater than 1 grain per 100 standard cubic feet of natural gas) shall be considered as a change in the natural gas supply.  Sulfur content of the natural gas will be monitored weekly by the natural gas supplier during the interim period when this monitoring schedule is being reexamined.

[Permit No. PSD-FL-267/0310485-001-AC, Specific Condition 45; and, 40 CFR 60.334(h)(3)]

{Permitting Note:  Under Subpart GG, monitoring of the total sulfur content of the gaseous fuel combusted is not required if pipeline-supplied natural gas is used.}

Continuous Emissions Monitoring Requirements

- Continuous Monitoring System (CEMS).  The permittee shall calibrate, maintain, and operate a continuous emission monitor in the stack to measure and record the nitrogen oxides emissions from the CT unit.  Periods when NOX emissions are above the standards as listed in Specific Condition A.6., shall be reported to the Compliance Authority office pursuant to Rule 62-4.160(8), F.A.C.  Following the format of 40 CFR 60.7, periods of startup, shutdown and malfunction shall be monitored, recorded, and reported as excess emissions when emission levels exceed the standards listed in Specific Condition A.6., except as noted in Specific Conditions A.16., A.17., and A.25.  [Rule 62-204.800, F.A.C.; 40 CFR 60.7; and, Permit No. PSD-FL-267/0310485-001-AC, Specific Condition 41]

- CEMS in lieu of Water to Fuel Ratio.  The NOX CEMS shall be used in lieu of the water/fuel monitoring system for reporting excess emissions in accordance with 40 CFR 60, Subpart GG.  The calibration of the water/fuel-monitoring device required in 40 CFR 60 Subpart GG will be replaced by the 40 CFR 75 certification tests of the NOX CEMS.  Upon request from the Compliance Authority office, the CEMS emission rates for NOX shall be corrected to ISO conditions to demonstrate compliance with the NOX standard established in 40 CFR 60 Subpart GG.  [40 CFR 60.334(b)]

- Continuous Monitoring System Reports.  The monitoring devices shall comply with the certification and quality assurance, and any other applicable requirements of 40 CFR 60.13, including certification of each device in accordance with 40 CFR 60, Appendix B, Performance Specifications, and 40 CFR 60.7(a)(5) or 40 CFR 75.  Quality assurance procedures must conform to all applicable sections of 40 CFR 60, Appendix F, or 40 CFR 75.  [Permit No. PSD-FL-267/0310485-001-AC, Specific Condition 43]

Test Methods and Procedures

- Test Methods.  When required, tests shall be performed in accordance with the following reference methods:

| Method | Description of Method and Comments |
| --- | --- |
| 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| 7E | Determination of Nitrogen Oxide Emissions from Stationary Sources |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |
| 10 | Determination of Carbon Monoxide Emissions from Stationary Sources {Note: The method shall be based on a continuous sampling train.} |
| 18 | Measurement of Gaseous Organic Compound Emissions by Gas Chromatography |
| 19 | Determination of Sulfur Dioxide Removal Efficiency and Particulate Matter, Sulfur Dioxide, and Nitrogen Oxides Emission Rates (Optional F-factor method may be used to determine flow rate and gas analysis to calculate mass emissions in lieu of Methods 1-4.) |
| 25A | Method for Determining Gaseous Organic Concentrations (Flame Ionization) |

The above methods are described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Rule 62-204.800, F.A.C., Permit No. PSD-FL-267/0310485-001-AC]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- Annual Compliance Tests Required.  During each calendar year (January 1st to December 31st), this emissions unit shall be tested to demonstrate compliance with the emissions standards, pursuant to Rule 62-297.310(8), F.A.C., for Nox, VE and CO.  Method 7E or RATA test data required pursuant to 40 CFR 75 may be used to demonstrate compliance for annual compliance testing.  Annual compliance testing for CO may be conducted concurrent with the annual RATA testing for NOX as long as all testing requirements of 40 CFR 75 are met.  [Rule 62-297.310(8), F.A.C. and Permit No. PSD-FL-267/0310485-001-AC, Specific Condition 29 and 32]

- Continuous Compliance with the NOX Emission Limits.  Continuous compliance with the NOX BACT emission limits shall be demonstrated with the CEM system based on the applicable averaging time of 24-hr block average (DLN technology while burning gas) or a 3-hr block average (while burning oil).  For the 24-hr block average emissions may be determined via EPA Method 19 or equivalent EPA approved methods.  Based on CEMS data, a separate compliance determination is conducted at the end of each operating day (or 3-hr period when applicable) and a new average emission rate is calculated from the arithmetic average of all valid hourly emission rates from the previous operating day (or 3-hr period when applicable).  Valid hourly emission rates shall not include periods of startup, shutdown, or malfunction as defined in Rule 62-210.200, F.A.C., DLN tuning, or FSNL testing where emissions exceed the applicable NOX standard.  These excess emissions periods shall be reported as required in Specific Condition A.32.  A valid hourly emission rate shall be calculated for each hour in which at least two NOX concentrations are obtained at least 15 minutes apart.  [Rules 62-4.070, F.A.C. and 62-210.700, F.A.C.; 40 CFR 75; Permit Nos. 0310485-001-AC/PSD-FL-267, 0310485-021-AC, Specific Condition 2, and 0310485-025-AC/PSD-FL-267D]

- Compliance with the SO2 and PM/PM10 Emission Limits.  Notwithstanding the requirements of Rule 62-297.310(8), F.A.C., the use of natural gas and maximum 0.0015 percent sulfur (by weight) No. 2 or superior grade distillate fuel oil, is the method for determining compliance for SO2 and PM10.  For the purposes of demonstrating compliance with the 40 CFR 60 Subpart GG SO2 standard and the 0.0015% sulfur limit, fuel oil analysis using ASTM D2880-941 or D4294-90 (or equivalent latest version) for the sulfur content of liquid fuels and D1072-80, D3031-81, D4084-82 or D3246-81 (or equivalent latest version) for sulfur content of gaseous fuel shall be utilized in accordance with the EPA-approved custom fuel monitoring schedule or natural gas supplier data may be submitted or the natural gas sulfur content referenced in 40 CFR 75, Appendix D, may be utilized.  The applicant is responsible for ensuring that the procedures above are used for determination of fuel sulfur content.  Analysis may be performed by the owner or operator, a service contractor retained by the owner or operator, the fuel vendor, or any other qualified agency pursuant to 40 CFR 60 Subpart GG.  [Permit No. PSD-FL-267/0310485-001-AC, Specific Condition 31; 0310485-021-AC, Specific Condition 2]

- Compliance with the CO Emission Limit.  Annual compliance testing for CO may be conducted concurrently with the annual RATA testing for NOX required pursuant to 40 CFR 75 (required for gas only).  [Permit No. PSD-FL-267/0310485-001-AC, Specific Condition 32]

- Compliance with the VOC Emission Limit.  The CO emission limit shall be employed as a surrogate, and no annual VOC testing is required.  [Permit No. PSD-FL-267/0310485-001-AC, Specific Condition 33]

- Operating Rate During Testing.  Testing of emissions shall be conducted with the combustion turbine operating at permitted capacity.  Permitted capacity is defined as 90-100 percent of the maximum heat input rate allowed by the permit, corrected for the average ambient air temperature during the test (with 100 percent represented by a curve depicting heat input vs. ambient temperature).  If it is impracticable to test at permitted capacity, the source may be tested at less than permitted capacity.  In this case, subsequent operation is limited by adjusting the entire heat input vs. ambient temperature curve downward by an increment equal to the difference between the maximum permitted heat input (corrected for ambient temperature) and 110 percent of the value reached during the test until a new test is conducted.  Once the unit is so limited, operation at higher capacities is allowed for no more than 15 consecutive days for the purposes of additional compliance testing to regain the permitted capacity.  Test procedures shall meet all applicable requirements (i.e., testing time frequency, minimum compliance duration, etc.) of Rule 62-204.800 F.A.C.  [Rules 62-297.310(2) & (2)(b), F.A.C.; and, PSD-FL-267/0310485-001-AC, Specific Condition 34]

Recordkeeping and Reporting Requirements

- Reporting Schedule.  The following reports and notifications shall be submitted to the Compliance Authority:

| Report | Reporting Frequency | Related Condition(s) |
| --- | --- | --- |
| Subpart GG Excess Emissions Report | Semiannual | A.32.a. |
| State Excess Emissions Report | Semiannual | A.32.b. |

[Rule 62-213.440(1)(b), F.A.C.]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440(1)(b), F.A.C.]

- Excess Emissions Reporting.

- Semiannual NSPS Excess Emissions.  For emission units that elect to continuously monitor parameters or emissions, or to periodically determine the fuel sulfur content or fuel nitrogen content required under 40 CFR 60 Subpart GG, the owner or operator shall submit semiannual reports of excess emissions and monitor downtime, in accordance with 40 CFR 60.7(c).  Excess emissions shall be reported for all periods of unit operation, including startup, shutdown and malfunction.  For the purpose of reports required under 40 CFR 60.7(c), periods of excess emissions and monitor downtime shall be reported as defined in 40 CFR 60.334.  For NOX, excess emissions and monitor downtime that must be reported shall be defined as described in 40 CFR 60.334(j)(1).  For SO2 excess emissions and monitor downtime that must be reported shall be defined as described in 40 CFR 60.334(j)(2).  [40 CFR 60.334]

- Semiannual BACT Excess Emissions.  Excess emissions periods of startup, shutdown, malfunction, DLN tuning, or FSNL testing that are excluded from demonstrations of compliance with the state-issued NOX limits in Specific Condition A.6. shall be reported in a semiannual excess emissions report.  Excess emissions shall be reported following the format in 40 CFR 60.7.  [Rule 62-4.070, F.A.C.; Permit No. 0310485-001-AC/PSD-FL-267 and 0310485-025-AC/PSD-FL-267D]

- Malfunction Notification.  If excess emissions occur due to malfunction, the owner or operator shall notify the Compliance Authority within one working day of: the nature, extent, and duration of the excess emissions; the cause of the excess emissions; and the actions taken to correct the problem.  In addition, the Department may request a quarterly report with a written summary report of the incident.  [Rules 62-4.130 and 62-210.700(5), F.A.C.; Permit No. 0310485-001-AC/PSD-FL-267]

- Records.  All measurements, records, and other data required to be maintained by the owner or operator shall be recorded in a permanent form and retained for at least five years following the date on which such measurements, records, or data are recorded.  These records shall be made available to the Permitting and Compliance Authorities upon request.  [Permit Nos. PSD-FL-267/0310485-001-AC, Specific Condition 38; and PSD-FL-310/0310485-003-AC, Specific Condition 38; 40 CFR 60.7(f)]

- Special Recordkeeping Requirements.  The owner or operator shall obtain, make, and keep the following records related to fuel usage:

  - Hours of operation for the combustion turbine by fuel type shall be submitted with the Annual Operating Report (AOR) for the prior year.

  - Hours of operation for the combustion turbine shall be kept for each consecutive 12-month period by fuel type.

  - Daily hours of fuel oil operation shall be kept for the combustion turbine during any day in which fuel oil is fired.

[Permit No. 0310485-001-AC/PSD-FL-267, Specific Condition 40]

Table of Contents

The specific conditions in this section apply to the following emissions unit:

| EU No. | Brief Description |
| --- | --- |
| 002 | Combined-Cycle Combustion Turbine-Electrical Generator with supplementary-fired HRSG |
| 003 | Combined Cycle Combustion Turbine-Electrical Generator with supplementary-fired HRSG |

Each emissions unit consists of a nominal 170 MW (Make/Model: General Electric PG7241 FA) stationary combustion turbine-electrical generator equipped with an evaporative cooler, a supplementary-fired (natural gas) heat recovery steam generator (HRSG) duct burner, an associated 190-foot stack, and a selective catalytic reduction (SCR) unit for reducing NOX emissions, including ancillary equipment and ammonia storage; in addition, the emission units share one nominal 200 MW steam electrical generator and one freshwater cooling tower.  For the CTs, natural gas is the primary fuel, with low-sulfur distillate fuel oil as the back-up fuel.  Compliance Assurance Monitoring (CAM) does not apply to these emissions units.  Initial startup was November 27, 2004 for both EUs 002 and 003.

{Permitting note:  This emissions unit is regulated under:  Acid Rain-Phase II, 40 CFR 60, Subpart GG, Standards of Performance for Stationary Gas Turbines, adopted by reference in Rule 62-204.800(7)(b), F.A.C.; Rule 212.400, F.A.C., Prevention of Significant Deterioration (PSD); Best Available Control Technology (BACT); Air Construction Permit No. PSD-FL-310 and amendments (A thru H); and, Power Plant Siting Project No. PA 00-43.  The CT began commercial operation on November 27, 2004.  Stack height = 190 feet, exit diameter = 18.0 feet, exit temperature = 204ºF, actual volumetric flow rate = 1,009,200 acfm.}

Essential Potential to Emit (PTE) Parameters

- Permitted Capacity.

  - Combustion Turbines.  The maximum heat input rates, based on the higher heating value (HHV) of the fuel to these units shall not exceed:

| Unit Nos. | MMBtu/hr Heat Input | Fuel Type |
| --- | --- | --- |
| 002 and 003 | 1,911 | Natural Gas |
|  | 2,060 | Oil |

This maximum heat input rate will vary depending upon turbine inlet conditions and the combustion turbine characteristics. Manufacturer’s curves corrected for site conditions or equations for correction to other ambient conditions have been provided to the Department of Environmental Protection (DEP) and shall be re-submitted within 45 days of re-establishing the curves due to a compliance test or combustor tuning session.  [Rules 62-4.160(2), F.A.C., 62-204.800, F.A.C., 62-210.200(Definitions - PTE), F.A.C., 62-214.330, F.A.C.; Permit No. 0310485-003-AC/PSD-FL-310, Specific Condition 8]

  - HRSG equipped with Duct Burners.  The maximum heat input rate of each natural gas-fired HRSG duct burner shall not exceed 200 MMBtu/hr (HHV).  [Rule 62-210.200(Definitions-PTE), F.A.C.; Permit Nos. PSD-FL-310(0310485-003-AC, Specific Condition 9.), 0310485-006-AC/PSD-FL-310A and 0310485-017-AC/PSD-FL-310F]

- Emissions Unit Operating Rate Limitation After Testing.  See the related testing provisions in Appendix TR, Facility-wide Testing Requirements.  [Rule 62-297.310(3), F.A.C.]

- Methods of Operation – Fuels.  The facility is authorized to burn any combination of natural gas (2.0 grains sulfur/100 scf), and/or ultra-low-sulfur fuel oil (0.0015% sulfur content, by weight).  These fuels are subject to the hour limitations and recordkeeping requirements set forth in this permit.  Unless otherwise authorized by this permit, CT operation below 62 gross megawatts shall be limited to 2 hours during each calendar day.  [Rules 62-210.200(Definitions - PTE), F.A.C.; PSD-FL-310, Specific Condition 7; Permit Nos. 0310485-007-AC and 0310485-015-AC; 0310485-021-AC, Specific Condition 5]

{Permitting Note:  The limitation of this specific condition is more stringent than the NSPS Subpart GG sulfur dioxide limitation and thus assures compliance with 40 CFR 60.333 and 60.334.}

- Hours of Operation.  Except for the HRSG duct burners, the emission units are authorized to operate 8,760 hours per year while firing natural gas (2.0 grains sulfur/100 scf).  The combined cycle units are authorized to operate up to a combined maximum of 1,478 actual hours per consecutive 12-month period while firing fuel oil.  HRSG duct burner operations shall not exceed 1,800,000 MMBtu per consecutive 12-months for both duct burner systems.  [Rules 62-210.200(Definitions - PTE) and 62-212.400(12), F.A.C.; Permit Nos. 0310485-003-AC/PSD-FL-310, Specific Condition 14, 0310485-007-AC/PSD-FL-310B and 0310485-017-AC/PSD-FL-310F; 0310485-021-AC, Specific Condition 7.]

Control Technology

- Control Equipment.  Dry Low NOX (DLN) combustors and a selective catalytic reduction system shall be installed on each stationary combustion turbine to comply with the NOX and ammonia limits listed in this permit.  Wet injection shall additionally be installed on each stationary combustion turbine for use during fuel oil firing, in conjunction with the SCR.  [Design; Rules 62-4.070, F.A.C. and 62-212.400, F.A.C.; and, Permit No. 0310485-003-AC/PSD-FL-310, Specific Conditions 16 & 17]

- Selective Catalytic Reduction System.  EU 002 and EU 003 shall be operated with the use of the SCR system, except during periods of startup and shutdown in accordance with the manufacturer’s requirements.  [Permit No. 0310485-003-AC/PSD-FL-310, Specific Condition 45]

Emission Limitations and Standards

Unless otherwise specified, the averaging times for Specific Conditions B.6. - B.12. are based on the specified averaging time of the applicable test method.

- Nitrogen Oxides (NOX).  The concentration of NOX in the stack exhaust gas, with the combustion turbine operating on natural gas and the duct burner on, shall not exceed 3.5 ppmvd @ 15% O2 on a 3-hr block average.  The concentration of NOX in the stack exhaust gas, with the combustion turbine operating on fuel oil (duct burner firing not permitted), shall not exceed 15.0 ppmvd @ 15% O2 on a 3-hr block average.  Compliance shall be determined by the continuous emission monitor (CEMS).  [BACT; Rule 62-212.400, F.A.C.; and, Permit No. 0310485-003-AC/PSD-FL-310, Specific Condition 20]

- Ammonia.  The concentration of ammonia in the exhaust gas from each CT/HRSG shall not exceed 5.0 ppmvd @ 15% O2 while firing natural gas, nor 9 ppmvd @ 15% O2 while firing oil.  [BACT; Rules 62-212.400, F.A.C. and 62-4.070, F.A.C.; and, Permit No. 0310485-003-AC/PSD-FL-310. Specific Condition 20.]

- Carbon Monoxide (CO).  Emissions of CO in the stack exhaust gas (at ISO conditions) with the combustion turbine operating on any fuel (with duct burners on or off) shall not exceed 14 ppmvd @ 15% O2, on a 24-hr block average to be demonstrated by CEMS.  [BACT; Rule 62-212.400, F.A.C.; Permit No. 0310485-006-AC, and, Permit No. 0310485-003-AC/PSD-FL-310, Specific Condition 21]

- Volatile Organic Compounds (VOC).  Emissions of VOC in the stack exhaust gas (base load at ISO conditions) with the combustion turbine operating on gas shall not exceed 6.81 lbs/hour (4.0 lbs/hour with duct burners off) and with the combustion turbine operating on oil shall not exceed 7.68 lbs/hr.  (See Specific Condition B.29.)  [BACT; Rule 62-212.400, F.A.C.; Permit No. 0310485-006-AC, and, 0310485-003-AC/PSD-FL-310, Specific Condition 22]

- Sulfur Dioxide (SO2) and Sulfuric Acid Mist (SAM).  SO2 and SAM emissions shall be limited by firing natural gas (sulfur content not greater than 2 grains per 100 standard cubic feet) and a limited amount of 0.0015% sulfur content, by weight, fuel oil (or superior).  Compliance with this requirement will demonstrate compliance with the applicable NSPS SO2 emissions limitations from the combustion turbines as well as the duct burners.  [BACT; 40 CFR 60 Subpart GG; Rules 62-4.070, 62-212.400 and 62-204.800(7), F.A.C.; and Permit No. 0310485-003-AC/PSD-FL-310, Specific Condition 23.; 0310485-021-AC, Specific Condition 4]

- Particulate Matter (PM/PM10).  PM/PM10 emissions from each combustion turbine and HRSG train shall not exceed 22.02 lbs/hr at 100% output firing natural gas with the duct burner on and 62.1 lbs/hr at 100% output firing fuel oil - to be demonstrated by opacity.  [BACT; Rules 62-4.070, F.A.C. 62-212.400, F.A.C. and 62-204.800(7), F.A.C.; Permit No. 0310485-006-AC and, Permit No. 0310485-003-AC/PSD-FL-310, Specific Condition 24]

- Visible emissions (VE).  VE emissions shall not exceed 10 percent opacity from the stack in use.  [BACT; Rules 62-4.070, F.A.C. 62-212.400, F.A.C. and 62-204.800(7), F.A.C.; Permit No. 0310485-006-AC and, Permit No. 0310485-003-AC/PSD-FL-310, Specific Condition 25]

- Operating Procedures.  Operating procedures shall include good operating practices and proper training of all operators and supervisors.  The good operating practices shall meet the guidelines and procedures as established by the equipment manufacturers.  All operators (including supervisors) of air pollution control devices shall be properly trained in plant specific equipment.  [Rule 62-4.070(3), F.A.C.; and, 0310485-001-AC, Specific Condition 11]

Excess Emissions

Rule 62-210.700 (Excess Emissions), F.A.C. cannot vary any requirement of an NSPS, NESHAP or Acid Rain program provision.

- Definitions. The following definitions apply:

- Startup.  Startup is defined as the commencement of operation of any emissions unit which has shut down or ceased operation for a period of time sufficient to cause temperature, pressure, chemical or pollution control device imbalances.  [Rule 62-210.200(246), F.A.C.]

- Shutdown.  Shutdown is defined as the cessation of the operation of an emissions unit for any purpose.  [Rule 62-210.200(233), F.A.C.]

- Malfunction.  Malfunction is defined as any unavoidable mechanical and/or electrical failure of air pollution control equipment or process equipment or of a process resulting in operation in an abnormal or unusual manner.  [Rule 62-210.200(155), F.A.C.]

- Excess Emissions Allowed.  Excess emissions resulting from startup, shutdown or malfunction of any emissions unit shall be permitted provided:

- Best operational practices are adhered to and the duration of excess emissions shall be minimized.

- Excess emissions occurrences shall in no case exceed two hours (120 minutes) in any calendar day except during start-up, shutdown or during DLN major tuning as described in the alternate NOX and CO emissions standards below.  (See Specific Condition B.19.)

- A startup of any type is defined as being complete upon the first 3-hour block NOX average of 3.5 ppmvd or less (15 ppmvd or less for oil firing); and,

- Operation below 62 gross megawatts while firing fuel oil and/or natural gas shall be limited to 2 hours per unit cycle (breaker closed to breaker open).

[Rules 62-212.400, F.A.C., and 62-210.700(1), F.A.C.; Permit Nos. 0310485-012-AC and 0310485-015-AC, and Permit No. 0310485-003-AC/PSD-FL-310, Specific Condition 25]

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C.]

- CEMS Data Exclusion for FSNL Testing:  As a periodic maintenance practice, the permittee may perform full-speed no-load (FSNL) tests the with CT generator in accordance with the manufacturer’s recommendations or industry standards.  NOX and CO emissions data gathered during periods of FSNL testing may be excluded from demonstrations of compliance with the state-issued concentration-based NOX and CO limits.  Emissions during FSNL testing are subject to the limits in Specific Condition B.19.   NOX and CO emissions data recorded during FSNL testing shall not be excluded from annual emissions reports and demonstrations of compliance with any NSPS provisions.  [Rule 62-210.700(4), F.A.C.; Permit No. 0310485-025-AC/PSD-FL-310H]

- Alternate NOX and CO Emissions Standards.  During any calendar day in which at least one hour of startup, shutdown, FSNL testing, or DLN major tuning session has occurred, the following alternate emission limits shall apply to each combined cycle combustion turbine:

- An alternate NOX limit of 3,000 lbs shall apply if natural gas is the exclusively fired fuel;

- An alternate NOX limit of 8,880 lbs shall apply if any fuel oil is fired; and,

- An alternate CO limit of 4,200 lbs shall apply when firing either natural gas or fuel oil.

[Rules 62-4.070 and 62-212.400(2)(d) and (e), F.A.C.; Permit Nos. 0310485-014-AC/PSD-FL-310D, Specific Condition 25A and 0310485-025-AC/PSD-FL-310H]

Monitoring of Operations

- Fuel Monitoring Schedule.  An optional SO2 Emissions Data Protocol (without additional EPA approvals) for Gas-Fired and Oil-Fired Units pursuant to 40 CFR 75, Appendix D, for natural gas may be used in lieu of the daily sampling requirements of 40 CFR 60 Subpart GG provided the following requirement is met:  Each unit shall be monitored for SO2 emissions using methods consistent with the requirements of 40 CFR 75 and certified by the USEPA.  [Permit No. 0310485-003-AC/PSD-FL-310, Specific Condition 42]

Continuous Monitoring Requirements

- Continuous Monitoring Systems (CEMS).

- CEM Requirement.  The permittee shall calibrate, maintain, and operate continuous emission monitors in the stack to measure and record the emissions of NOX and CO from these emissions units, and the oxygen (O2) content of the flue gas at the location where NOX and CO are monitored, in a manner sufficient to demonstrate compliance with the emission limits of this permit.

- Compliance demonstration using CEM.  The CEM system shall be used to demonstrate compliance with the emission limits for NOX and CO established in this permit.  Compliance with the emission limits for NOX shall be based on a 3-hour block average.  The 3-hour block average shall be calculated from 3 consecutive hourly average emission rate values.  Compliance with the emission limits for CO shall be based on a 24-hour block average starting at midnight of each operating day.  The 24-hour block average shall be calculated from 24 consecutive hourly average emission rate values.  Each hourly value shall be computed using at least one data point in each fifteen-minute quadrant of an hour, where the unit combusted fuel during that quadrant of an hour.  Notwithstanding this requirement, an hourly value shall be computed from at least two data points separated by a minimum of 15 minutes (where the unit operates for more than one quadrant of an hour).  The owner or operator shall use all valid measurements or data points collected during an hour to calculate the hourly averages.  All data points collected during an hour shall be, to the extent practicable, evenly spaced over the hour.  If the CEM system measures concentration on a wet basis, the CEM system shall include provisions to determine the moisture content of the exhaust gas and an algorithm to enable correction of the monitoring results to a dry basis (0% moisture).  Alternatively, the owner or operator may develop an algorithm based on fuel characteristics and stack CO2 (or O2) measurements to calculate the moisture content in the exhaust gas to enable correction of the monitoring results to a dry basis (0% moisture).  Final results of the CEM system shall be expressed as ppmvd, corrected to 15% oxygen.

- NOX Monitor Requirements.  The NOX monitor shall be certified and operated in accordance with the following requirements.  The NOX monitor shall be certified pursuant to 40 CFR 75 and shall be operated and maintained in accordance with the applicable requirements of 40 CFR 75, Subparts B and C.  For purposes of determining compliance with the emission limits specified within this permit, missing data shall not be substituted.  Instead the block average shall be determined using the remaining hourly data in the 3 or 24-hour block.  Record keeping and reporting shall be conducted pursuant to 40 CFR Part 75, Subparts F and G.  The RATA tests required for the NOX monitor shall be performed using EPA Method 20 or 7E, Appendix A, 40 CFR 60.  The NOX monitor shall be a dual range monitor.  The span values for the NOX monitor will be determined in accordance with section 2.1.2 in Appendix A, 40 CFR 75.

- CO Monitor Requirements.  The CO monitor and CO2 monitor shall be certified and operated in accordance with the following requirements.  The CO monitor shall be certified pursuant to 40 CFR 60, Appendix B, Performance Specifications 4 and 4A.  The CO2 monitor shall be certified and maintained pursuant to 40 CFR 75.  Quality assurance procedures for the CO monitor shall conform to the requirements of 40 CFR 60, Appendix F, and the Data Assessment Report of section 7 shall be made each calendar quarter, and reported semi-annually to Compliance Authority.  The RATA tests required for the CO monitor shall be performed using EPA Method 10, Appendix A, 40 CFR 60.  The Method 10 analysis shall be based on a continuous sampling train, and the ascarite trap may be omitted or the interference trap of section 10.1 may be used in lieu of the silica gel and ascarite traps.  The CO monitor shall be a dual range monitor.  The span for the lower range shall not be greater than 20 ppm, and the span for the upper range shall be set as appropriate to reflect the level of CO emissions seen during unit startup.  The RATA tests required for the CO2 monitor shall be performed using EPA Method 3A or 3B, Appendix A, 40 CFR 60.

- CEMS Excluded Data.  NOX, CO and CO2 emissions data shall be recorded by the CEM system during episodes of FSNL testing, DLN major tuning, startup, shutdown and malfunction.  Periods of data excluded for malfunctions shall not exceed two hours in any calendar day.  All periods of data excluded for any startup, shutdown, DLN major tuning, FSNL test, or malfunction episode shall be consecutive for each episode.  Periods of data excluded for start-up, shutdown, FSNL testing, or DLN major tuning are subject to the alternate NOX and CO emissions standard in Specific Condition B.19.  The owner or operator shall minimize the duration of data attributed to FSNL testing, DLN major tuning, startup, shutdown and malfunctions, to the extent practicable.  Data recorded during FSNL testing, DLN major tuning, startup, shutdown or malfunction events shall not be excluded if the FSNL testing, DLN major tuning, startup, shutdown or malfunction episode was caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure, which may reasonably be prevented.

- Failure to Maintain or Operate.  Best operational practices shall be used to minimize hourly emissions that occur during episodes of FSNL testing, DLN major tuning, startup, shutdown and malfunction.  Emissions of any quantity or duration that occur entirely or in part from poor maintenance, poor operation, or any other equipment or process failure, which may reasonably be prevented, shall be prohibited.

- Reporting.  A summary report of duration of data excluded from the block average calculation, and all instances of missing data from monitor downtime, shall be reported to Compliance Authority semi-annually, and shall be consolidated with the report required pursuant to 40 CFR 60.7.  For purposes of reporting “excess emissions” pursuant to the requirements of 40 CFR 60.7, excess emissions shall be defined as the hourly emissions which are recorded by the CEM system during periods of data excluded for episodes of DLN tuning, FSNL testing, startup, shutdown and malfunction, allowed above.  The duration of excess emissions shall be the duration of the periods of data excluded for such episodes.  Reports required by this paragraph and by 40 CFR 60.7 shall be submitted no less than semi-annually, including semi-annual periods in which no data is excluded or no instances of missing data occur.

- Compliance Demonstration with Subpart GG.  Upon request from the Compliance Authority, the CEMS emission rates shall be corrected to ISO conditions to demonstrate compliance with the applicable standards of 40 CFR 60 Subpart GG.  JEA shall be permitted to utilize O2 as a diluent (rather than CO2), but shall notify the Compliance Authority of this change prior to CEMS installation.

[Rule 62-204.800; 40 CFR 60.7; Permit Nos. 0310485-003-AC/PSD-FL-310, Specific Condition 41; 0310485-014-AC/PSD-FL-310D; 0310485-021-AC, Specific Condition 3; 0310485-025-AC/PSD-FL-310H]

{Permitting note:  Compliance with these requirements will ensure compliance with the other CEM system requirements of this permit to comply with Subpart GG requirements, as well as the applicable requirements of Rule 62-297.520, F.A.C., 40 CFR 60.7(a)(5) and 40 CFR 60.13, and with 40 CFR Part 51, Appendix P, 40 CFR 60, Appendix B, Performance Specifications and 40 CFR 60, Appendix F, Quality Assurance Procedures.}

- CEMS in lieu of Water to Fuel Ratio.  The NOX CEMS shall be used in lieu of the water/fuel monitoring system for reporting excess emissions in accordance with 40 CFR 60, Subpart GG.  The calibration of the water/fuel-monitoring device required in 40 CFR 60 Subpart GG will be replaced by the 40 CFR 75 certification tests of the NOX CEMS.  Upon request from the Compliance Authority office, the CEMS emission rates for NOX shall be corrected to ISO conditions to demonstrate compliance with the NOX standard established in 40 CFR 60 Subpart GG.  [40 CFR 60.334(b)]

Test Methods and Procedures

- Test Methods.  Required tests shall be performed in accordance with the following reference methods:

| Method | Description of Method and Comments |
| --- | --- |
| 7E | Determination of Nitrogen Oxide Emissions from Stationary Sources |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |
| 10 | Determination of Carbon Monoxide Emissions from Stationary Sources {Note: The method shall be based on a continuous sampling train.} This testing may be conducted during the NOX RATA tests, which includes loads that are less than permitted capacity. |
| 19 | Determination of Sulfur Dioxide Removal Efficiency and Particulate Matter, Sulfur Dioxide, and Nitrogen Oxides Emission Rates (Optional F-factor method may be used to determine flow rate and gas analysis to calculate mass emissions in lieu of Methods 1-4.) |
| 20 | Determination of Nitrogen Oxides, Sulfur Dioxide and Diluent Emissions from Stationary Gas Turbines |
| 18 | Measurement of Gaseous Organic Compound Emissions by Gas Chromatography |
| 25 | Determination of Total Gaseous Nonmethane Organic Emissions as Carbon |
| 25A | Determination of Total Gaseous Organic Concentration Using a Flame Ionization Analyzer |
| CTM-027 | Conditional EPA Test Method 027, Measurement of Ammonia Slip. The applicant shall calculate and report the ppmvd ammonia slip (@ 15% O2) at the measured lbs/hr NOX emission rate as a means of compliance with the BACT standard. The applicant shall also be capable of calculating ammonia slip at the Compliance Authority’s request, according to Specific Condition B.31. |

The above methods are described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [PSD-FL-310]

{Permitting Note:  The 40 CFR 60 Subpart GG requirement to correct test data to ISO conditions applies.  However, such correction is not used for compliance determinations with the BACT standard(s).  [PSD-FL-310]}

- Annual Compliance Tests.  During each calendar year (January 1 to December 31), these emissions units shall be tested to demonstrate compliance with the emissions standards for NOX, CO, ammonia, and VE.  RATA testing, required pursuant to 40 CFR 75, for NOX and CO CEMS may be utilized to demonstrate annual compliance.  [Rule 62-297.310(8), F.A.C., Permit No. 0310485-003-AC/PSD-FL-310, Conditions 29 and 32]

- Initial Testing Requirements.  Initial compliance tests meeting the requirements of 40 CFR 60.8 shall be conducted after any replacement of the major components of the air pollution control equipment (and shake down period not to exceed 100 days after re-starting the CT), such as replacement of SCR catalyst or change of combustors, if specifically requested by the Compliance Authority on a case-by-case basis.  [Permit No. 0310485-003-AC/PSD-FL-310, Specific Condition 29]

- Continuous Compliance with the CO and NOX Emission Limits.  Continuous compliance with the CO and NOX emission limits shall be demonstrated by the CEM system on the specified hour average basis.  Based on CEMS data, a separate compliance determination is conducted at the end of each period and a new average emission rate is calculated from the arithmetic average of all valid hourly emission rates from the previous period.  Specific Condition B.21. further describes the CEM system requirements.  Excess emissions periods shall be reported as required in Specific Conditions B.21. and B.34.  [Permit No. 0310485-003-AC/PSD-FL-310, Specific Condition 30; Rules 62-4.070, F.A.C. and 62-210.700, F.A.C.; 40 CFR 75; and, BACT]

- Compliance with the SO2 and PM/PM10 emission limits.  For the purposes of demonstrating compliance with the 40 CFR 60 Subpart GG SO2 standard, ASTM methods D4084-82 or D3246-81 (or equivalent) for sulfur content of gaseous fuel shall be utilized in accordance with the EPA-approved custom fuel monitoring schedule or natural gas supplier data may be submitted or the natural gas sulfur content referenced in 40 CFR 75, Appendix D, may be utilized.  However, the applicant is responsible for ensuring that the procedures in 40 CFR 60 Subpart GG or 40 CFR 75 are used when determination of fuel sulfur content is made.  Analysis may be performed by the owner or operator, a service contractor retained by the owner or operator, the fuel vendor, or any other qualified agency pursuant to 40 CFR 60 Subpart GG.  [Permit No. 0310485-003-AC/PSD-FL-310, Specific Condition 31]

- Compliance with the CO Emission Limit.  Annual RATA testing for the CO and NOX CEMS shall be required pursuant to 40 CFR 75.  [Permit No. 0310485-003-AC/PSD-FL-310, Specific Condition 32]

{Permitting Note:  40 CFR 75 does not address RATA requirements for CO CEMS.  The required annual RATA testing for the CO CEMS shall be performed instead as required by 40 CFR 60 Appendix B.}

- Compliance with the VOC Emission Limit.  Continuous monitoring of CO shall represent a surrogate for VOC emissions and provide assurance that the emission rates of the BACT Determination are being met.  [BACT; Rule 62-212.400, F.A.C.; Permit No. 0310485-006-AC, and, Permit No. 0310485-003-AC/PSD-FL-310, Specific Condition 33]

- Operating Rate during Testing.  Unless otherwise specified, testing of emissions shall be conducted with the combustion turbine operating at permitted capacity.  Permitted capacity is defined as 90-100 percent of the maximum heat input rate allowed by the permit, corrected for the average ambient air temperature during the test (with 100 percent represented by a curve depicting heat input vs. ambient temperature).  Procedures for these tests shall meet all applicable requirements (i.e., testing time frequency, minimum compliance duration, etc.) of Chapters 62-204 and 62-297, F.A.C.  If it is impracticable to test at permitted capacity, the source may be tested at less than permitted capacity.  In this case, subsequent operation is limited by adjusting the entire heat input vs. ambient temperature curve downward by an increment equal to the difference between the maximum permitted heat input (corrected for ambient temperature) and 110 percent of the value reached during the test until a new test is conducted.  Once the unit is so limited, operation at higher capacities is allowed for no more than 15 consecutive days for the purposes of additional compliance testing to regain the permitted capacity.  Test procedures shall meet all applicable requirements (i.e., testing time frequency, minimum compliance duration, etc.) of Rule 62-204.800 F.A.C.  [Rules 62-297.310(3) & (3)(b), F.A.C.; and, Permit No. 0310485-003-AC/PSD-FL-310, Specific Condition 34]

- Selective Catalytic Reduction System (SCR) Compliance Procedures.

- NOX and Ammonia Annual Testing.  An annual stack emission test for nitrogen oxides and ammonia from the CT/HRSG pair shall be simultaneously conducted while firing natural gas and operating with the duct burner on as defined in Specific Condition B.7.  The ammonia injection rate necessary to comply with the NOX standard shall be established and reported during each annual performance test.

- SCR Operation.  The SCR shall operate at all times that the turbine is operating, except during turbine start-up and shutdown periods, as dictated by manufacturer's guidelines and in accordance with this permit.

- Ammonia Flow Meter.  The permittee shall install and operate an ammonia flow meter to continuously measure and record the ammonia injection rate to the SCR system of the CT/HRSG set.  It shall be maintained and calibrated according to the manufacturer’s specifications.

- Ammonia Flow Rate.  During the stack test, the permittee (at each tested load condition) shall determine and report the ammonia flow rate required to meet the emissions limitations.  During NOX CEM downtimes or malfunctions, the permittee shall operate at the ammonia flow rate, which was established during the last stack test.

- Emission Calculations.  Ammonia emissions shall be calculated continuously using inlet and outlet NOX concentrations from the SCR system and ammonia flow supplied to the SCR system.  The calculated ammonia slip shall be used as an indicator of ammonia slip, and to assist in determining appropriate injection rates, but not as the method of determining compliance.  A calculated ammonia slip above the permitted value shall result in JEA taking appropriate and timely action, and documenting each event from its occurrence to its resolution.  The calculation procedure shall be provided with the CEM monitoring plan required by 40 CFR 75.  The following calculation represents one means by which the permittee may demonstrate compliance with this condition:

Ammonia slip @ 15% O2 = (A-(B x C/1,000,000)) x (1,000,000/B) x D, where:

A = ammonia injection rate (lbs/hr)/17 (lbs/lb-mol).

B = dry gas exhaust flow rate (lbs/hr)/29 (lbs/lb-mol).

C = change in measured NOX (ppmv @ 15% O2) across catalyst.

D = correction factor, derived annually during compliance testing by comparing actual to tested ammonia slip.

- Reporting.  The calculation along with each newly determined correction factor shall be submitted with each annual compliance test.  Calibration data (“as found” and “as left”) shall be provided for each measurement device utilized to make the ammonia emission measurement and submitted with each annual compliance test.

- Re-Testing.  Upon specific request by the local compliance authority or the DEP, a special re-test shall occur as described in the previous conditions concerning annual test requirements, in order to demonstrate that all NOX and ammonia slip related permit limits can be complied with.

[Permit No. 0310485-003-AC/PSD-FL-310, Specific Condition 45]

Recordkeeping and Reporting Requirements

- Reporting Schedule.  The following reports and notifications shall be submitted to the Compliance Authority:

| Report | Reporting Frequency | Related Condition(s) |
| --- | --- | --- |
| Subpart GG Excess Emissions Report | Semiannual | B.34.a |
| State Excess Emissions Report | Semiannual | B.34.b |

[Rule 62-213.440(1)(b), F.A.C.]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440(1)(b), F.A.C.]

- Excess Emissions Reporting.

- Semiannual NSPS Excess Emissions.  For emission units that elect to continuously monitor parameters or emissions, or to periodically determine the fuel sulfur content or fuel nitrogen content required under 40 CFR 60 Subpart GG, the owner or operator shall submit semiannual reports of excess emissions and monitor downtime, in accordance with 40 CFR 60.7(c).  Excess emissions shall be reported for all periods of unit operation, including startup, shutdown and malfunction.  For the purpose of reports required under 40 CFR 60.7(c), periods of excess emissions and monitor downtime shall be reported as defined in 40 CFR 60.334.  For NOX, excess emissions and monitor downtime that must be reported shall be defined as described in 40 CFR 60.334(j)(1).  For SO2 excess emissions and monitor downtime that must be reported shall be defined as described in 40 CFR 60.334(j)(2).  [40 CFR 60.334]

- Semiannual BACT Excess Emissions.  A summary report of duration of data excluded from the block average (BACT) calculation, and all instances of missing data from monitor downtime, shall be reported to the Compliance Authority semi-annually and shall be consolidated with the report required pursuant to 40 CFR 60.7 (paragraph a, above).  Excess emissions shall be defined as the hourly emissions which are recorded by the CEM system during periods of data excluded for episodes of DLN tuning, FSNL testing, startup, shutdown and malfunction, allowed above.  The duration of excess emissions shall be the duration of the periods of data excluded for such episodes.  Reports required by this paragraph and by 40 CFR 60.7 (paragraph a, above) shall be submitted no less than semi-annually, including semi-annual periods in which no data is excluded or no instances of missing data occur.  [Rule 62-4.070, F.A.C.; Permit No. 0310485-003-AC/PSD-FL-310 and 0310485-025-AC/PSD-FL-310H]

- Malfunction Notification.  If excess emissions occur due to malfunction, the owner or operator shall notify the Compliance Authority within one working day of: the nature, extent, and duration of the excess emissions; the cause of the excess emissions; and the actions taken to correct the problem.  In addition, the Department may request a quarterly report with a written summary report of the incident.  [Rules 62-4.130 and 62-210.700(5), F.A.C.]

- DLN Major Tuning.

- Notification.  At least one business day prior to performing any major tuning session, the permittee shall provide the Compliance Authority with an advance notice that details the activity and proposed major tuning schedule.  The notice may be by letter, facsimile transmittal, or electronic mail.  Once the major tuning session is completed, the Compliance Authority shall be notified in a like manner, within one business day.  Within 15 days of completion of the major tuning session, the excluded CEMS data shall be forwarded to the Compliance Authority.  CEMS data shall not be excluded from any Acid Rain reporting requirements.

- Compliance Data.  Data collected during periods covered by the alternate emissions standard provisions of Specific Condition B.19. may be excluded from the compliance determination calculation requirements of Specific Conditions B.7. and B.9.

[Rule 62-4.070(3), F.A.C.; Permit No. 0310485-014-AC/PSD-FL-310D, Specific Condition 25B]

- Compliance Test Reports.  The test report shall provide sufficient detail on the tested emission unit and the procedures used to allow the Compliance Authority to determine if the test was properly conducted and if the test results were properly computed.  At a minimum, the test report shall provide the applicable information listed in Rule 62-297.310(10), F.A.C.  [Permit No. 0310485-003-AC/PSD-FL-310, Specific Condition 39]

- Special Recordkeeping Requirements.  The owner or operator shall obtain, make, and keep records of hours of operation and heat input.  The records shall be:

- submitted with the Annual Operation Report (AOR) for the prior year for each combustion turbine by fuel type;

- kept for each consecutive 12-month period for each combustion turbine by fuel type; and

- kept for each consecutive 12-month period while firing natural gas for each HRSG duct burner.  (See Specific Condition B.4.)

[Permit No. 0310485-003-AC/PSD-FL-310, Specific Condition 40; and, Permit Nos. 0310485-017-AC/PSD-FL-310F, 0310485-014-AC/PSD-FL-310D, Specific Condition 40; 0310485-012-AC/PSD-FL-310C; 0310485-021-AC, Specific Condition 3]

- Records.  All measurements, records, and other data required to be maintained by the owner or operator shall be recorded in a permanent form and retained for at least five years following the date on which such measurements, records, or data are recorded.  These records shall be made available to DEP and the Compliance Authority representatives upon request.  [Permit Nos. PSD-FL-267/0310485-001-AC, Specific Condition 38; and PSD-FL-310/0310485-003-AC, Specific Condition 38; 40 CFR 60.7(f)]

Table of Contents

The specific conditions in this section apply to the following emissions unit:

| E.U. No. | Brief Description |
| --- | --- |
| 008 | Emergency Diesel-Fired Fire Pump Engine |

One diesel fire pump, manufactured by Caterpillar, serial number 64Z31958, Model 3306, 266 HP, 198.5 kW, in service June 2000, 6 cylinders, 10.5 Liters.

This emissions unit is a diesel-fired reciprocating internal combustion engine (RICE) used to drive an emergency fire pump.  The emergency fire pump engine uses diesel fuel oil only.

The following table provides important details for the above emission unit:

| Engine Brake HP | Date of Construction | Primary Fuel | Displacement liters/cylinder(l/c) | Serial Number | Manufacturer |
| --- | --- | --- | --- | --- | --- |
| 266 HP | 2000 | Diesel | 1.75 L per Cylinder | 64Z31958 | Caterpillar |

{Permitting Note:  This compression ignition (CI) engine is regulated under 40 CFR 63, Subpart ZZZZ, National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines (RICE) adopted in Rule 62.204.800(11)(b), F.A.C.  This permit section addresses an “existing” emergency stationary CI RICE less than or equal to 500 HP with a displacement of less than 10 liters per cylinder that is located at an area source of HAP and that has not been modified or reconstructed after 6/12/2006.  If the RICE is modified or reconstructed after 7/11/2005, the NSPS 40 CFR 60, Subpart IIII, will then apply.}

Essential Potential to Emit (PTE) Parameters

- Hours of Operation.

  - Emergency Situations.  There is no time limit on the use of this fire pump engine in emergency situations.  [40 CFR 63.6640(f)(1)]

  - Maintenance and Testing.  This unit is authorized to operate for the purpose of maintenance checks and readiness testing, provided that the tests are recommended by federal, state or local government, the manufacturer, the vendor, or the insurance company associated with the engine.  Maintenance checks and readiness testing of such units is limited to 100 hours per year.  The owner or operator may petition the Administrator for approval of additional hours to be used for maintenance checks and readiness testing, but a petition is not required if the owner or operator maintains records indicating that Federal, State, or local standards require maintenance and testing of emergency RICE beyond 100 hours per year.  [40 CFR 63.6640(f)(2)(i)]

  - Non-emergency Situations.  This unit is authorized to operate up to 50 hours per year in non-emergency situations, but those 50 hours are counted towards the 100 hours per year provided for maintenance and testing.  [40 CFR 63.6640(f)(4)]

Emission Limitations and Operating Requirements

- Work or Management Practice Standards.

- Oil.  Change oil and filter every 500 hours of operation or annually, whichever comes first.  [40 CFR 63.6603(a), Table 2d.4.a.]

- Air Cleaner.  Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first.  [40 CFR 63.6603(a) & Table 2d.4.b]

- Hoses and Belts.  Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary.  [40 CFR 63.6603(a), Table 2d.4.c.]

- Operation and Maintenance.  Operate and maintain the stationary RICE according to the manufacturer's emission-related operation and maintenance instructions or develop and follow your own maintenance plan which must provide, to the extent practicable for the maintenance and operation of the engine in a manner consistent with good air pollution, control practice for minimizing emissions.  [40 CFR 63.6625(e)]

- Oil Analysis.  The owner or operator has the option of using oil analysis to extend the change requirement.  The oil analysis must be performed at the same frequency specified for changing the oil.  The analysis program must at a minimum analyze the following three parameters: Total Base Number, viscosity, and percent water content.  The condemning limits for these parameters are as follows: Total Base Number is less than 30 percent of the Total Base Number of the oil when new; viscosity of the oil has changed by more than 20 percent from the viscosity of the oil when new; or percent of water content (by volume) is greater than 0.5.  If all of these condemning limits are not exceeded, the engine owner or operator is not required to change the oil.  If any of the limits are exceeded, the engine owner or operator must change the oil within 2 days of receiving the results of the analysis; if the engine is not in operation when the results of the analysis are received, the engine owner or operator must change the oil within 2 days or before commencing operation, whichever is later.  The owner or operator must keep records of the parameters that are analyzed as part of the program, the results of the analysis, and the oil changes for the engine. The analysis program must be part of the maintenance plan for the engine.  [40 CFR 63.6625(i)]

Compliance Requirements

- Hour Meter.  The owner or operator must install a non-resettable hour meter if one is not already installed.  [40 CFR 63.6625(f)]

Compliance

- Continuous Compliance.  Each unit shall be in compliance with the emission limitations, operating limitations and other requirements in this section at all times.  [40 CFR 63.6605(a)]

- Operation and Maintenance of Equipment.  At all times the owner or operator must operate and maintain, any affected source, including associated air pollution control equipment and monitoring equipment, in a manner consistent with safety and good air pollution control practices for minimizing emissions.  Determination of whether such operation and maintenance procedures are being used will be based on information available to the compliance authority which may include, but is not limited to, monitoring results, review of operation and maintenance procedures, review of operation and maintenance records, and inspection of the source.  [40 CFR 63.6605(b)]

Recordkeeping Requirements

- Notification, Performance, and Compliance Records.  The owner or operator must keep the records described below.

- A copy of each notification and report that the owner or operator submitted to comply with this section, including all documentation supporting any Initial Notification or Notification of Compliance Status that the owner or operator submitted.

- Records of the occurrence and duration of each malfunction of operation.

- Records of actions taken during periods of malfunction to minimize emissions in accordance with Specific Condition C.5, including corrective actions to restore malfunctioning process and monitoring equipment to its normal or usual manner of operation.

- Records of the actions required in Specific Condition C.2.d to show continuous compliance with each emission limitation or operating requirement.

- Records of the Work or Management Practice Standards specified in Specific Condition C.2

- Records of the maintenance conducted in order to demonstrate that the RICE was operated and maintained according to your own maintenance plan.

- Records of the hours of operation of the engine that is recorded through the non-resettable hour meter.  The owner or operator must document how many hours are spent for emergency operation including what classified the operation as emergency and how many hours are spent for non-emergency operation.  If the engines are used for emergency demand response operation or for periods of voltage or frequency deviations, the owner or operator must keep records of the notification of the emergency situation, and the time of engine operation for these purposes.

[40 CFR 63.6655]

- Record Retention.

- The owner or operator must keep records in a suitable and readily available form for expeditious reviews.

- The owner or operator must keep each record readily accessible in hard copy or electronic form for at least 5 years after the date of each occurrence, measurement, maintenance, corrective action, report, or record.

[40 CFR 63.6660 and 40 CFR 63.10(b)(1)]

Reporting Requirements

- Emergency Situation.  If an emergency engine is operating during an emergency and it is not possible to shut down the engine in order to perform the work practice requirements on the schedule required of this section, or if performing the work practice on the required schedule would otherwise pose an unacceptable risk under federal, state, or local law, the work practice can be delayed until the emergency is over or the unacceptable risk under federal, state, or local law has abated.  The work practice should be performed as soon as practicable after the emergency has ended or the unacceptable risk under federal, state, or local law has abated.  Sources must report any failure to perform the work practice on the schedule required and the federal, state or local law under which the risk was deemed unacceptable.  [40 CFR 63.6602 Table 2c, footnote 1]

General Provisions

- 40 CFR 63 Subpart A - General Provisions.  The owner or operator shall comply with the following applicable requirements of 40 CFR 63 Subpart A - General Provisions, which have been adopted by reference in Rule 62-204.800(11)(d)1., F.A.C., except that the Secretary is not the Administrator for purposes of 40 CFR 63.5(e), 40 CFR 63.5(f), 40 CFR 63.6(g), 40 CFR 63.6(h)(9), 40 CFR 63.6(j), 40 CFR 63.13, and 40 CFR 63.14.  Link to 40 CFR 63, Subpart A - General Provisions

| General Provisions Citation | Subject of Citation |
| --- | --- |
| §63.1 | General applicability of the General Provisions |
| §63.2 | Definitions (Additional terms defined in §63.6675) |
| §63.3 | Units and abbreviations |
| §63.4 | Prohibited activities and circumvention |
| §63.5 | Construction and reconstruction |
| §63.6(a) | Applicability |
| §63.9(a) | Applicability and State delegation of notification requirements |
| §63.9(b)(1)–(5) | Initial notifications (Except that §63.9(b)(3) is reserved) |
| §63.9(i) | Adjustment of submittal deadlines |
| §63.9(j) | Change in previous information |
| §63.10(a) | Administrative provisions for recordkeeping/reporting |
| §63.10(b)(1) | Record retention |
| §63.10(b)(2)(vi)–(xi) | Records |
| §63.10(b)(2)(xii) | Record when under waiver |
| §63.10(b)(2)(xiv) | Records of supporting documentation |
| §63.10(b)(3) | Records of applicability determination |
| §63.10(d)(1) | General reporting requirements |
| §63.10(f) | Waiver for recordkeeping/reporting |
| §63.12 | State authority and delegations |
| §63.13 | Addresses |
| §63.14 | Incorporation by reference |
| §63.15 | Availability of information |

[40 CFR 63.6665 & Table 8 to Subpart ZZZZ of Part 63]

Table of Contents

Operated by:  JEA

ORIS Code:  7846

The emissions units listed below are regulated under Acid Rain, Phase II.

| E.U. No. | Brief E.U. Description |
| --- | --- |
| 001 | Simple-Cycle Combustion Turbine-Electrical Generator |
| 002 | Combined-Cycle Combustion Turbine-Electrical Generator with supplementary-fired HRSG |
| 003 | Combined Cycle Combustion Turbine-Electrical Generator with supplementary-fired HRSG |

A.1.	The Phase II Acid Rain Part application submitted for this facility, as approved by the Department, is a part of this permit.  The owners and operators of these Phase II acid rain units must comply with the standard requirements and special provisions set forth in the application listed below:

a.	DEP Form No. 62-210.900(1)(a), dated May 16, 2018, received May 17, 2018.

[Chapter 62-213, F.A.C. and Rule 62-214.320, F.A.C.]

A.2.	Sulfur Dioxide (SO2) Emission Allowances.  SO2 emissions from sources subject to the Federal Acid Rain Program (Title IV) shall not exceed any allowances that the source lawfully holds under the Federal Acid Rain Program.  Allowances shall not be used to demonstrate compliance with a non-Title IV applicable requirement of the Act.

a.	No permit revision shall be required for increases in emissions that are authorized by allowances acquired pursuant to the Federal Acid Rain Program, provided that such increases do not require a permit revision pursuant to Rule 62-213.400(3), F.A.C.

b.	No limit shall be placed on the number of allowances held by the source under the Federal Acid Rain Program.

c.	Allowances shall be accounted for under the Federal Acid Rain Program.

[Rule 62-213.440(1)(c)1., 2. & 3., F.A.C.]

A.3.	Comments, Notes, and Justifications:  None.

Table of Contents