# Vandolah Power Company, LLC

# Vandolah Power Project

# Facility ID No. 0490043

# Hardee County

#### Title V Air Operation Permit Renewal

#### Permit No. 0490043-011-AV

(Renewal of Title V Air Operation Permit No. 0490043-009-AV)

# Permitting Authority:

State of Florida

Department of Environmental Protection

Division of Air Resource Management

Office of Permitting and Compliance

2600 Blair Stone Road

Mail Station #5505

Tallahassee, Florida  32399-2400

# Telephone:  (850) 717-9000

Email:  DARM_Permitting@dep.state.fl.us

# Compliance Authority:

Department of Environmental Protection

Southwest District Office

13051 North Telecom Parkway

Temple Terrace, Florida  33637

Telephone:  (813) 632-7600

Email (preferred):  SWD_Air@dep.state.fl.us

Title V Air Operation Permit Renewal

Permit No. 0490043-011-AV

Table of Contents

Section	Page Number

Placard Page. 	 1

I.	Facility Information.

A.	Facility Description. 	 2

B.	Summary of Emissions Units. 	 2

C.	Applicable Regulations. 	 2

II.	Facility-wide Conditions. 	 4

III.	Emissions Units and Conditions.

A.	EU Nos. 001 – 004, Four 170 MW Simple Cycle Combustion Turbines. 	 7

B.	EU No. 007 – 011, Five Diesel-Fueled Emergency Engines. 	 13

IV.	Acid Rain Part. 	 16

Phase II Acid Rain Application/Compliance Plan.

Phase II Acid Rain NOX Compliance Plan.

V.	Appendices. 	 Attached

Appendix A, Glossary.

Appendix I, List of Insignificant Emissions Units and/or Activities.

Appendix NESHAP Subpart A, General Provisions.

Appendix NESHAP Subpart ZZZZ, National Emissions Standards for Hazardous Air Pollutants For

Stationary Reciprocating Internal Combustion Engines.

Appendix NSPS Subpart A, General Provisions.

Appendix NSPS Subpart GG, Standards of Performance for Stationary Gas Turbines.

Appendix RR, Facility-wide Reporting Requirements.

Appendix TR, Facility-wide Testing Requirements.

Appendix TV, Title V General Conditions.

Referenced Attachments. 	 At End of Attachment

Figure 1, Summary Report-Gaseous and Opacity Excess Emission and

Monitoring System Performance (40 CFR 60, July, 1996).

Table H, Permit History.

| Permittee: Vandolah Power Company, LLC 2394 Vandolah Road Wauchula, Florida 33873 | Permit No. 0490043-011-AV Vandolah Power Project Facility ID No. 0490043 Title V Air Operation Permit Renewal |
| --- | --- |

The purpose of this permit is to renew the Title V air operation permit for the above referenced facility.  The existing Vandolah Power Project is in Hardee County at 2394 Vandolah Road, Wauchula, Florida.  UTM Coordinates are:  Zone 17, 407.85 km East and 3044.5 km North.  Latitude is 27 31’ 22” North, and Longitude is 81 55’ 28” West.

The Title V air operation permit is issued under the provisions of Chapter 403, Florida Statutes (F.S.), and Florida Administrative Code (F.A.C.) Chapters 62-4, 62-210, 62-213 and 62-214.  The above named permittee is hereby authorized to operate the facility in accordance with the terms and conditions of this permit.

Executed in Tallahassee, Florida.

0490043-009-AV Effective Date:  January 1, 2013

0490043-011-AV Effective Date:  DATE, 20yy

Renewal Application Due Date:  Exp. DATE -225, 20zz

Expiration Date:  Eff. DATE + 5 years, 20zz

(Proposed)

For:

Syed Arif, P.E., Program Administrator

Office of Permitting and Compliance

Division of Air Resource Management

SA/dlr/jpd

Subsection A.  Facility Description.

Vandolah Power Project is operated as a peaking facility.  The facility consists of four dual-fuel, nominal 170 megawatt (MW) General Electric model PG7241FA combustion turbine-electric generators with evaporative inlet coolers and two 2.8 million gallon fuel oil storage tanks.  Each combustion turbine can fire both natural gas and distillate fuel oil.  The combustion turbine units can operate in simple cycle mode and intermittent duty mode.  NOX emissions are controlled by dry low NOX (DLN-2.6) combustors when firing natural gas and water injection when firing distillate oil (No. 2 oil or superior).  A continuous emissions monitoring system (CEMS) for NOX is installed on each unit.  The turbines commenced operation in April 2002.

The facility has one 265 horsepower (hp) Clarke Model JDFP-06WA diesel-fired fire protection system, with a John Deere Co. 6081A base model engine, for the operations/maintenance building.  Other than maintenance and readiness testing, the engine is operated only in emergency situations.

The Vandolah facility has four 555 hp diesel-fired Generac Power Systems, Inc. Model 12.0 DTA emergency generator sets at the facility.  Other than maintenance and readiness testing, the generators are operated only in emergency situations.

Subsection B.  Summary of Emissions Units.

| EU No. | ## Brief Description |
| --- | --- |
| Regulated Emissions Units |  |
| 001 | 170 MW simple cycle combustion turbine-electrical generator |
| 002 | 170 MW simple cycle combustion turbine-electrical generator |
| 003 | 170 MW simple cycle combustion turbine-electrical generator |
| 004 | 170 MW simple cycle combustion turbine-electrical generator |
| 007 | Clarke Model JDFP-06WA diesel-fired fire protection system |
| 008 | Generac Power Systems, Inc. Model 12.0 DTA emergency generator set |
| 009 | Generac Power Systems, Inc. Model 12.0 DTA emergency generator set |
| 010 | Generac Power Systems, Inc. Model 12.0 DTA emergency generator set |
| 011 | Generac Power Systems, Inc. Model 12.0 DTA emergency generator set |

Also included in this permit are miscellaneous insignificant emissions units and/or activities (see Appendix I – List of Insignificant Emissions Units and/or Activities).

Subsection C.  Applicable Regulations.

Based on the Title V air operation permit renewal application received May 19, 2017, this facility is not a major source of hazardous air pollutants (HAP).  The existing facility is a prevention of significant deterioration (PSD) major source of air pollutants in accordance with Rule 62-212.400, F.A.C.  A summary of applicable regulations is shown in the following table.

| Regulation | ## EU No(s). |
| --- | --- |
| Federal Rule Citations |  |
| 40 CFR 60, Subpart A, NSPS General Provisions | 001, 002, 003, 004 |
| 40 CFR 60, Subpart GG, Standards of Performance for Stationary Gas Turbines | 001, 002, 003, 004 |
| 40 CFR 63, Subpart A, General Provisions | 007, 008, 009, 010, 011 |
| 40 CFR 63, Subpart ZZZZ, National Emissions Standards For Hazardous Air Pollutants For Stationary Reciprocating Internal Combustion Engines | 007, 008, 009, 010, 011 |
| 40 CFR 75 Acid Rain Monitoring Provisions | 001, 002, 003, 004 |
| State Rule Citations |  |
| Rule 62-4, Florida Administrative Code (F.A.C.) (Permitting Requirements) | 001, 002, 003, 004, 007, 008, 009, 010, 011 |
| Rule 62-204, F.A.C. (Ambient Air Quality Requirements, PSD Increments, and Federal Regulations Adopted by Reference) | 001, 002, 003, 004 |
| Rule 62-210, F.A.C. (Permits Required, Public Notice, Reports, Stack Height Policy, Circumvention, Excess Emissions, and Forms) | 001, 002, 003, 004, 007, 008, 009, 010, 011 |
| Rule 62-212, F.A.C. (Preconstruction Review, PSD Review and Best Available Control Technology (BACT)) | 001, 002, 003, 004 |
| Rule 62-213, F.A.C. (Title V Air Operation Permits for Major Sources of Air Pollution) | 001, 002, 003, 004, 007, 008, 009, 010, 011 |
| Rule 62-214, F.A.C. (Requirements for Sources Subject To The Federal Acid Rain Program) | 001, 002, 003, 004 |
| Rule 62-296, F.A.C. (Emission Limiting Standards) | 001, 002, 003, 004, 007, 008, 009, 010, 011 |
| Rule 62-297, F.A.C. (Test Methods and Procedures, Continuous Monitoring Specifications, and Alternate Sampling Procedures) | 001, 002, 003, 004 |

Table of Contents

The following conditions apply facility-wide to all emission units and activities:

- Appendices.  The permittee shall comply with all documents identified in Section V, Appendices, listed in the Table of Contents.  Each document is an enforceable part of this permit unless otherwise indicated.  [Rule 62-213.440, F.A.C.]

Emissions and Controls

- Not federally Enforceable.  Objectionable Odor Prohibited.  No person shall cause, suffer, allow or permit the discharge of air pollutants, which cause or contribute to an objectionable odor.  An “objectionable odor” means any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance.  [Rule 62-296.320(2) and 62-210.200(Definitions), F.A.C.]

- General Volatile Organic Compounds (VOC) Emissions or Organic Solvents (OS) Emissions.  The permittee shall allow no person to store, pump, handle, process, load, unload or use in any process or installation, volatile organic compounds or organic solvents without applying known and existing vapor emission control devices or systems deemed necessary and ordered by the Department.  [Rule 62-296.320(1), F.A.C.]

{Permitting Note:  Nothing is deemed necessary and ordered at this time.}

- General Visible Emissions.  No person shall cause, let, permit, suffer or allow to be discharged into the atmosphere the emissions of air pollutants from any activity equal to or greater than 20% opacity.  This regulation does not impose a specific testing requirement.  [Rule 62-296.320(4)(b), F.A.C.]

- Unconfined Particulate Matter.  No person shall cause, let, permit, suffer or allow the emissions of unconfined particulate matter from any activity, including vehicular movement; transportation of materials; construction; alteration; demolition or wrecking; or industrially related activities such as loading, unloading, storing or handling; without taking reasonable precautions to prevent such emissions.  Reasonable precautions to prevent emissions of unconfined particulate matter at this facility include:

  - Paving and maintenance of all process and storage areas.

  - Paving and maintenance of the majority of material transfer routes.

  - Application of water or chemicals to control fugitive emissions from road traffic as necessary.

  - Removal of PM from roads and other paved areas to prevent re-entrainment.

  - Landscaping or planting vegetation.

  - Exercise good housekeeping practices at all times.

  - Confining abrasive blasting where possible.

[Rule 62-296.320(4)(c), F.A.C.; and, proposed by applicant in Title V air operation permit renewal application received May 19, 2017.]

Reports and Fees

See Appendix RR, Facility-wide Reporting Requirements, for additional details and requirements.

- Electronic Annual Operating Report and Title V Annual Emissions Fees.  The information required by the Annual Operating Report for Air Pollutant Emitting Facility [Including Title V Source Emissions Fee Calculation] (DEP Form No. 62-210.900(5)) shall be submitted by April 1 of each year, for the previous calendar year, to the Department of Environmental Protection’s Division of Air Resource Management.  Each Title V source shall submit the annual operating report using the DEP’s Electronic Annual Operating Report (EAOR) software, unless the Title V source claims a technical or financial hardship by submitting DEP Form No. 62-210.900(5) to the DEP Division of Air Resource Management instead of using the reporting software. Emissions shall be computed in accordance with the provisions of subsection 62-210.370(2), F.A.C.  Each Title V source must pay between January 15 and April 1 of each year an annual emissions fee in an amount determined as set forth in subsection 62-213.205(1), F.A.C.  The annual fee shall only apply to those regulated pollutants, except carbon monoxide and greenhouse gases, for which an allowable numeric emission-limiting standard is specified in the source’s most recent construction permit or operation permit.  Upon completing the required EAOR entries, the EAOR Title V Fee Invoice can be printed by the source showing which of the reported emissions are subject to the fee and the total Title V Annual Emissions Fee that is due.  The submission of the annual Title V emissions fee payment is also due (postmarked) by April 1st of each year.  A copy of the system-generated EAOR Title V Annual Emissions Fee Invoice and the indicated total fee shall be submitted to:  Major Air Pollution Source Annual Emissions Fee, P.O. Box 3070, Tallahassee, Florida  32315-3070.  Additional information is available by accessing the Title V Annual Emissions Fee On-line Information Center at the following Internet web site:  http://www.dep.state.fl.us/air/emission/tvfee.htm.  [Rules 62-210.370(3), 62-210.900 & 62-213.205, F.A.C.; and, §403.0872(11), Florida Statutes (2013)]

{Permitting Note:  Resources to help you complete your AOR are available on the electronic AOR (EAOR) website at:  http://www.dep.state.fl.us/air/emission/eaor.  If you have questions or need assistance after reviewing the information posted on the EAOR website, please contact the Department by phone at (850) 717-9000 or email at eaor@dep.state.fl.us.}

{Permitting Note:  The Title V Annual Emissions Fee form (DEP Form No. 62-213.900(1)) has been repealed.  A separate Annual Emissions Fee form is no longer required to be submitted by March 1st each year.}

- Annual Statement of Compliance.  The permittee shall submit an annual statement of compliance to the compliance authority at the address shown on the cover of this permit and to the US. EPA at the address shown below within 60 days after the end of each calendar year during which the Title V air operation permit was effective.  (See also Appendix RR, Conditions RR1 and RR7.)  [Rules 62-213.440(3)(a)2. & 3. and (b), F.A.C.]

U.S. Environmental Protection Agency, Region 4

Atlanta Federal Center

61 Forsyth Street, SW

Atlanta, Georgia  30303

Attn:  Air Enforcement Branch

FW9.	Prevention of Accidental Releases (Section 112(r) of CAA).  If, and when, the facility becomes subject to 112(r), the permittee shall:

a.	Submit its Risk Management Plan (RMP) to the Chemical Emergency Preparedness and Prevention Office (CEPPO) RMP Reporting Center.  Any Risk Management Plans, original submittals, revisions or updates to submittals, should be sent electronically through EPA’s Central Data Exchange system at the following address:  https://cdx.epa.gov.  Information on electronically submitting risk management plans using the Central Data Exchange system is available at:  http://www2.epa.gov/rmp.  The RMP Reporting Center can be contacted at:  RMP Reporting Center, Post Office Box 10162, Fairfax, VA  22038, Telephone:  (703) 227-7650.

b.	Submit to the permitting authority Title V certification forms or a compliance schedule in accordance with Rule 62-213.440(2), F.A.C.

[40 CFR 68]

- Semi-Annual Monitoring Reports.  The permittee shall monitor compliance with the terms and conditions of this permit and shall submit reports of any deviations from the requirements of these conditions at least every six (6) months.  All instances of deviations from permit requirements must be clearly identified in such reports, including reference to the specific requirement and the duration of such deviation.  All reports shall be accompanied by a certification by a responsible official, pursuant to subsection 62-213.420(4), F.A.C.  (See also Conditions RR2. – RR4. of Appendix RR, Facility-wide Reporting Requirements, for additional reporting requirements related to deviations.)  [Rule 62-213.440(1)(b)3.a., F.A.C.]

{Permitting Note:  EPA has clarified that, pursuant to 40 CFR 70.6(a)(3), the word “monitoring” is used in a broad sense and means monitoring (i.e., paying attention to) the compliance of the source with all emissions limitations, standards, and work practices specified in the permit.}

Table of Contents

The specific conditions in this section apply to the following emissions unit(s):

| EU No. | Brief Description |
| --- | --- |
| 001 | Nominal 170 MW simple cycle combustion turbine-electrical generator #1 |
| 002 | Nominal 170 MW simple cycle combustion turbine-electrical generator #2 |
| 003 | Nominal 170 MW simple cycle combustion turbine-electrical generator #3 |
| 004 | Nominal 170 MW simple cycle combustion turbine-electrical generator #4 |

Each of the four emission units consist of a dual-fuel nominal 170 MW General Electric PG7241FA combustion turbine-electrical generator.  Nitrogen oxide (NOX) emissions are controlled by dry low-NOX (DLN-2.6) combustors when firing natural gas and wet injection when firing distillate oil.  Inherently clean fuels and good combustion practices are employed to control all pollutants.  A continuous emissions monitoring system (CEMS) for NOX is installed on each unit.  These emissions units are regulated under:  Phase II of the federal Acid Rain Program; NSPS Subpart A (General Provisions) and Subpart GG (Stationary Gas Turbines) in 40 CFR 60; and Rule 62-212.400(PSD), F.A.C.  Permit No. PSD-FL-275 (0490043-001-AC) specified emissions standards representing the Best Available Control Technology (BACT) for the following pollutants:  carbon monoxide (CO), NOX, particulate matter (PM), PM ≤ 10 microns (PM10), sulfuric acid mist (SAM), sulfur dioxide (SO2), and volatile organic compounds (VOC).  Although water injection is used for NOX control, a Compliance Assurance Monitoring (CAM) plan is not required because compliance is demonstrated by CEMS data.  Each unit has a 75-foot-high, 23-foot-diameter stack with a temperature of 1,113ºF and a flow of 2,646,000 acfm (300,000 dscfm).  This facility began commercial operations on June 1, 2002.

Essential Potential to Emit (PTE) Parameters

- Permitted Capacity.  The maximum heat input rates shall not exceed 1612 million Btu per hour (MMBtu/hr) when firing natural gas or 1806 MMBtu/hr when firing No. 2 or superior grade of distillate fuel oil based on the lower heating value (LHV) of each fuel at ambient conditions of 59°F temperature, 60% relative humidity, 100% load, and 14.7 psi pressure.  These maximum heat input rates will vary depending upon ambient conditions and the combustion turbine characteristics.  [Rules 62-210 (PTE) and 62-212.400 (PSD), F.A.C.; Permit No. 0490043-001-AC/PSD-FL-275]

- Emissions Unit Operating Rate Limitation After Testing.  See the related testing provisions in Appendix TR, Facility-wide Testing Requirements.  [Rule 62-297.310(3), F.A.C.]

- Methods of Operation – Fuels.  The combustion turbines shall fire natural gas as the primary fuel, which shall contain no more than 1 grain of sulfur per 100 standard cubic feet of natural gas.  As a restricted alternate fuel, the combustion turbines may fire distillate oil containing no more than 0.05% sulfur by weight.  The amount of distillate oil burned at the site in BTU shall not exceed the amount of natural gas burned at the site in BTU during any consecutive 12-month period.  [Rule 62-212.400 (BACT), F.A.C. Permit No. 0490043-001-AC/PSD-FL-275]

- Hours of Operation.  The four stationary gas turbines shall only operate up to an average of 3,390 hours, including up to a maximum average of 1,000 hours on fuel oil, during any calendar year, to be determined as the average operation across all four combustion turbines, and no single unit may operate more than 5,000 hours per year.  [Rules 62-210.200(PTE) and 62-212.400(PSD), F.A.C.; Permit No. 0490043-010-AC/PSD-FL-275B]

Control Technology

- Combustion Controls.  Dry low-NOX (DLN-2.6) combustors shall be operated on the stationary combustion turbines to control NOX emissions while firing natural gas.  [Rule 62-212.400 (PSD), F.A.C.; Permit No. 0490043-001-AC/PSD-FL-275]

- Water Injection.  A water injection system shall be operated when firing No. 2 or superior grade distillate fuel oil for control of NOX emissions.  [Rule 62-212.400 (PSD), F.A.C.; Permit No. 0490043-001-AC/PSD-FL-275]

- Control System Characteristics.  DLN systems shall each be operated to optimize emissions reductions consistent with normal operation and maintenance practices and shall be maintained to minimize NOX and CO emissions, consistent with normal operation and maintenance practices.  Operation of the DLN systems in the diffusion-firing mode shall be minimized when firing natural gas.  [Rule 62-210.650, F.A.C.; Permit No. 0490043-001-AC/PSD-FL-275]

Emission Limitations and Standards

Unless otherwise specified, the averaging times for Specific Conditions A.8. through A.18. are based on the specified averaging time of the applicable test method.

- Visible Emissions.  Visible emissions from each combustion turbine shall not exceed 10 percent opacity.  Compliance with this limit shall be demonstrated using EPA Method 9.  [Rule 62-212.400 (BACT), F.A.C.; Permit No. 0490043-001-AC/PSD-FL-275]

- CO Emissions.  Carbon monoxide emissions from each combustion turbine when combusting natural gas shall exceed neither 12.0 parts per million by volume, dry, (ppmvd) nor 42.5 lb/hour (at ISO conditions).  Compliance with these limits shall be demonstrated using EPA Method 10.  [Rule 62-212.400 (BACT), F.A.C.; Permit No. 0490043-001-AC/PSD-FL-275]

- CO Emissions.  Carbon Monoxide emissions from each combustion turbine when combusting oil shall exceed neither 20.0 ppmvd nor 71.4 lb/hour (at ISO conditions).  Compliance with these limits shall be demonstrated using EPA Method 10.  [Rule 62-212.400 (BACT), F.A.C.; Permit No. 0490043-001-AC/PSD-FL-275]

- NOx Emissions.  Nitrogen oxide emissions from each combustion turbine when combusting natural gas shall exceed neither 9.0 ppmvd @ 15% O2 nor 64.1 lb/hour (at ISO conditions).  Compliance with these limits shall be demonstrated using a continuous emissions monitor, 24-hour block average.  [Rule 62-212.400 (BACT), F.A.C.; Permit No. 0490043-001-AC/PSD-FL-275]

- NOx Emissions.  Nitrogen oxide emissions from each combustion turbine when combusting oil shall exceed neither 42 ppmvd @ 15% O2 nor 351.0 lb/hour (at ISO conditions).  Compliance with these limits shall be demonstrated using a continuous emissions monitor, 3-hour rolling average.  The permittee shall develop a NOX reduction plan in the subsequent calendar year following when the hours of oil firing exceed 1000 hours in a single calendar year for any one turbine.  This plan shall include a testing protocol designed to establish the maximum water injection rate and the lowest NOX emissions possible without affecting the actual performance of the gas turbine.  The testing protocol shall set a range of water injection rates and attempt to quantify the corresponding NOX emissions for each rate and noting any problems with performance.  Based on the test results, the plan shall recommend a new NOX emissions limiting standard and shall be submitted to the Department’s Office of Permitting and Compliance and the Compliance Authority for review.  If the Department determines that a lower NOX emissions standard is warranted for oil firing, this permit shall be revised.  [Rule 62-212.400 (BACT), F.A.C.; Permit No. 0490043-001-AC/PSD-FL-275]

- PM/PM10 Emissions.  Emissions of particulate matter and particulate matter less than 10 microns from each combustion turbine when combusting natural gas shall not exceed 10.0 lb/hour.  Compliance with this limit shall be demonstrated by complying with the visible emissions limit.  [Rule 62-212.400 (BACT), F.A.C.; Permit No. 0490043-001-AC/PSD-FL-275]

- PM/PM10 Emissions.  Emissions of particulate matter and particulate matter less than 10 microns from each combustion turbine when combusting oil shall not exceed 17.0 lb/hour.  Compliance with this limit shall be demonstrated by complying with the visible emissions limit.  [Rule 62-212.400 (BACT), F.A.C.; Permit No. 0490043-001-AC/PSD-FL-275]

- SO2 and SAM.  Emissions of sulfur dioxide and sulfuric acid mist when combusting natural gas shall be limited by firing gas with a sulfur content not to exceed 1 grain sulfur/100 SCF of gas.  Emissions of SO2 while firing natural gas shall not exceed 5 lb/hr (at ISO conditions).  Compliance with these limits shall be demonstrated through record keeping with the fuel specification serving as a surrogate.  [Rule 62-212.400 (BACT), F.A.C.; Permit No. 0490043-001-AC/PSD-FL-275]

- SO2 and SAM.  Emissions of sulfur dioxide and sulfuric acid mist when combusting fuel oil shall be limited by firing No. 2 or superior oil with a sulfur content not to exceed 0.05 percent by weight.  Emissions of SO2 while firing oil shall not exceed 98.7 lb/hr (at ISO conditions).  Compliance with these limits shall be demonstrated through record keeping with the fuel specification serving as a surrogate.  [Rule 62-212.400 (BACT), F.A.C.; Permit No. 0490043-001-AC/PSD-FL-275]

- VOC.  Volatile organic compound emissions from each combustion turbine when combusting natural gas shall exceed neither 1.4 ppmvw (parts per million by volume, wet) nor 2.8 lb/hour (at ISO conditions).  Compliance with these limits shall be demonstrated by complying with the carbon monoxide emissions limit.  [Rule 62-212.400 (BACT), F.A.C.; Permit No. 0490043-001-AC/PSD-FL-275]

- VOC.  Volatile organic compound emissions from each combustion turbine when combusting oil shall exceed neither 7 ppmvw and 16.2 lb/hour (at ISO conditions).  Compliance with these limits shall be demonstrated by complying with the carbon monoxide emissions limit.  [Rule 62-212.400 (BACT), F.A.C.; Permit No. 0490043-001-AC/PSD-FL-275]

Excess Emissions

Rule 62-210.700 (Excess Emissions), F.A.C. cannot vary any requirement of an NSPS, NESHAP or Acid Rain program provision.

- Excess Emissions.  Excess emissions resulting from startup, shutdown or malfunction shall be permitted provided that best operational practices to minimize emissions are adhered to and the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  Operation below 50% output shall be limited to 2 hours per unit cycle (breaker closed to breaker open), except for Dry Low-NOX (DLN) tuning events.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown or malfunction shall be prohibited.  [Rule 62-210.700(1), F.A.C.; Permit Nos. 0490043-001-AC/PSD-FL-275 and 0490043-010-AC/PSD-FL-275B]

{Permitting note:  The BACT limits for these units were established in Permit No. 0490043-001-AC/PSD-FL-275, in December 1999.  By Rule 62-210.700(7), F.A.C., Rule 62-210.700(1), F.A.C., applies to these units.}

Continuous Monitoring Requirements

- NOX CEMS.  Continuous compliance with the NOX emissions standard (ppmvd @ 15% O2) shall be demonstrated with data collected from the required CEMS.  [Rule 62-212.400 (PSD), F.A.C.; 40 CFR 60 Subpart GG; Permit No. 0490043-001-AC/PSD-FL-275]

- NOx CEMS.  The permittee shall operate a CEMS to measure and record the emissions of NOX from each combustion turbine in a manner sufficient to demonstrate continuous compliance with the CEMS emission standards of this section.

- NOX Monitor:  Each NOX monitor shall be certified pursuant to the specifications of 40 CFR 75 and comply with the applicable requirements of 40 CFR 60 Subpart GG.  Quality assurance procedures shall conform to the requirements of 40 CFR 75.  The annual and required RATA tests required for the NOX monitor shall be performed using EPA Method 20 or 7E in Appendix A of 40 CFR 60.

- Diluent Monitor:  The oxygen (O2) or carbon dioxide (CO2) content of the flue gas shall be monitored at the location where NOX is monitored to correct the measured emissions rates to 15% oxygen.  If a CO2 monitor is installed, the oxygen content of the flue gas shall be calculated using F-factors that are appropriate for the fuel fired.  Each monitor shall comply with the performance and quality assurance requirements of 40 CFR 75.

- Continuous Operation:  All CEMS shall be in continuous operation except for breakdowns, repairs, calibration checks, and zero and span adjustments.  The CEMS shall meet minimum frequency of operation requirements:  one cycle of operation (sampling, analyzing, and data recording) for each successive 15-minute period.  Data recorded during periods of continuous monitoring system breakdowns, repairs, calibration checks, and zero and span adjustments shall not be included in the data average.  A separate 24-hour block compliance determination is conducted at the end of each operating day, and a new average emission rate is calculated from the arithmetic average of all valid hourly emission rates from the previous operating day.  A valid hourly emission rate shall be calculated for each hour in which at least two NOX concentrations are obtained at least 15 minutes apart.  Valid hourly emissions rates shall not include the startup, shutdown, or malfunction data excluded pursuant to Specific Condition A.19. or A.22; these excess emissions periods shall be reported as required by Specific Conditions A.26 and A.27.

[Rule 62-212.400 (PSD), F.A.C.; Permit No. 0490043-001-AC/PSD-FL-275]

- DLN Tuning.  Data collected by the NOX CEMS during a DLN tuning session may be excluded from demonstrations of compliance with the numerical NOX BACT emission limit, provided the tuning session is performed in accordance with the manufacturer's specifications or determined best practices.  Prior to performing any tuning session, the permittee shall provide the Compliance Authority with advance notice that details the activity and proposed tuning schedule.  The notice may be by telephone, facsimile transmittal, or electronic mail.  The permittee shall operate the NOX CEMS during all DLN tuning sessions, and the permittee shall comply with NSPS Subpart GG at all times.  [Permit No. 0490043-010-AC/PSD-FL-275B; Rule 62-210.710(2)(b), F.A.C.]

{Permitting note:  NSPS Subpart GG applies during periods of DLN tuning.}

Test Methods and Procedures

- Test Methods.  When required, tests shall be performed in accordance with the following reference methods:

| Method | Description of Method and Comments |
| --- | --- |
| 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| 7E | Determination of Nitrogen Oxide Emissions from Stationary Sources |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |
| 10 | Determination of Carbon Monoxide Emissions from Stationary Sources {Note: The method shall be based on a continuous sampling train.} |
| 20 | Determination of Nitrogen Oxides, Sulfur Dioxide and Diluent Emissions from Stationary Gas Turbines |

The above methods are described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Rule 62-297.401, F.A.C.; Permit No. 0490043-001-AC/PSD-FL-275; and, 40 CFR 60, Subpart GG]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- Annual Compliance Tests Required.  During each calendar year (January 1 to December 31), annual compliance tests shall be performed for CO and visible emissions for each unit operating more than 400 hours when firing natural gas or for each unit operating for more than 400 hours when firing distillate oil.  The testing shall be conducted during the same calendar year in which the 400 hours will be exceeded.  [Rule 62-297.310(8), F.A.C.; Permit Nos. 0490043-001-AC/PSD-FL-275, 0490043-006-AC/PSD-FL-275A, and 0490043-010-AC/PSD-FL-275B]

Recordkeeping and Reporting Requirements

- Excess Emissions Reports, BACT Standards.

- Malfunctions:  If excess emissions occur due to malfunction, the owner or operator shall notify the Compliance Authority within one working day of:  the nature, extent, and duration of the excess emissions; the cause of the excess emissions; and the actions taken to correct the problem.  In addition, the Compliance Authority may request a written summary report of the incident.  [Rule 62-210.700(5), F.A.C.; Permit No. 0490043-001-AC/PSD-FL-275]

- Exceedances of NOX BACT Standards:  Periods when NOX emissions are above a BACT standard (Specific Condition A.11 or A.12) shall be reported to the Compliance Authority within one working day (verbally) followed up by a written explanation not later than three working days.  [Permit No. 0490043-001-AC/PSD-FL-275]

- Excess Emissions Report, NSPS Standards.  Within 30 days following each calendar quarter, the permittee shall submit to the Compliance Authority a report including any applicable periods of excess emissions and monitoring systems performance, as defined in 40 CFR 60, Subpart GG (Standards of Performance for Stationary Combustion Turbines), that occurred during the previous quarter.  Following the format in 40 CFR 60.7, periods of startup, shutdown, malfunction, shall be monitored, recorded, and reported as excess emissions when emission levels exceed the NSPS Subpart GG standards.  [40 CFR 60.7(c), 60.332, and 60.334; Permit No. 0490043-001-AC/PSD-FL-275]

- Fuel Sulfur Records.  The permittee shall monitor fuel sulfur in accordance with 40 CFR 60 Subpart GG as summarized in Appendix NSPS Subpart GG of this permit.  [40 CFR 60, Subpart GG]

- Relative Accuracy Test Assessments (RATA).  At least 15 days prior to conducting any RATA on a CEMS, the permittee shall provide written notification to the Compliance Authority of the schedule by letter, e-mail or fax.  A summary of the RATA reports shall be provided to the Compliance Authority within 45 days of the completion of the last run.  [Rules 62-212.400 (PSD) and 62-297.310(9) & (10)(a), F.A.C.; Permit No. 0490043-001-AC/PSD-FL-275]

- Records.  All measurements, records, and other data required to be maintained by the owner or operator shall be recorded in a permanent form and retained for at least five years following the date on which such measurements, records, or data are recorded.  These records shall be made available to the Department upon request.  [Permit No. 0490043-001-AC/PSD-FL-275]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440(1)(b), F.A.C.]

Other Requirements

- Operating Procedures. Operating procedures shall include good operating practices and proper training of all operators and supervisors.  The good operating practices shall meet the guidelines and procedures as established by the equipment manufacturers.  All operators (including supervisors) of air pollution control devices shall be properly trained in plant-specific equipment.  [Rule 62-4.070(3), F.A.C. and Permit No. 0490043-001-AC/PSD-FL-275]

- NSPS Provisions.  The emissions units are also subject to the applicable provisions of Subpart A (General Provisions) and Subpart GG (Stationary Gas Turbines) in 40 CFR 60.  These provisions are provided in the attached appendices.  [Rule 62-204.800, F.A.C. and Subpart A and GG in 40 CFR 60]

Table of Contents

The specific conditions in this section apply to the following emissions units:

| EU No. | ## Brief Description |
| --- | --- |
| 007 | Clarke Model JDFP-06WA diesel-fired fire protection system |
| 008 | Generac Power Systems, Inc. Model 12.0 DTA emergency generator set |
| 009 | Generac Power Systems, Inc. Model 12.0 DTA emergency generator set |
| 010 | Generac Power Systems, Inc. Model 12.0 DTA emergency generator set |
| 011 | Generac Power Systems, Inc. Model 12.0 DTA emergency generator set |

The following table provides important details for these emissions units:

| E.U. ID No. | Engine Brake HP | Date of Construction | Manufacture Date | Displacement liters/cylinder(l/c) |
| --- | --- | --- | --- | --- |
| 007 | 265 | Before 6/12/2006 | May 2005 | 1.35 |
| 008 | 555 | Before 6/12/2006 | September 2001 | 2.0 |
| 009 | 555 | Before 6/12/2006 | September 2001 | 2.0 |
| 010 | 555 | Before 6/12/2006 | September 2001 | 2.0 |
| 011 | 555 | Before 6/12/2006 | September 2001 | 2.0 |

{Permitting Note: These emissions units, compression ignition (CI) engines, are regulated under 40 CFR 63, Subpart ZZZZ, NESHAP for Stationary RICE adopted in Rule 62.204.800(11)(b), F.A.C.  These RICE are emergency engines.  This permit section addresses “existing” emergency stationary CI RICE that are located at an Area source of HAPs and that have not been modified or reconstructed after 6/12/2006.}

Essential Potential to Emit (PTE) Parameters

- Hours of Operation

  - Emergency Situations.  There is no time limit on the use of emergency stationary RICE in emergency situations.  [40 CFR 63.6640(f)(1)]

  - Maintenance and Testing.  Each RICE is authorized to operate for the purpose of maintenance checks and readiness testing, provided that the tests are recommended by federal, state or local government, the manufacturer, the vendor, or the insurance company associated with the engine. Maintenance checks and readiness testing of such units is limited to 100 hours per year.  [40 CFR 63.6640(f)(2)]

Emission Limitations and Operating Requirements

- Work or Management Practice Standards.

- Oil.  Change oil and filter every 500 hours of operation or annually, whichever comes first.  [40 CFR 63.6603 & Table 2d.4.a. of Subpart ZZZZ]

- Air Cleaner.  Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first and replace as necessary.  [40 CFR 63.6603 & Table 2d.4.b. of Subpart ZZZZ]

- Hoses and Belts.  Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary.  [40 CFR 63.6603 & Table 2d.4.c. of Subpart ZZZZ]

- Operation and Maintenance.  Operate and maintain the stationary RICE according to the manufacturer's emission-related operation and maintenance instructions or develop and follow your own maintenance plan which must provide, to the extent practicable for the maintenance and operation of the engine in a manner consistent with good air pollution, control practice for minimizing emissions.  [40 CFR 63.6625(e), 63.6640(a) & Table 6.9.a. of Subpart ZZZZ]

- Engine Startup.  During periods of startup the owner or operator must minimize the engine's time spent at idle during startup and minimize the engine's startup time to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes.  [40 CFR 63.6625(h)]

- Oil Analysis.  The owner or operator has the option of using an oil analysis program to extend the oil change requirement.  The oil analysis must be performed at the same frequency specified for changing the oil in paragraph a., above.  The analysis program must at a minimum analyze the following three parameters:  Total Base Number, viscosity, and percent water content.  The condemning limits for these parameters are as follows:  Total Base Number is less than 30 percent of the Total Base Number of the oil when new; viscosity of the oil has changed by more than 20 percent from the viscosity of the oil when new; or percent water content (by volume) is greater than 0.5.  If all of these condemning limits are not exceeded, the engine owner or operator is not required to change the oil.  If any of the limits are exceeded, the engine owner or operator must change the oil within 2 days of receiving the results of the analysis; if the engine is not in operation when the results of the analysis are received, the engine owner or operator must change the oil within 2 days or before commencing operation, whichever is later.  The owner or operator must keep records of the parameters that are analyzed as part of the program, the results of the analysis, and the oil changes for the engine.  The analysis program must be part of the maintenance plan for the engine.  [40 CFR 63.6625(i)]

Monitoring of Operations

- Hour Meter.  The owner or operator must install a non-resettable hour meter if one is not already installed.  [40 CFR 63.6625(f)]

Compliance

- Continuous Compliance.  Each unit shall be in compliance with the emission limitations and operating standards in this section at all times.  [40 CFR 63.6605(a)]

- Operation and Maintenance of Equipment.  At all times the owner or operator must operate and maintain, any affected source, including associated air pollution control equipment and monitoring equipment, in a manner consistent with safety and good air pollution control practices for minimizing emissions.  Determination of whether such operation and maintenance procedures are being used will be based on information available to the compliance authority which may include, but is not limited to, monitoring results, review of operation and maintenance procedures, review of operation and maintenance records, and inspection of the source.  [40 CFR 63.6605(b)]

Recordkeeping Requirements

- Notification, Performance and Compliance Records.  The owner or operator must keep:

- A copy of each notification and report that the owner or operator submitted to comply with this section, including all documentation supporting any Initial Notification or Notification of Compliance Status that the owner or operator submitted.

- Records of the occurrence and duration of each malfunction of operation.

- Records of all required maintenance performed on the hour meter.

- Records of actions taken during periods of malfunction to minimize emissions in accordance with Specific Condition B.5., including corrective actions to restore malfunctioning process and monitoring equipment to its normal or usual manner of operation.

- Records of the actions required in Specific Condition B.2.d. to show continuous compliance with each emission limitation or operating requirement.

- Records of the Work or Management Practice Standards specified in Specific Condition B.2.

- Records of the maintenance conducted in order to demonstrate that the RICE was operated and maintained according to your own maintenance plan.

- Records of the hours of operation of the engine that is recorded through the non-resettable hour meter.  The owner or operator must document how many hours are spent for emergency operation including what classified the operation as emergency and how many hours are spent for non-emergency operation.  If the engines are used for emergency demand response operation or for periods of voltage or frequency deviations, the owner or operator must keep records of the notification of the emergency situation, and the time of engine operation for these purposes.

[40 CFR 63.6655]

- Record Retention.

- The owner or operator must keep records in a suitable and readily available form for expeditious reviews.

- The owner or operator must keep each record readily accessible in hard copy or electronic form for at least 5 years after the date of each occurrence, measurement, maintenance, corrective action, report, or record.

[40 CFR 63.6660 and 40 CFR 63.10(b)(1)]

Reporting Requirements

- Delay of Performing Work Practice Requirements.  If an emergency engine is operating during an emergency and it is not possible to shut down the engine in order to perform the work practice requirements on the schedule required in Specific Condition B.2., or if performing the work practice on the required schedule would otherwise pose an unacceptable risk under federal, state, or local law, the work practice can be delayed until the emergency is over or the unacceptable risk under federal, state, or local law has abated.  The work practice should be performed as soon as practicable after the emergency has ended or the unacceptable risk under federal, state, or local law has abated.  Sources must report any failure to perform the work practice on the schedule required and the federal, state or local law under which the risk was deemed unacceptable.  [40 CFR 63, Subpart ZZZZ, Table 2d, footnote 2]

Table of Contents

Operated by:  Vandolah Power Company, LLC

ORIS Code:  55415

The emissions units listed below are regulated under Acid Rain, Phase II.

| E.U. ID No. | Brief Description |
| --- | --- |
| 001 | Nominal 170 MW simple cycle combustion turbine-electrical generator #1 |
| 002 003 004 | Nominal 170 MW simple cycle combustion turbine-electrical generator #2 Nominal 170 MW simple cycle combustion turbine-electrical generator #3 Nominal 170 MW simple cycle combustion turbine-electrical generator #4 |

A.1.	The Phase II Acid Rain Part application submitted for this facility, as approved by the Department, is a part of this permit.  The owners and operators of these Phase II acid rain units must comply with the standard requirements and special provisions set forth in the application listed below:

DEP Form No. 62-210.900(1)(a), dated 04/10/2017, received 05/19/2017.

[Chapter 62-213, F.A.C. and Rule 62-214.320, F.A.C.]

A.2.	Sulfur Dioxide (SO2) Emission Allowances.  SO2 emissions from sources subject to the Federal Acid Rain Program (Title IV) shall not exceed any allowances that the source lawfully holds under the Federal Acid Rain Program.  Allowances shall not be used to demonstrate compliance with a non-Title IV applicable requirement of the Act.

a.	No permit revision shall be required for increases in emissions that are authorized by allowances acquired pursuant to the Federal Acid Rain Program, provided that such increases do not require a permit revision pursuant to Rule 62-213.400(3), F.A.C.

b.	No limit shall be placed on the number of allowances held by the source under the Federal Acid Rain Program.

c.	Allowances shall be accounted for under the Federal Acid Rain Program.

[Rule 62-213.440(1)(c)1., 2. & 3., F.A.C.]

A.3.	Comments, Notes, and Justifications:  None.

Table of Contents