Title V Air Operation Permit Renewal

Permit No. 0490043-011-AV

Applicant

The applicant for this project is Vandolah Power Company, LLC.  The applicant’s responsible official and mailing address are:  Douglas Jensen, Plant Manager, Vandolah Power Company, LLC, 2394 Vandolah Road, Wauchula, Florida 33873.

Facility Description

The applicant operates the existing Vandolah Power Project, which is in Hardee County at 2394 Vandolah Road, Wauchula, Florida.

The facility consists of four dual-fuel, nominal 170-megawatt (MW) General Electric model PG7241FA combustion turbine-electric generators with evaporative inlet coolers and two 2.8 million gallon fuel oil storage tanks.  Each combustion turbine can fire both natural gas and distillate fuel oil.  The combustion turbine units can operate in simple cycle mode and intermittent duty mode.  NOX emissions are controlled by dry low NOX combustors when firing natural gas and water injection when firing distillate oil (No. 2 oil or superior).  The facility also includes four diesel-fueled emergency generators and one diesel-fueled fire pump engine.

This facility also includes miscellaneous insignificant emissions units and/or activities.

regulated Emissions Unit IDentification Numbers and descriptions

| EU No. | ## Brief Description |
| --- | --- |
| 001 | 170 MW simple cycle combustion turbine-electrical generator |
| 002 | 170 MW simple cycle combustion turbine-electrical generator |
| 003 | 170 MW simple cycle combustion turbine-electrical generator |
| 004 | 170 MW simple cycle combustion turbine-electrical generator |
| 007 | Clarke Model JDFP-06WA diesel-fired fire protection system |
| 008 | Generac Power Systems, Inc. Model 12.0 DTA emergency generator set |
| 009 | Generac Power Systems, Inc. Model 12.0 DTA emergency generator set |
| 010 | Generac Power Systems, Inc. Model 12.0 DTA emergency generator set |
| 011 | Generac Power Systems, Inc. Model 12.0 DTA emergency generator set |

Applicable Regulations

Based on the Title V air operation permit renewal application received on May 19, 2017, this facility is not a major source of hazardous air pollutants (HAP).  The existing facility is a prevention of significant deterioration (PSD) major source of air pollutants in accordance with Rule 62-212.400, F.A.C.  A summary of applicable regulations is shown in the following table:

| Regulation | EU No(s). |
| --- | --- |
| Federal Rule Citations |  |
| 40 CFR 60, Subpart A, NSPS General Provisions | 001, 002, 003, 004 |
| 40 CFR 60, Subpart GG, Standards of Performance for Stationary Gas Turbines | 001, 002, 003, 004 |
| 40 CFR 63, Subpart A, General Provisions | 007, 008, 009, 010, 011 |
| 40 CFR 63, Subpart ZZZZ, National Emissions Standards For Hazardous Air Pollutants For Stationary Reciprocating Internal Combustion Engines | 007, 008, 009, 010, 011 |
| 40 CFR 75 Acid Rain Monitoring Provisions | 001, 002, 003, 004 |
| State Rule Citations |  |
| Rule 62-4, Florida Administrative Code (F.A.C.) (Permitting Requirements) | 001, 002, 003, 004, 007, 008, 009, 010, 011 |
| Rule 62-204, F.A.C. (Ambient Air Quality Requirements, PSD Increments, and Federal Regulations Adopted by Reference) | 001, 002, 003, 004 |
| Rule 62-210, F.A.C. (Permits Required, Public Notice, Reports, Stack Height Policy, Circumvention, Excess Emissions, and Forms) | 001, 002, 003, 004, 007, 008, 009, 010, 011 |
| Rule 62-212, F.A.C. (Preconstruction Review, PSD Review and Best Available Control Technology (BACT)) | 001, 002, 003, 004 |
| Rule 62-213, F.A.C. (Title V Air Operation Permits for Major Sources of Air Pollution) | 001, 002, 003, 004, 007, 008, 009, 010, 011 |
| Rule 62-214, F.A.C. (Requirements for Sources Subject To The Federal Acid Rain Program) | 001, 002, 003, 004 |
| Rule 62-296, F.A.C. (Emission Limiting Standards) | 001, 002, 003, 004, 007, 008, 009, 010, 011 |
| Rule 62-297, F.A.C. (Test Methods and Procedures, Continuous Monitoring Specifications, and Alternate Sampling Procedures) | 001, 002, 003, 004 |

This facility also includes miscellaneous insignificant emissions units and/or activities.

Project DESCRIPTION

The purpose of this permitting project is to renew Title V permit for the above referenced facility.

Processing Schedule and Related Documents

Initial Title V Air Operation Permit issued January 1, 2003

Title V Air Operation Permit No. 0490043-009-AV effective January 1, 2013

Application for a Title V Air Operation Permit Renewal received May 19, 2017

Primary Regulatory requirements

Standard Industrial Classification (SIC) Code:  4911 – Electrical Generation.

North American Industry Classification System (NAICS):  221112 – Fossil Fuel Electric Power Generation.

HAP:  The facility is not identified as a major source of hazardous air pollutants (HAP).

Title IV:  The facility operates units subject to the acid rain provisions of the Clean Air Act.

Title V:  The facility is a Title V major source of air pollution in accordance with Chapter 62-213, Florida Administrative Code (F.A.C.).

PSD:  The facility is a Prevention of Significant Deterioration (PSD)-major source of air pollution in accordance with Rule 62-212.400, F.A.C.

NSPS:  The facility operates units subject to the New Source Performance Standards (NSPS) of 40 Code of Federal Regulations (CFR) 60.

NESHAP:  The facility operates units subject to the National Emissions Standards for Hazardous Air Pollutants (NESHAP) of 40 CFR 63.

CAM:  Compliance Assurance Monitoring (CAM) does not apply to any of the units at the facility.

PROJECT REVIEW

The following changes have been made in this permit renewal.

- The provisions of Permit No. 0490043-010-AC/PSD-FL-275B have been incorporated.  This air construction permit created an allowance for NOX CEMS data collected during Dry Low-NOX tuning sessions to be excluded from demonstrations of compliance with the state emissions limit for NOX.  The permit also shifted required stack testing from a federal fiscal year basis to a calendar year basis.  The permit also resolved a discrepancy between the facility’s air construction permit and Title V permits regarding the averaging of permitted hours of operation across units.

- The condition related to the NOX BACT emission limit for natural gas operation is on a 24-hour block average basis, consistent with the air construction/PSD permitting for these units.  Previous Title V permits had erroneously employed a rolling average, rather than a block average.

- The testing requirements have been clarified, consistent with revisions to Rule 62-297.310, F.A.C.  The turbines are subject to stack test requirements for carbon monoxide and visible emissions in calendar years when the hours of operation on a given fuel (i.e., gas or oil) exceed 400 hours.

- The Acid Rain Part of the permit has been updated with the facility’s most recent Acid Rain application.

- Appendix I, for insignificant emissions units or activities, has been updated based on the application.

- The following appendices have been updated to reflect changes in federal subparts:  NESHAP Subpart A, NESHAP Subpart ZZZZ, NSPS Subpart A, NSPS Subpart GG.

- The following appendices have been updated to reflect changes in the Department’s templates:  Appendix RR, Appendix TR.

- Table H has been updated to reflect the current permitting history.

Conclusion

This project renews Title V air operation permit No. 0490043-009-AV, which was effective on January 1, 2013.  This Title V air operation permit renewal is issued under the provisions of Chapter 403, Florida Statues (F.S.), and Chapters 62-4, 62-210, and 62-213, F.A.C.