## EU -001, -002 & -003
Table 2, Summary of Compliance Requirements
Tampa Electric Company | [5 empty] | Final Permit No. 0570039-061-AV
Big Bend Station | [5 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-001, -002 & -003 | Fossil Fuel Fired Steam Generator Unit Nos. 1 - 3
|  |  | Testing | Frequency | Min. Compliance
Pollutant Name |  | Compliance | Time | Base | Test
or Parameter | Fuel(s) | Method | Frequency | Date * | Duration | CMS** | See permit condition(s)
VE | All | DEP Method 9 | annual & renewal |  | 60 minutes | yes | III.A.43., 47. & 48.
VE-SB | All | DEP Method 9 | annual & renewal |  | 60 minutes | yes | III.A.43., 47. & 48.
PM | All | EPA Method 17, 5, 5B,or 5F | annual & renewal |  | 1 hour |  | III.A.43. & 49.
PM-SB | All | EPA Method 17, 5, 5B,or 5F | annual & renewal |  | 1 hour |  | III.A.43. & 49.
SO2 | #2 Fuel Oil | fuel sampling & analysis | upon each fuel delivery |  |  | yes | III.A.51. & 52.
SO2 | Solid Fuel | CEMS | annual RATA |  |  | yes | III.A.36. & 50.
NOx | Solid Fuel | CEMS | annual RATA |  |  | yes | III.A.37. & 43.
Ammonia slip |  | EPA conditional test method (CTM-027), EPA Method 320 | annual testing if > 5 ppmv |  |  |  | III.A.43. & 53.
CO2 | All |  |  |  |  | yes | III.A.41.
stack gas flow | All |  |  |  |  | yes | III.A.41.
Notes:
* The frequency base date is established for planning purposes only; see Rule 62-297.310, F.A.C.
**CMS [=] continuous monitoring system

## EU -004
Table 2, Summary of Compliance Requirements
Tampa Electric Company | [5 empty] | Final Permit No. 0570039-061-AV
Big Bend Station | [5 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-004 | Fossil Fuel Fired Steam Generator Unit No. 4
|  |  | Testing | Frequency | Min. Compliance
Pollutant Name |  | Compliance | Time | Base | Test
or Parameter | Fuel(s) | Method | Frequency | Date * | Duration | CMS** | See permit condition(s)
VE | All | EPA Method 9 | annual & renewal |  | 60 minutes | yes | III.B.43. & 48.
PM | All | EPA Method 17, 5, 5B,or 5F | annual & renewal |  | 1 hour |  | III.B.49.
SO2 | #2 Fuel Oil | fuel sampling & analysis | upon each fuel delivery |  |  | yes | III.B.51. & 52.
SO2 | Solid Fuel | CEMS | annual RATA |  |  | yes | III.B.35.
NOx | Solid Fuel | CEMS | annual RATA |  |  | yes | III.B.36. & 376.
Ammonia slip |  | EPA conditional test method (CTM-027), EPA Method 320 | annual testing if > 5 ppmv |  |  |  | III.B.53.
CO |  | EPA Method 10 | annual RATA |  |  | yes | III.B.38. & 39.
CO2 | All |  |  |  |  | yes | III.B.41.
stack gas flow | All |  |  |  |  | yes | III.B.41.
Notes:
* The frequency base date is established for planning purposes only; see Rule 62-297.310, F.A.C.
**CMS [=] continuous monitoring system

## EU -007
Table 2, Summary of Compliance Requirements
Tampa Electric Company |  | Final Permit No. 0570039-061-AV
Big Bend Station |  | Facility ID No. 0570039
This Unit was removed from service on 10/26/2010. Refer to Subsection C (reserved to preserve numbering)
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-007 | Combustion Turbine No. 1

## EU -008 ...
Table 2, Summary of Compliance Requirements
Tampa Electric Company | [5 empty] | Final Permit No. 0570039-061-AV
Big Bend Station | [5 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-008 ... | Flyash Handling and Storage - Silo Nos. 1 & 2
|  |  | Testing | Frequency | Min. Compliance
Pollutant Name |  | Compliance | Time | Base | Test
or Parameter | Fuel(s) | Method | Frequency | Date * | Duration | CMS** | See permit condition(s)
-008 &-018 PM |  | EPA Method 5 | waived |  |  |  | III.D.3. & 13.
-008 &-018 VE |  | EPA Method 9 | annual |  | 30 minutes |  | III.D.8. - 11.
-009 &-019 PM |  | EPA Method 5 | waived |  |  |  | III.D.3. & 13.
-009 &-019 VE |  | EPA Method 9 | annual |  | 30 minutes |  | III.D.8. - 11.
-026 VE |  | EPA Method 9 or 22 | not required |  |  |  | FW4.
Notes:
* The frequency base date is established for planning purposes only; see Rule 62-297.310, F.A.C.
**CMS [=] continuous monitoring system

## EU -010, -029 & -030
Table 2, Summary of Compliance Requirements
Tampa Electric Company | [5 empty] | Final Permit No. 0570039-061-AV
Big Bend Station | [5 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-010, -029 & -030 | Solid Fuel Yard
|  |  | Testing | Frequency | Min. Compliance
Pollutant Name |  | Compliance | Time | Base | Test
or Parameter | Fuel(s) | Method | Frequency | Date * | Duration | CMS** | See permit condition(s)
-010 VE |  | EPA Method 9 | annual |  | 30 minutes |  | III. H.7. H.11. - 15.
-029 VE |  | EPA Method 9 | annual |  | 30 minutes |  | III.P.8. - 12.
-030 VE |  | EPA Method 9 | annual |  | 30 minutes |  | III.P.8. - 12.
Notes:

## EU -011 ...
Table 2, Summary of Compliance Requirements
Tampa Electric Company | [5 empty] | Final Permit No. 0570039-061-AV
Big Bend Station | [5 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
011,-012,-013,-023,-025 | Limestone Handling and Storage
|  |  | Testing | Frequency | Min. Compliance
Pollutant Name |  | Compliance | Time | Base | Test
or Parameter | Fuel(s) | Method | Frequency | Date * | Duration | CMS** | See permit condition(s)
-011 VE |  | EPA Method 9 or 22 | not required |  |  |  | FW4.
-012 & -013 PM |  | EPA Method 5 | waived |  |  |  | III.F.8.
-012 & -013 VE |  | EPA Method 9 | annual |  | 30 minutes |  | III.F.16.
-023 PM |  | EPA Method 5 | waived |  |  |  | III.F.7.
-023 VE |  | EPA Method 9 | annual |  | 30 minutes |  | III.F.16.
-020 PM |  | EPA Method 5 | waived |  |  |  | III.F.18.
-020 VE |  | EPA Method 9 | annual |  | 30 minutes |  | III.F.13.
-021 PM |  | EPA Method 5 | waived |  |  |  | III.F.18.
-021 VE |  | EPA Method 9 | annual |  | 30 minutes |  | III.F.13.
-025 VE |  | EPA Method 9 or 22 | not required |  |  |  | FW4.
Notes:
* The frequency base date is established for planning purposes only; see Rule 62-297.310, F.A.C.
**CMS [=] continuous monitoring system

## EU -014, -027 & -028
Table 2, Summary of Compliance Requirements
Tampa Electric Company | [5 empty] | Final Permit No. 0570039-061-AV
Big Bend Station | [5 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-014, -027 & -028 | Flyash Handling and Storage Silo No. 3
|  |  | Testing | Frequency | Min. Compliance
Pollutant Name |  | Compliance | Time | Base | Test
or Parameter | Fuel(s) | Method | Frequency | Date * | Duration | CMS** | See permit condition(s)
-014 & -027 PM |  | EPA Method 5 | waived |  |  |  | III.E.8. - 12.
-014 & -027 VE |  | EPA Method 9 | annual |  | 30 minutes |  | III.E.8. - 12.
-028 VE |  | EPA Method 9 | not required |  |  |  | FW4.
Notes:
* The frequency base date is established for planning purposes only; see Rule 62-297.310, F.A.C.
**CMS [=] continuous monitoring system

## EU -015 ...
Table 2, Summary of Compliance Requirements
Tampa Electric Company | [5 empty] | Final Permit No. 0570039-061-AV
Big Bend Station | [5 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
015, -016, -017, 039 | Coal Bunkers with Roto-Clones
|  |  | Testing | Frequency | Min. Compliance
Pollutant Name |  | Compliance | Time | Base | Test
or Parameter | Fuel(s) | Method | Frequency | Date * | Duration | CMS** | See permit condition(s)
-015 PM |  | EPA Method 5 | waived |  |  |  | III.G.3.
-015 VE |  | EPA Method 9 | annual |  | 30 minutes |  | III.G.6. - 10.
-016 PM |  | EPA Method 5 | waived |  |  |  | III.G.3.
-016 VE |  | EPA Method 9 | annual |  | 30 minutes |  | III.G.6. - 10.
-017 PM |  | EPA Method 5 | waived |  |  |  | III.G.3.
-017 VE |  | EPA Method 9 | annual |  | 30 minutes |  | III.G.6. - 10.
-039 PM |  | EPA Method 5 | waived |  |  |  | III.G.3.
-039 VE |  | EPA Method 9 | annual |  | 30 minutes |  | III.G.6. - 10.
Notes:
* The frequency base date is established for planning purposes only; see Rule 62-297.310, F.A.C.
**CMS [=] continuous monitoring system

## EU -022
Table 2, Summary of Compliance Requirements
Tampa Electric Company | [5 empty] | Final Permit No. 0570039-061-AV
Big Bend Station | [5 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-022 | Lime Silo for Wastewater Treatment Plant with one Baghouse
|  |  | Testing | Frequency | Min. Compliance
Pollutant Name |  | Compliance | Time | Base | Test
or Parameter | Fuel(s) | Method | Frequency | Date * | Duration | CMS** | See permit condition(s)
PM |  | EPA Method 5 | waived |  |  |  | III.L.3., & 11.
VE |  | EPA Method 9 | annual |  | 30 minutes |  | III.L.6., 7. & 10.
Notes:
* The frequency base date is established for planning purposes only; see Rule 62-297.310, F.A.C.
**CMS [=] continuous monitoring system

## EU -032
Table 2, Summary of Compliance Requirements
Tampa Electric Company | [5 empty] | Final Permit No. 0570039-061-AV
Big Bend Station | [5 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-032 | Surface Coating of Miscellaneous Metal Parts
|  |  | Testing | Frequency | Min. Compliance
Pollutant Name |  | Compliance | Time | Base | Test
or Parameter | Fuel(s) | Method | Frequency | Date * | Duration | CMS** | See permit condition(s)
VOC |  | Material balance |  |  |  |  | III.I.7. - 10. & 13.
Notes:
* The frequency base date is established for planning purposes only; see Rule 62-297.310, F.A.C.
**CMS [=] continuous monitoring system

## EU -033 & -034
Table 2, Summary of Compliance Requirements
Tampa Electric Company | [5 empty] | Final Permit No. 0570039-061-AV | Final Permit No. 0570039-061-AV
Big Bend Station | [5 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-033 & -034 | Abrasive Blasting
|  |  | Testing | Frequency | Min. Compliance
Pollutant Name |  | Compliance | Time | Base | Test
or Parameter | Fuel(s) | Method | Frequency | Date * | Duration | CMS** | See permit condition(s)
PM |  | EPA Method 5 | waived |  |  |  | III.J.7., 10. & 11.
VE |  | EPA Method 9 | annual |  | 30 minutes |  | III.J.7. - 10.
Notes:
* The frequency base date is established for planning purposes only; see Rule 62-297.310, F.A.C.
**CMS [=] continuous monitoring system

## EU -035
Table 2, Summary of Compliance Requirements
Tampa Electric Company | [5 empty] | Final Permit No. 0570039-061-AV
Big Bend Station | [5 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-035 | Surface Coating of Ships
|  |  | Testing | Frequency | Min. Compliance
Pollutant Name |  | Compliance | Time | Base | Test
or Parameter | Fuel(s) | Method | Frequency | Date * | Duration | CMS** | See permit condition(s)
VOC |  | Material balance |  |  |  |  | III.K.4.
Notes:
* The frequency base date is established for planning purposes only; see Rule 62-297.310, F.A.C.
**CMS [=] continuous monitoring system

## EU -037 & -038
Table 2, Summary of Compliance Requirements
Tampa Electric Company | [5 empty] | Final Permit No. 0570039-061-AV
Big Bend Station | [5 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-037 & -038 | Coal Residual Storage and Transfer from the Polk Power Station
|  |  | Testing | Frequency | Min. Compliance
Pollutant Name |  | Compliance | Time | Base | Test
or Parameter | Fuel(s) | Method | Frequency | Date * | Duration | CMS** | See permit condition(s)
-037 VE |  | EPA Method 9 | not required |  |  |  | FW4.
-038 VE |  | EPA Method 9 | annual |  | 30 minutes |  | III.M.7. - 11.
Notes:
* The frequency base date is established for planning purposes only; see Rule 62-297.310, F.A.C.
**CMS [=] continuous monitoring system

## EU -041 & -042
Table 2, Summary of Compliance Requirements
Tampa Electric Company | [5 empty] | Final Permit No. 0570039-061-AV
Big Bend Station | [5 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-041 & -042 | Simple Cycle Combustion Turbine
|  |  | Testing | Frequency | Min. Compliance
Pollutant Name |  | Compliance | Time | Base | Test
or Parameter | Fuel(s) | Method | Frequency | Date * | Duration | CMS** | See permit condition(s)
-041 & -042 VE |  | EPA Method 9 | not required |  |  |  | III.O.26
-041 & -042 CO |  | EPA Method 10 |  |  | 3 hr. rolling avg. |  | III.O.27
-041 & -042 NOx |  | EPA Method 7E, 19 &20 | anuual |  |  |  | III.O.28
-041 & -042 SO2 |  | EPA Method 6 or 6C & 8 |  |  |  |  | III.O.30
Notes:
* The frequency base date is established for planning purposes only; see Rule 62-297.310, F.A.C.
**CMS [=] continuous monitoring system

## EU -046 & -047
Table 2, Summary of Compliance Requirements
Tampa Electric Company | [5 empty] | Final Permit No. 0570039-061-AV
Big Bend Station | [5 empty] | Facility ID No. 0570039
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
-046 | Transloading and off site Transfer
-047 | Railroad Unloading and Conveying
|  |  | Testing | Frequency | Min. Compliance
Pollutant Name |  | Compliance | Time | Base | Test
or Parameter | Fuel(s) | Method | Frequency | Date * | Duration | CMS** | See permit condition(s)
-046 VE |  | EPA Method 9 | annual |  | 30 minute |  | III.Q.13
-047 VE |  | EPA Method 9 | annual |  | 30 minute |  | III.R.12
Notes:
* The frequency base date is established for planning purposes only; see Rule 62-297.310, F.A.C.
**CMS [=] continuous monitoring system