Tampa Electric Company

Big Bend Station

Facility ID No. 0570039

Hillsborough County

Title V Air Operation Permit Revision

Final Permit No. 0570039-061-AV

(3rd4th Revision of Title V Air Operation Permit No. 0570039-039-AV)

Permitting Authority

State of Florida

Department of Environmental Protection

Division of Air Resource Management

Mail Station #5505

2600 Blair Stone Road

Tallahassee, Florida  32399-2400

Telephone:  850/717-9000

Fax:  850/717-9097

Compliance Authority

Environmental Protection Commission of Hillsborough County

3629 Queen Palm Drive

Tampa, Florida  33619

Telephone:  813/627-2600

Fax:  813/627-2660

Title V Air Operation Permit Revision

Final Permit No. 0570039-061-AV

Table of Contents

Section	Page Number

Placard Page. 	 1

I.	Facility Information. 	 2

A.	Facility Description. 	2

B. 	Summary of Emissions Units. 	2

C. 	Applicable Requirements.	3

II.	Facility-wide Conditions. 	 6

III. 	Emissions Units and Conditions.

A.	E.U. ID Nos. -001, -002 & -003:  Steam Generators Units Nos. 1, 2 & 3. 	 8

B.	E.U. ID Nos. -004:  Steam Generator Unit No. 4. 	 21

C.	(Reserved).	 31

D.	E.U. ID Nos. -008 &, -018, -009, -019 & -026:  Flyash Handling and Storage - Silo Nos. 1 & 2 
Baghouses. 	 	33

E.	E.U. ID Nos. -014, -027 & -028:  Flyash Handling and Storage - Silo No. 3 Baghouse. 	 36

F.	E.U. ID Nos. -011, -012, -013, -023, -0250, -020 & -021:  Limestone Handling and Storage Baghouses. 				38

G.	E.U. ID Nos. -015, -016, -017 & -039:  Coal Bunkers with Roto-Clones. 	 42

H.	E.U. ID Nos. -010:  Solid Fuel Yard. 	 44

I.	E.U. ID Nos. -032:  Surface Coating of Miscellaneous Metal Parts. 	 48

J.	E.U. ID Nos. -033 & -034:  Abrasive Blasting(Reserved).	 51

K.	E.U. ID Nos. -035:  Surface Coating of Ships(Reserved). 	 53

L.	E.U. ID Nos. -022:  Lime Silo for Wastewater Treatment Plant for the Chloride Bleed Stream. 	 54

M.	E.U. ID Nos. -037 & -038:  Coal Residual Storage and Transfer. 	 56

N.	E.U. ID Nos. -043 & -044:  Diesel Generators (Engines). 	 58

O.	E.U. ID Nos. -041 & -042:  Simple-Cycle Combustion Turbines. 	 61

P.	E.U. ID Nos. -029 & -030:  Solid Fuel Blending and Milling. 	 71

Q.	E.U. ID No. -046:  Transloading and Off-site Transfer of of Solid Fuels and SlagCoal and Petcoke. 	 74

R.	E.U. ID No. -047:  Railcar Unloading and Conveying System. 	 78

S	E.U. ID No. -048:  Supplemental Material Handling J3 Conveyor System	81

IV. 	Acid Rain Part.

A.	Phase II Acid Rain SO2 Application/Compliance Plan. 	 83

B.	Phase II Acid Rain NOX Application/Compliance Plan.	 88

V. 	Clean Air Interstate Rule (CAIR) Part.

A.	E.U. ID Nos. -001, -002, -003 & -004:  Steam Generators Units Nos. 1, 2, 3 & 4. 	 95

B.	Retired Unit Exemptions, E.U. ID Nos. -005 & -006:  Combustion Turbine Nos. 2 & 3. 	 101

VI.	Appendices. 	 110

Appendix A, Glossary.

Appendix BOP, Best Operational Practices for Start up and Shutdown.

Appendix CAM, Compliance Assurance Monitoring Plan.

Appendix CEMS.

Appendix CEMS for E.U. ID Nos. -041 and -042.

Appendix CFJ, Consent Final Judgment (DEP vs. TEC).

Appendix CP-1 Compliance Plan.

Appendix 40 CFR 60, Subpart A, General Provisions.

Appendix 40 CFR 60, Subpart Da, Standards of Performance for Fossil-Fuel Fired Steam Generators.

Appendix 40 CFR 60, Subpart KKKK, Standards of Performance for Stationary Combustion Turbines.

Appendix 40 CFR 60, Subpart IIII, Standards of Performance for Stationary Compression Ignition Internal Combustion Engines.

Appendix 40 CFR 60, Subpart OOO, Standards of Performance for Nonmetallic Mineral Processing Plants.

Appendix 40 CFR 63, Subpart A, General Provisions.

Appendix 40 CFR 63, Subpart II, National Emission Standards for Shipbuilding and Ship Repair (Surface Coating).

Appendix 40 CFR 63, Subpart ZZZZ, National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines.

Appendix I, List of Insignificant Emissions Units and/or Activities.

Appendix O&M, Operation and Maintenance Plan under RACT for PM.

Appendix RR, Facility-wide Reporting Requirements.

Appendix TR, Facility-wide Testing Requirements.

Appendix TV, Title V General Conditions.

Appendix U, List of Unregulated Emissions Units and/or Activities.

Referenced Attachments. 	 At End

Figure 1, Summary Report-Gaseous and Opacity Excess Emission and

Monitoring System Performance (40 CFR 60, July, 1996).

Table H, Permit History.

Table 1, Summary of Air Pollutant Standards and Terms.

Table 2, Compliance Requirements.

Permittee:

Tampa Electric Company (TEC)	Permit No. 0570039-067-AV

Big Bend Power Station	Facility ID No. 0570039

13031 Wyandotte Road	SIC No. 4911

Apollo Beach, Florida  33572-9200	Project:  Title V Air Operation Permit Revision

The purpose of this permit is to revise and incorporate the specific condition revisions related to Project No. 0570039-066-AC.  This existing facility is located in Hillsborough County at Big Bend Road, Apollo Beach, Florida.  UTM Coordinates:  Zone 17, 361.9 kilometers (km) East and 3075.0 km North; Latitude: 27 47’ 36” North and Longitude: 82 24’ 11” West.

This Title V air operation permit revision is issued under the provisions of Chapter 403, Florida Statutes (F.S.), and Florida Administrative Code (F.A.C.) Chapters 62-4, 62-210, 62-213 and 62-214.  The above named permittee is hereby authorized to perform the work or operate the facility in accordance with the terms and conditions of this permit.

0570039-039-AV Renewal Effective Date:  January 1, 2010

0570039-045-AV 1st Revision Effective Date:  April 5, 2011

0570039-054-AV 2nd Revision Effective Date:  Sept. 18, 2012

0570039-061-AV 3rd Revision Effective Date:  April 10, 2013

0570039-067-AV 4th Revision Effective Date:  XXXX

Renewal Application Due Date:  May 20, 2014

Expiration Date:  December 31, 2014

Executed in Tallahassee

(DRAFT/PROPOSED)

for	Jeffery F. Koerner, Program Administrator

Permitting and Compliance Section

Division of Air Resource Management

JFK/dr/ttm

Subsection A.  Facility Description.

The Big Bend Station is a nominal 1,892 megawatt (MW) electric generation facility.  This facility consists of four fossil fuel fired steam generators, Boiler Unit Nos. 1 through 4; four steam turbines; a simple cycle combustion turbine (SCCT)-generator peaking unit set; solid fuels, fly ash, limestone, gypsum, slag, and bottom ash storage and handling facilities; and, fuel oil storage tanks.  Unit Nos. 1, 2, 3 and 4 have nominal maximum heat inputs of 4,037, 3,996, 4,115 and 4,330 million British thermal units (Btu) per hour, respectively.  Unit Nos. 1 through 4 are fired with coal and with petcokepetroleum coke in a mixture with coal up to 20.0% petcokepetroleum coke/80.0% coal (by weight), or a coal blended with coal residual generated from the Polk Power Station, or a coal/petroleum coke blend further blended with coal residual generated from the Polk Power Station.  The combustion turbine is fired with pipeline-quality natural gas and ultra low sulfur diesel (ULSD) fuel.  In addition, there is a ship surface coating operation.  Also included in this permit are miscellaneous unregulated/insignificant emissions units and/or activities.

Subsection B.  Summary of Emissions Units.

| E.U. ID No. | ## Brief Description |
| --- | --- |
| Regulated Emissions Units |  |
|  | Fossil Fuel Fired Steam Generator Units |
| -001 | Fossil Fuel Fired Steam Generator Unit No. 1 |
| -002 | Fossil Fuel Fired Steam Generator Unit No. 2 |
| -003 | Fossil Fuel Fired Steam Generator Unit No. 3 |
| -004 | Fossil Fuel Fired Steam Generator Unit No. 4 |
|  | Solid Fuel Yard |
| -010 | Solid Fuel Yard Fugitive Emissions |
| -029 | Fuel Blending Bin Cyclone Collectors (FH-032 through FH-035) |
| -030 | Fuel Mill Cyclone Collectors (FH-048 and FH-049) |
| -046 | Transloading and Off-site Transfer of Solid Fuels and Slag (by truck, rail and barge) |
| -047 | Railcar Unloading and Conveying System |
|  | Coal Bunkers with Roto-Clones |
| -015 | Unit No. 1 Coal Bunker with Roto-Clone |
| -016 | Unit No. 2 Coal Bunker with Roto-Clone |
| -017 | Unit No. 3 Coal Bunker with Roto-Clone |
| -039 | Unit No. 4 Coal Bunker with Roto-Clone |
|  | Flyash Handling and Storage - Silo Nos. 1 & 2 |
| -008 | Fly Ash Silo No. 1 Baghouse |
| -018 | Fly Ash Silo No. 1 Truck Loadout |
| -009 | Fly Ash Silo No. 2 Baghouse |
| -019 | Fly Ash Silo No. 2 Truck Loadout |
| -026 | Fly Ash Handling and Storage Fugitive Emissions (all except silos) |
|  | Flyash Handling and Storage - Silo No. 3 |
| -014 | Fly Ash Silo No. 3 Baghouse |
| -027 | Fly Ash Silo No. 3 Truck Loadout |
| -028 | Fly Ash Handling System Fugitive Emissions |
|  | Limestone Handling and Storage |
| -011 | Truck Limestone Unloading Receiving Hopper |
| -012 | Limestone Silo A with 2 Baghouses (2) |
| -013 | Limestone Silo B with 2 Baghouses (2) |
| -023 | Limestone Handling Conveyor LB/ to Conveyor LC with Baghouse |
| -02350 | Limestone Handling Conveyor LD/ to Conveyor LE with Baghouse |
| -025 | Limestone Storage and Handling Fugitive Emissions |
|  | Limestone Handling for FGD System for Units 1 & 2 |
| -020 | Drops from Limestone Conveyors LE,/LF/ and LG/ and Silo C Belt Feeder with Baghouse |
| -021 | Silo C with one Baghouse |
|  | Wastewater Treatment Plant |
| -022 | Lime Silo for Wastewater Treatment Plant with one Baghouse |
|  | Abrasive Blasting |
| -033 | Abrasive Blast Booth with Baghouse |
| -034 | Abrasive Blast Media Storage with Baghouse |
| -032 | Surface Coating of Miscellaneous Metal Parts |
|  | Surface Coating Operations |
| -035 | Surface Coating of Ships |
|  | Coal Residual Storage and Transfer from the Polk Power Station |
| -037 | Coal Residual Storage Facility |
| -038 | Coal Residual Transfer System |
|  | Simple-Cycle Combustion Turbines |
| -041 | SCCT 4A with a common electric generator that it shares with SCCT 4B |
| -042 | SCCT 4B with a common electric generator that it shares with SCCT 4A |
|  | Engines |
| -043 | SCCT Black Start Diesel Engine, 1,000 ekW |
| -044 | Coal Field Diesel Generator |
| Unregulated Emissions Units and/or Activities |  |
| -036 | Slag and Bottom Ash Sources BH-001 through BH-004 |
| -036 | Gypsum Handling and Storage Sources GH-001 through GH-017 |
| -036 | No. 2 Fuel Oil Storage Tanks > 550 gallons |
| -036 | Vehicle Refueling Operations |
| -045 | Emergency Diesel Generator and Fire Pump Diesel Engine |

Subsection C.  Applicable Requirements.

Based on the Title V air operation permit renewal application received on June 6, 2008, this facility is a major source of hazardous air pollutants (HAP).  This facility is classified as a Prevention of Significant Deterioration (PSD) major facility.  A summary of important applicable requirements is shown in the following table.

| Applicable Requirement/Regulation | ## E.U. ID No(s). |
| --- | --- |
| Federal Rule Citations |  |
| 40 CFR 60, Subpart A, New Stationary Source Performance Standards (NSPS) General Provisions | 004, 020 & 021 |
| NSPS - 40 CFR 60, Subpart Da, Standards of Performance for Electric Utility Steam Generating Units for Which Construction is Commenced After September 18, 1978 | 004 |
| 40 CFR 60, Subpart OOO, Standards of Performance for Nonmetallic Mineral Processing Plants | 020 & 021 |
| 40 CFR 60, Subpart KKKK (Standards of Performance for Stationary Combustion Turbines for which Construction is Commenced after February 18, 2005) | 041 & 042 |
| 40 CFR 63, Subpart A, National Emissions Standards for Hazardous Air Pollutants (NESHAP) General Provisions | 035 & 044 |
| Appendix 40 CFR 63, Subpart II - National Emissions Standards for Hazardous Air Pollutants from Shipbuilding and Ship Repair (Surface Coating) | 035 |
| 40 CFR 63, Subpart ZZZZ, National Emission Standards for Hazardous Air Pollutants (NESHAP) for Stationary Reciprocating Internal Combustion Engines (RICE) also referred to as the “RICE Maximum Achievable Control Technology (MACT)” | 044 & 043 |
| 40 CFR 64, Compliance Assurance Monitoring | 001, 002, 003 & 004 |
| State Rule Citations |  |
| Rule 62-210.300, F.A.C., Permits Required | 008, 018, 009, 019 & 026 037 & 038 |
| Rule 62-212.400, F.A.C., Prevention of Significant Deterioration | 004, 010, 029 & 030 |
| Rule 62-214, F.A.C., Acid Rain, Phase II SO2 | 001, 002, 003 & 004 |
| Rule 62-214, F.A.C., Acid Rain, Phase II NOX | 001, 002, 003 & 004 |
| Rule 62-296.405(1), F.A.C., Fossil Fuel Steam Generators with More than 250 million Btu per Hour Heat Input | 001, 002 & 003 |
| Rule 62-296.405(2), F.A.C., Fossil Fuel Steam Generators with More than 250 million Btu per Hour Heat Input | 004 |
| Rule 62-296.470, F.A.C., Clean Air Interstate Rule | 001, 002, 003 & 004 |
| Rule 62-296.470, F.A.C., Clean Air Interstate Rule (CAIR) Retired Units | 005 & 006 |
| Rule 62-296.500, F.A.C., Reasonably Available Control Technology (RACT) - Volatile Organic Compounds (VOC) and Nitrogen Oxides (NOX) Emitting Facilities | 032 & 035 |
| Rule 62-296.513, F.A.C., RACT VOC - Surface Coating of Miscellaneous Metal Parts and Products | 032 |
| Rule 62-296.700(2)(c), F.A.C., RACT PM - Exemption | 015, 016, 017, 022 & 039 |
| Rule 62-296.700(6), F.A.C., RACT PM - O&M Plan | 001, 002, 003 & 004 |
| Rule 62-296.711, F.A.C., Reasonably Available Control Technology (RACT) Particulate Matter (PM) - Materials Handling, Sizing, Screening, Crushing and Grinding Operations | 020, 021, 029 & 030 |
| Rule 62-296.712, F.A.C., RACT PM - Miscellaneous Manufacturing Process Operations | 033 & 034 |
| Other Requirements |  |
| Consent Final Judgment (DEP vs. TEC) dated December 16, 1999. | 001, 002, 003 & 004 |

The following conditions apply facility-wide to all emission units and activities:

- Appendices.  The permittee shall comply with all documents identified in Section VI., Appendices, listed in the Table of Contents.  Each document is an enforceable part of this permit unless otherwise indicated.  [Rule 62-213.440, F.A.C.]

Emissions and Controls

- Not federally enforceable.  Objectionable Odor Prohibited.  No person shall cause, suffer, allow or permit the discharge of air pollutants, which cause or contribute to an objectionable odor.  An “objectionable odor” means any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance.  [Rule 62-296.320(2) and 62-210.200(Definitions), F.A.C.]

- General Volatile Organic Compounds (VOC) Emissions or Organic Solvents (OS) Emissions.  The permittee shall allow no person to store, pump, handle, process, load, unload or use in any process or installation, volatile organic compounds or organic solvents without applying known and existing vapor emission control devices or systems deemed necessary and ordered by the Department.  Nothing was deemed necessary and ordered at this time.  [Rule 62-296.320(1), F.A.C.]

- General Visible Emissions.  No person shall cause, let, permit, suffer or allow to be discharged into the atmosphere the emissions of air pollutants from any activity equal to or greater than 20% opacity.  EPA Method 9 is the method of compliance pursuant to Chapter 62-297, F.A.C.Emissions from the following types of activities in Hillsborough County are further subject to a general 5% opacity standard:  loading or unloading of materials to or from containers such as rail cars, trucks, ships, storage structures and stockpiles; permanent conveyor systems; storage of materials in structures such as silos or enclosed bins, which have a storage capacity of 50 cubic yards or more; crushing, grinding, sizing and screening operations; and, static drop transfer points.  ThisThese regulations does not impose a specific testing requirement.  [Rule 62-296.320(4)(b)1., F.A.C.; and Rule 1-3.52, EPCHC]

- Unconfined Particulate Matter.  No person shall cause, let, permit, suffer or allow the emissions of unconfined particulate matter from any activity, including vehicular movement; transportation of materials; construction; alteration; demolition or wrecking; or industrially related activities such as loading, unloading, storing or handling; without taking reasonable precautions to prevent such emissions.

- Reasonable precautions to prevent emissions of unconfined particulate matter at this facility include:

  - Chemical or water application to: unpaved roads and unpaved yard areas;

  - Paving and maintenance of roads, parking areas and yards;

  - Landscaping or planting of vegetation;

  - Confining abrasive blasting where possible; and

  - Other techniques, as necessary.

  - Trucks used to transport solid fuels shall utilize tarps at all times except when loading/unloading.

- The following reasonable precaution shall be taken to control unconfined PM emissions associated with the fly ash silo/truck operations.  Reasonable precautions shall include, but not limited to:

- Fly ash transported by dump truck shall be adequately wetted and processed through the pugmill;

- Dump trucks used to transport fly ash shall utilize tarps at all times except when loading/unloading;

- Fly ash transported in a dry state shall be accomplished utilizing an enclosed tanker truck;

- Fly ash spilled and/or leaked on plant grounds shall be adequately wetted and disposed of daily;

- Fly ash collected from spills and/or leaks must be adequately wetted at all times;

- Ensure the proper seating of the unloader chute onto the tanker inlet prior to loading;

- Keep the dust extractor operational during loading;

- Close the tanker's inlet as soon as practical after the loading process;

- Extend the tubing from the silo into the closed tanker type trucks during loadout; and,

- Periodic watering of plant roads.

- The following reasonable precautions shall be taken to control unconfined PM emissions associated with abrasive blasting operations.  Reasonable precautions shall include, but not limited to:

- Maintain curtains on open ends of abrasive blasting building and keep curtains fully closed when performing abrasive blasting activities.

- Maintain screens or filters on louvered vents, as necessary, to prevent fugitive emissions from the building ventilation openings.

- Water yard areas surrounding abrasive blasting building, as necessary.

[Rule 62-296.320(4)(c), F.A.C.; and, proposed by applicant in Title V air operation permit renewal application received on September 13, 2013.]

Annual Reports and Fees

See Appendix RR, Facility-wide Reporting Requirements, for additional details.

- Annual Operating Report.  The permittee shall submit an annual report that summarizes the actual operating rates and emissions from this facility.  Annual operating reports shall be submitted to the Compliance Authority by April 1st of each year.  [Rule 62-210.370(3), F.A.C.]

- Annual Emissions Fee Form and Fee.  The annual Title V emissions fees are due (postmarked) by March 1st of each year.  The completed form and calculated fee shall be submitted to:  Major Air Pollution Source Annual Emissions Fee, P.O. Box 3070, Tallahassee, Florida  32315-3070.  The forms are available for download by accessing the Title V Annual Emissions Fee On-line Information Center at the following Internet web site:  http://www.dep.state.fl.us/air/emission/tvfee.htm.  [Rule 62-213.205, F.A.C.]

- Annual Statement of Compliance.  The permittee shall submit an annual statement of compliance to the compliance authority at the address shown on the cover of this permit within 60 days after the end of each calendar year during which the Title V air operation permit was effective.  [Rules 62-213.440(3)(a)2. & 3. and (b), F.A.C.]

- Prevention of Accidental Releases (Section 112(r) of CAA).  If and when the facility becomes subject to 112(r), the permittee shall:

a.	Submit its Risk Management Plan (RMP) to the Chemical Emergency Preparedness and Prevention Office (CEPPO) RMP Reporting Center.  Any Risk Management Plans, original submittals, revisions or updates to submittals, should be sent to:  RMP Reporting Center, Post Office Box 10162, Fairfax, VA  22038, Telephone:  703/227-7650.

b.	Submit to the permitting authority Title V certification forms or a compliance schedule in accordance with Rule 62-213.440(2), F.A.C.

[40 CFR 68]

- Settlement Agreement.  The permittee shall comply with the Consent Final Judgment (DEP vs. TEC) dated December 6, 1999.  [Rules 62-4.070(1), (3) & (5) and 62-213.440, F.A.C.]

The specific conditions in this section apply to the following emissions units:

| E.U. ID No. | ## Brief Description |
| --- | --- |
| -001 | Fossil Fuel Fired Steam Generator Unit No. 1 |
| -002 | Fossil Fuel Fired Steam Generator Unit No. 2 |
| -003 | Fossil Fuel Fired Steam Generator Unit No. 3 |

The fuel fired in fossil fuel fired steam generator Unit Nos. 1, 2 and 3 consists of coal, or a coal/petroleum coke (petcoke) blend containing a maximum of 20% petroleum coke by weight, or coal blended with coal residual generated from the Polk Power Station, or a coal/petroleum coke blend further blended with coal residual generated from the Polk Power Station.

Unit No. 1 is a fossil fuel fired steam boiler electrical generating unit with a design capacity rating of 4,037 MMBtu/hour and a design electrical generating capacity of 445 megawatts (MW).  It is a wet bottom utility boiler manufactured by Riley Stoker Corporation.  Nitrogen oxides (NOX) emissions are controlled by low NOX burners (LNB) and selective catalytic reduction (SCR) system which was installed in 2010.  Particulate matter (PM) emissions are controlled by a dry electrostatic precipitator (ESP) manufactured by Western Precipitator Division, Joy Manufacturing Corporation.  The PM control efficiency is 99.7%.  Unit No. 1 began commercial operation in 1970.

Unit No. 2 is a fossil fuel fired steam boiler electrical generating unit with a design capacity rating of 3,996 MMBtu/hour and a design electrical generating capacity of 445 MW.  It is a wet bottom utility boiler manufactured by Riley Stoker Corporation.  Nitrogen oxides (NOX) emissions are controlled by low NOX burners (LNB) and selective catalytic reduction (SCR) system which was installed in 2009.  Particulate matter (PM) emissions are controlled by a dry electrostatic precipitator (ESP) manufactured by Western Precipitator Division, Joy Manufacturing Corporation.  The PM control efficiency is 99.7%.  Unit No. 2 began commercial operation in 1973.

Unit No. 1 and Unit No. 2 share a common stack (identified as CS-0W1).  Immediately prior to the common stack, sulfur dioxide (SO2) emissions from Unit Nos. 1 and 2 are controlled by wet flue gas desulfurization (FGD) equipment installed in 1999 and manufactured by Wheelabrator.  The emissions from Unit Nos. 1 and 2 have no ability to bypass any of the installed control devices prior to exiting through the common stack.  The CS-0W1 common stack parameters are:  height, 490 feet; diameter, 29.0 feet; exit temperature, 132 degrees F; and, actual stack gas flow rate of 2,306,709 acfm.

Unit No. 3 is a fossil fuel fired steam boiler electrical generating unit with a design capacity rating of 4,115 MMBtu/hour and a design electrical generating capacity of 445 MW.  It is a wet bottom utility boiler manufactured by Riley Stoker Corporation.  Sulfur dioxide (SO2) emissions from Unit No. 3 are controlled by wet flue gas desulfurization (FGD) equipment installed in 1995 and manufactured by Research Cottrell.  NOX emissions are controlled by LNB and its own SCR system.  The SCR system on Unit No. 3 was installed in 2008.  Particulate matter emissions generated during the operation of the unit are controlled by a dry electrostatic precipitator (ESP) manufactured by Research-Cottrell, Inc.  The ESP control efficiency is 99.7%.  Unit No. 3 began commercial operation in 1976.  The Unit No. 3 stack (stack identification BB-003) parameters are:  height, 490 feet: diameter, 24.0 feet; exit temperature, 127 degrees F; and, actual stack gas flow rate, 1,389,740 acfm.

{Permitting note(s):  Fossil Fuel Fired Steam Generator Unit Nos. 1, 2 and 3 are regulated under the federal Acid Rain Program for Phase II SO2 and NOX; Rule 62-296.405(1), F.A.C., Fossil Fuel Steam Generators with More than 250 million Btu per Hour Heat Input; Rule 62-296.700(6), F.A.C., Reasonable Available Control Technology (RACT) PM – Operation and Maintenance O&M Plan; Compliance Assurance Monitoring (CAM), adopted and incorporated by reference in Rule 62-204.800, F.A.C.; and, Rule 62-296.470, F.A.C., Clean Air Interstate Rule (CAIR).  These emissions units are also regulated under a Consent Final Judgment (DEP vs. TEC) dated December 16, 1999.  These units were formerly regulated under the federal Acid Rain Program as Phase I SO2 substitution units.}

Essential Potential to Emit (PTE) Parameters

- Hours of Operation.  These emissions units may operate continuously (8,760 hours/year).  [Rule 62-210.200 (Definitions - (PTE), F.A.C.]

- Design Capacity.  The design heat input rates are as follows:

| Unit No. | MMBtu/hr Heat Input |
| --- | --- |
| 1 | 4,037 |
| 2 | 3,996 |
| 3 | 4,115 |

These design heat input rates are based on the original design of each unit for firing coal with a certain lower heating value (LHV) that was used to design each boiler.  At any given time, the actual heat input rate is a function of the actual demand load, the coal mass firing rate, and the fuel properties of the coal being fired at that time.  Although the above design capacities are not intended as operational restrictions, the permittee shall obtain the appropriate air construction permits before making any physical or operational changes that would increase the actual heat input rate capabilities of a unit.  [Rules 62-4.160(2), 62-210.200 (Definitions – Modification, Potential to Emit (PTE)), 62.210.300, 62-213.440 & 62-296.405(1), F.A.C.; and, Permit Nos. 0570039-014-AC (Unit Nos. 1 – 4 LNB installations) & 0570039-022-AC, Condition A.16 (Unit No. 3 SCR installation).]

{Permitting Note:  For purposes of the Acid Rain program, the actual heat input rate of each of these units is reported based on the measured exhaust gas flow rate.  According to the applicant, the Acid Rain CEMS at this site have historically predicted higher heat input rates than methods based on the mass flow and fuel properties of coal.}

- Emissions Unit Operating Rate Limitation During Testing.  Testing of emissions shall be conducted with the emissions unit operating at or above 90% of the design capacity specified in this permit.  The values above represent design values which, in some cases, may be exceeded as the unit is operated at full load for stack testing.  The heat input values are to be measured during stack testing to within +/- 10% of its true value using the methods/procedures contained in Specific Condition A.49.  If it is impracticable to test at this rate, an emissions unit may be tested at less than 90% of the design capacity; in this case, subsequent emissions unit operation is limited to 110% of the test rate until a new test is conducted.  Once the unit is so limited, operation at higher capacities is allowed for no more than 15 consecutive days for the purpose of additional compliance testing to regain the authority to operate at the design capacity.  See the related testing provisions in Appendix TR, Facility-wide Testing Requirements.  [Rules 62-297.310(2) & 62-213.440, F.A.C.]

- Methods of Operation.

  - Fuels - Normal Operation.  The only fuels allowed to be burned in Unit Nos. 1, 2 and 3 shall consist of coal, or a coal/petroleum coke blend, or coal blended with raw coal residual, or a coal/petroleum coke blend further blended with raw coal residual.  In any case, the petroleum coke content of any fuel blend shall not exceed 20% by weight.

  - Fuels - Startup, Shutdown, Flame Stabilization.  In addition to the fuels allowed to be burned during normal operation, each unit may also burn new No. 2 fuel oil during startup, shutdown, flame stabilization, and during the start of an additional solid fuel mill on an already operating unit.

  - Other Operation.

(1)	Boiler Chemical Cleaning Waste.  Evaporation of up to 150,000 gallons per year, total at the facility, is allowed of non-hazardous, but potentially hazardous air pollutant (HAP)-emitting, mineral acid solution boiler chemical cleaning waste which was generated on site.

- (2)  Raw Coal Residual.  The total amount of raw coal residual fired at Big Bend Station (all Unit Nos. 1 - 4 combined) shall be limited to 200 tons per day.  The raw coal residual is a by-product of the gasification of coal at the Polk Power Station.  The permittee shall only fire raw coal residual in the event of a gasification process malfunction at the Polk Power Station that results in raw coal residual that has some remaining fuel value.  The permittee shall document all gasification process malfunctions and record the amount of raw coal residual, if any, fired at Big Bend Station.  These records should be kept on site at Big Bend and made readily available to the Department and the Environmental Protection Commission of Hillsborough County upon request.

- (3)  Supplemental Material Injection.  The following materials may be injected as needed for boiler conditioning and energy recovery purposes:

(a)	Magnesium Oxide, Limestone and Fluxing Agents may be injected as needed for boiler conditioning.  Supplemental injection of liquid magnesium oxide as needed to reduce upper furnace pluggage.

(b)	Fluxing.  Supplemental injection of iron ore to assist in lowering the ash fusion temperature.

(b)	Fly Ash.  Reinjection of on-site generated flyash for energy recoveryUnit 4 flyash for energy recovery.

(d)	Limestone.  Mixed with the fuel in-feed as needed to optimize coal blend.

d.	Daily Log.  The permittee shall maintain a daily log of the amounts and types of fuels used and copies of fuel analyses containing information on sulfur content, ash content and heating values.

e.	Control Devices.  All air pollution control devices shall be in operation according to manufacturer’s recommendations whenever the boilers are in operation.  Note:  under current permitted ductwork configuration, none of the air pollution control devices can be physically bypassed.  In the event of a control device malfunction resulting in excess emissions beyond the allowable periods established for these units, the associated boiler shall be removed from service until such time that the control device resumes normal operation.

[Rule 62-213.410, F.A.C.; and Permit Nos. 0570039-05366-ACCondition 3.]

{Permitting note:  “Flame stabilization” is defined as the use of new No. 2 fuel oil to stabilize a flame during times of unexpected poor coal quality or equipment failure such as coal piping pluggage.  Flame stabilization due to poor coal quality occurs when coal is wet or does not provide the necessary heat to maintain a stable flame.  In this situation, new No. 2 fuel oil is combusted to provide the additional required heat input to maintain a stable flame.  Flame stabilization due to equipment failure occurs when coal piping is plugged, or equipment is otherwise damaged, that results in an inconsistent amount of coal reaching the burners.  Under certain conditions, this may result in the burners intermittently seeing large amounts of fuel at one time, causing a potentially explosive flame “puff”.  In this situation, new No. 2 fuel oil must be used for stabilization to prevent flame “puffing” and ensure safe operation.  Combustion of No. 2 fuel oil is also necessary during periods of load change to initialize and stabilize the flame until coal flow to the burners reaches steady state.  As defined in 62-210.700(3), F.A.C., load change occurs when the operational capacity of a unit is in the 10 to 100 percent capacity range, other than startup or shutdown, which exceeds 10 percent of the unit's rated capacity and which occurs at a rate of 0.5percent per minute or more.}

Air Pollution Control Technologies and Measures

- FGD Operation Required for Petcoke and Coal Residual.  Whenever Unit Nos. 1 or 2 is fired with petcoke in any amount up to the allowable percentage, or any amount of coal residual, its flue gases shall be directed to the FGD system for Unit Nos. 1 and 2.  [Permit Nos. 0570039-003-AC, 0570039-004-AC and 0570039-012-AC.]

- Limit on Petcoke Bunkering.  The owner or operator at any given time shall not bunker more than the amount of petcoke that may be fired in each emissions Unit No. 1 or No. 2 in one day.  [0570039-003-AC and 0570039-004-AC]

{Permitting Note:  This condition is intended to limit possible excess emissions in the event of an unexpected breakdown of the FGD system that requires its shutdown while either emissions unit is firing petcokepetroleum coke.}

- Low NOX Burners (LNB).  Unit Nos. 1, 2 and 3 shall be operated using the low NOX burners and in accordance with the operational procedures that have been developed to minimize NOX emissions.  [Permit No. 0570039-014-AC.]

- Selective Catalytic Reduction (SCR) System.  The permittee shall operate and maintain the selective catalytic reduction (SCR) systems for nitrogen oxides (NOX) control on Unit Nos. 1, 2, and 3.  [Permit Nos. 0570039-022-AC (amended by 0570039-035-AC) and 0570039-024-AC.]

{Permitting Note:  Selective catalytic reduction (SCR) systems commenced operation under the following schedule:

Unit No. 3 – July 1, 2008, as authorized by Permit No. 0570039-022-AC;

Unit No. 2 - April 30, 2009, as authorized by Permit No. 0570039-024-AC; and,

Unit No. 1 –April 19, 2010, as authorized by Permit No. 0570039-024-AC.}

- SCR System Operation.  The permittee shall operate and maintain each SCR system in accordance with the SCR system supplier’s recommendations or in accordance with methods established by the owner/operator through site-specific testing, including operating the SCR between minimum and maximum operating temperatures, which have been demonstrated by the applicant to assure compliance with the applicable emissions limits.  The owner or operator shall not operate the SCR system equipment nor circumvent the air pollution control equipment in such a manner which would violate allowable emission rates.  [Rule 62-210.650, F.A.C.; and, Permit Nos. 0570039-022-AC, (amended by 0570039-035-AC), 0570039-024-AC & 0570039-053-AC, Condition 5.]

- Circumvention.  The owner or operator shall not circumvent or operate the air pollution control equipment in such a manner which would violate allowable emission rates established for these units.  [Rule 62-210.650, F.A.C.; and, Permit Nos. 0570039-022-AC, (amended by 0570039-035-AC), 0570039-024-AC & 0570039-05366-AC, Condition 5.]

- SCR System.  Each partial SCR system maintenance bypass duct shall be normally closed except during maintenance periods.  [Rule 62-4.070(1) & (3), F.A.C.; and, Permit Nos. 0570039-022-AC (amended by 0570039-035-AC) and 0570039-024-AC.]

Emission Limitations and Standards

Unless otherwise specified, the averaging times for Specific Conditions A.10. - A.25. are based on the specified averaging time of the applicable test method.

Visible Emissions (VE)

- VE.  Visible emissions from each unit shall not exceed 20 percent opacity, except for one six-minute period per hour during which opacity shall not exceed 27 percent.  Emissions units governed by this visible emissions limit shall compliance test for particulate matter emissions annually and as otherwise required by Chapter 62-297, F.A.C.  [Rule 62-296.405(1)(a), F.A.C.]

- VE - Soot Blowing and Load Change.  Visible emissions from each unit shall not exceed 60 percent opacity during the 3-hours in any 24-hour period of excess emissions allowed for boiler cleaning (soot blowing) and load change.  A load change occurs when the operational capacity of a unit is in the 10 percent to 100 percent capacity range, other than startup or shutdown, which exceeds 10 percent of the unit’s rated capacity and which occurs at a rate of 0.5 percent per minute or more.  Visible emissions above 60 percent opacity shall be allowed for not more than 4, six (6)-minute periods, during the 3-hour period of excess emissions allowed for boiler cleaning and load changes, at units which have installed continuous opacity monitors (COMS).  [Rule 62-210.700(3), F.A.C.]

Particulate Matter (PM) Emissions

- PM Emissions.  Particulate matter emissions from each unit shall not exceed 0.03 pounds per million Btu heat input.  [Permit No. 0570039-060-AC.]

{Permitting Note:  This PM limit originating from the Consent Final Judgment and/or the Consent Decree as amended; supersedes the SIP PM limit of 0.1 pounds per million Btu heat input from Rule 62-296.405(1)(b), F.A.C.}

- PM Emissions.  The maximum particulate matter emission rate for each unit is as follows:

| Unit No. | lbs./hour | tons/yr |
| --- | --- | --- |
| 1 | 121.1 | 530 |
| 2 | 119.9 | 525 |
| 3 | 123.5 | 541 |

In the event that the design heat input rate for a unit is reduced, the maximum permitted particulate matter emission rate for that unit shall also be reduced accordingly.  [Rule 62-296.700(4)(b)1. (PM RACT - lbs./hour & tons/year), F.A.C.; and, Permit No. 0570039-060-AC.]

- PM Emissions - Unit Nos. 1 - 4.  In order to provide reasonable assurance that a significant net emission rate increase will not occur as a result of combusting raw and beneficiated coal residual at Big Bend, the combined emissions from Fossil Fuel Fired Steam Generator Unit Nos. 1 - 4 shall not exceed an annual emissions cap of 2,767 tons/year of PM/PM10.  This cap corresponds to the average emissions of the years 1999 and 2000.  Any relaxation in this limit that increases the facility’s potential to emit by at least 1 ton of pollutant per year will result in a reevaluation of PSD applicability for the facility as though construction had not yet commenced at the facility.  [Rule 62-212.400 (escape Prevention of Significant Deterioration (PSD)), F.A.C.; and, Permit No. 0570039-012-AC.]

- PM - Soot Blowing and Load Change.  Particulate matter emissions from each unit shall not exceed an average of 0.3 pound per million Btu heat input during the 3-hours in any 24-hour period of excess emissions allowed for boiler cleaning (soot blowing) and load change.  [Rule 62-210.700(3), F.A.C.]

Sulfur Dioxide (SO2) Emissions

- SO2 - Liquid Fuel.  When burning liquid fuel, sulfur dioxide emissions from each unit shall not exceed 2.75 tons per heat input, as measured by applicable compliance methods.  [Rule 62-296.405(1)(c)1.j., F.A.C.]

- SO2 - Sulfur Content.  The No. 2 fuel oil sulfur content from each unit shall not exceed 0.5 percent, by weight.  [Rule 62-296.405(1)(e)3., F.A.C.; and, Applicant Request.]

- SO2 - Solid Fuel.

- SIP Limits.  Unit Nos. 1, 2 and 3, each shall not emit more than 6.5 pounds of sulfur dioxide per million Btu heat input on a two-hour average; nor shall Unit Nos. 1, 2 and 3, in total, emit more than 31.5 tons per hour of sulfur dioxide on a three-hour average and 25 tons per hour of sulfur dioxide on a 24-hour block average (midnight to midnight).  [Rules 62-296.405(1)(c)2.b. and 3., F.A.C.; and, Rule 62-204.240(1), F.A.C.]

(1)	Unit Nos. 1 and 2, in total, shall not emit more than 16.5 tons per hour of sulfur dioxide on a 24-hour block average.  [Rules 62-296.405(1)(c)2.b. and 3., F.A.C.; and, Rule 62-204.240(1), F.A.C.]

(2)	Unit No. 3 shall not emit more than 8.5 tons per hour of sulfur dioxide on a 24-hour block average.

[Rules 62.204.800(1)(b)20., and 62-296.405(1)(c)2.b. and 3., F.A.C.; and, Rule 62.62-204.240(1), F.A.C.]

- SO2 Emissions - Unit Nos. 1 - 4.  In order to provide reasonable assurance that a significant net emission rate increase will not occur as a result of combusting raw and beneficiated coal residual at Big Bend, the combined emissions from Fossil Fuel Fired Steam Generator Unit Nos. 1 - 4 shall not exceed an annual emissions cap of 71,810 tons per year of SO2.  This cap corresponds to the average emissions of the years 1999 and 2000.  Any relaxation in this limit that increases the facility’s potential to emit by at least 1 ton of pollutant per year will result in a reevaluation of PSD applicability for the facility as though construction had not yet commenced at the facility.  [Rule 62-212.400 (escape Prevention of Significant Deterioration (PSD), F.A.C.; and, Permit No. 0570039-012-AC.]

- SO2 Emissions - Unit Nos. 1 - 2.  When combusting solid fuels, Unit Nos. 1 and 2, each shall meet at least one of the following limits:

  - the scrubber shall remove at least 95% of the SO2 in the flue gas that entered the scrubber; or,

  - on and after January 1, 2013, the “emission rate” for SO2 does not exceed 0.25 pound per million Btu heat input on a 30-day rolling average.  The term “emission rate” is specifically defined in Specific Condition A.25.

[Applicant Request; and, Permit No. 0570039-060-AC.]

- SO2 Emissions - Unit No. 3.  When combusting solid fuels, Unit No. 3 shall meet at least one of the following limits:

  - the scrubber shall remove at least 95% of the SO2 in the flue gas that entered the scrubber; or,

  - the “emission rate” for SO2 does not exceed 0.25 pound per million Btu heat input on a 30-day rolling average.  The term “emission rate” is specifically defined in Specific Condition A.25.

[Applicant Request; and, Permit No. 0570039-060-AC.]

Nitrogen Oxides (NOX) Emissions

- Nitrogen Oxides (NOx) Emissions - Unit Nos. 1 and 2.  NOx emissions from Unit No. 1 when combusting solid fuel, shall not exceed 0.12 lb NOx/million Btu heat input on a heat input weighted 30-day  rolling average basis {calculated equivalent NOx emissions from Unit No. 1 are 484.4 lb/hr and 2,121.9 TPY}.  NOx  emissions from Unit No. 2 when combusting solid fuel, shall not exceed 0.12 lb NOx/million Btu heat input on a heat input weighted 30-day rolling average basis {calculated equivalent NOx emissions from Unit No. 2 are 479.5 lb/hr and 2,100.3 TPY}.  [Consent Decree (U.S. vs. TEC) dated February 29, 2000, amendment dated June 12, 2009; and, Permit No. 0570039-024-AC (revised by Permit No. 0570039-060-AC).]

- Nitrogen Oxides (NOx) Emissions - Unit 3.  NOx emissions from Unit No. 3 when combusting solid fuel, shall not exceed 0.12 lb NOx/million Btu heat input on a heat input weighted 30-day rolling average basis {calculated equivalent NOx emissions from Unit No. 3 are 494 lb/hr and 2,163.7 TPY}.  [Consent Decree (U.S. vs. TEC) dated February 29, 2000, amendment dated June 12, 2009; and, Permit No. 0570039-022-AC (amended by 0570039-035-AC and revised by Permit No. 0570039-060-AC).]

{Permitting Note:  The Consent Decree as amended; supersedes the SIP NOX limit of 0.70 pounds per million Btu heat input from Rules 62-296.405(1)(d)4. and 62-296.405(1)(e)4., F.A.C.}

- Ammonia Slip.  Ammonia slip, measured at the stack downstream of all emissions control systems, shall not exceed 10 parts per million by volume (ppmv).  Annual testing of ammonia slip shall be conducted, and corrective measures taken if measured values exceed 5 ppmv.  [Rule 62-4.070(1) & (3), F.A.C.; and, Permit Nos. 0570039-022-AC (amended by 0570039-035-AC) and 0570039-024-AC.]

Nitrogen Oxides (NOx) and Sulfur Dioxide (SO2) Emissions

- Calculation of Emission Rate.  A "30-day rolling average emission rate” for NOX and SO2 shall be herein defined as the emission rate expressed as lb/MMBtu and calculated in accordance  with the following procedure:  first, sum the total pounds of the pollutant in question emitted from the Unit during an operating day and the previous twenty-nine (29) operating days; second, sum the total heat input to the Unit in MMBtu during the operating day and the previous twenty-nine (29) operating days; and third, divide the total number of pounds of the pollutant emitted during the thirty (30) operating days by the total heat input during the thirty (30) operating days.  A new 30-day rolling average emission rate shall be calculated for each new operating day. The 30-day rolling average emission rate:

- Shall include all emissions and heat input in MMBtu commencing from the time the Unit is synchronized with a utility electric distribution system through the time that the unit ceases to be synchronized with such utility electric distribution  system;

- May exclude emissions of NOx and heat input in MMBtu occurring during the fifth and subsequent “Cold Start Up” period(s) that occur in any 30-day period if inclusion of such emissions would result in a violation of any applicable 30-day rolling average emission rate. A "Cold Start Up Period" occurs whenever there has been no fire in the boiler of a Unit (no combustion of any fossil fuel) for a period of six hours of more.  The emissions to be excluded  during the fifth and subsequent Cold Start Up Period(s) shall be the lesser of: (1) those NOx emissions emitted during the eight hour period commencing when the Unit is synchronized with a utility electric distribution  system and concluding eight hours later, or (2) those emitted prior to the time that the flue gas has achieved the SCR operational temperature as specified by the catalyst manufacturer; and (3)(4) may exclude NOx emissions and heat input in MMBtu occurring during any period of malfunction  (as defined at 40 CFR 60.2) of the SCR; and

- Shall use the methodologies and procedures set forth in 40 C.F.R. Part 75, Appendix F.

[Consent Final Judgment (DEP vs. TEC) dated December 16, 1999; Consent Decree (U.S. vs. TEC) dated February 29, 2000, amendment dated June 12, 2009; and, Permit No. 0570039-060-AC.]

Excess Emissions

Rule 62-210.700 (Excess Emissions), F.A.C., cannot vary any requirement of a NSPS, NESHAP or Acid Rain provision.

- Excess Emissions Allowed - Malfunctions.  Excess emissions resulting from malfunction shall be permitted providing (1) best operational practices to minimize emissions are adhered to and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C.]

- Excess Emissions Allowed - Startup And Shutdown.  Excess emissions resulting from startup or shutdown shall be permitted provided that best operational practices to minimize emissions are adhered to and the duration of excess emissions shall be minimized.  [Rule 62-210.700(2), F.A.C.]

- Best Operational Practices to Minimize Excess Emissions.  The permittee shall follow the best operational practices to minimize excess emissions during startup and shutdown as described in Appendix BOP, Best Operational Practices for Start up and Shutdown.  [Rules 62-210.700(2) and 62-213.440(1) (Operational Requirements that Assure Compliance), F.A.C.; and, Proposed by the Applicant in the Renewal Application.]

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C.]

Monitoring of Operations

- Monitoring of PetcokePetroleum Coke Usage.  The permittee shall operate and maintain equipment to record and calculate the weight percentage of petcokepetroleum coke and coal bunkered and fired in each emissions unit, to verify compliance with the bunkering limit and the percentage limitation on petcokepetroleum coke usage of this permit.  [Rule 62-4.070(1) & (3), F.A.C.Permit No. 0570039-066-AC]

Monitoring Requirements

{Permitting Note:  In accordance with the Acid Rain Phase II requirements, the following continuous monitors are installed on these units:  opacity, SO2, NOX, CO2 and stack gas flow.}

- Continuous Monitoring Systems.  These emissions units shall operate and maintain continuous monitoring systems for monitoring opacity, SO2, NOX and CO2.  [Rule 62-296.405(1)(f)1., F.A.C.]

- Operation and Maintenance Plan.  An Operation and Maintenance Plan required under RACT for PM is attached and a part of this permit pursuant to Rule 62-296.700(6), F.A.C.  All activities shall be performed as scheduled and recorded data made available to the Department upon request.  Records shall be maintained on file for a minimum of five (5) years.  Appendix O&M, Operation and Maintenance Plan under RACT for PM, is attached as part of this permit.  [Rule 62-296.700(6), F.A.C.]

- CAM Plan.  These emissions units are subject to the Compliance Assurance Monitoring (CAM) requirements contained in the attached Appendix CAM for the controlled emissions of particulate matter.  Failure to adhere to the monitoring requirements specified does not necessarily indicate an exceedance of a specific emissions limitation; however, it may constitute good reason to require compliance testing pursuant to Rule 62-297.310(7)(b), F.A.C.  [40 CFR 64; Rules 62-204.800 and 62-213.440(1)(b)1.a., F.A.C.]

Continuous Emissions Monitoring Systems (CEMS)

- CEMS.  The continuous emissions monitoring systems shall meet the quality assurance requirements and performance specifications contained in 40 CFR 75.  [Rule 62-296.405(1)(e)4., F.A.C.]

- SO2 Compliance by CEMS.  The permittee shall demonstrate compliance with the sulfur dioxide limits by means of continuous emissions monitoring systems.  In addition to any other requirements associated with the operation and maintenance of these CEMS (i.e., Acid Rain requirements), operation of the CEMS shall be in accordance with the requirements listed in this permit.  The annual calibration RATA associated with these CEMS may be used in lieu of the required annual EPA Reference Method 6, as long as all of the requirements of Rule 62-297.310, F.A.C., are met, i.e., prior test notification, proper test result submittal, etc.  [Rule 62-296.405(1)(f)1.b., F.A.C.; and, Applicant Request.]

- NOx Compliance by CEMS.  Nitrogen oxides (NOx) emissions from Unit Nos. 1, 2 and 3 shall be continuously monitored to confirm compliance, using the Unit’s existing continuous emissions monitoring system (CEMS).  Compliance is determined by calculating the heat input weighted average of all hourly emission rates for NOX for the 30 successive boiler operating days, except for data obtained during startup, shutdown, malfunction, or abnormal events.  "Abnormal events" are defined as an unanticipated interruption, malfunction, or failure of the pipeline or associated equipment utilized to supply ammonia to the Big Bend Station for use in the operation of the selective catalytic reduction control system.  Excess emissions occurring from operation of the boilers during an abnormal event are authorized provided that best operational practices are employed to minimize the amount and duration of the emissions during an abnormal event.  Emissions data collected during “abnormal events” may be excluded from the 30-day rolling compliance averages in accordance with this condition.  For the purpose of calculating a 30-day rolling average, a boiler operating day is defined as a 24-hour period (between 12:01 a.m. and 12:00 midnight) during which fossil fuel is combusted in a steam operating unit for the entire 24-hours.  [Rules 62-297.310(7)(a)2. and 4., and 62-4.070(1) & (3), F.A.C.); 40 CFR 60.46a(g); and, Permit Nos. 0570039-022-AC and 0570039-024-AC.]

- NOx Compliance Schedule - Unit No. 1 and 2.  Compliance with the heat input weighted 30-day rolling average NOX emission limit of 0.12 lb NOX/MMBtu shall be demonstrated using CEMS data beginning May 31, 2010 (or 30 boiler operating days after May 1, 2010), for Unit No. 1, and beginning May 31, 2009 (or 30 boiler operating days after May 1, 2009), for Unit No. 2, and every 30 boiler operating days thereafter.  [Permit No. 0570039-022-AC (amended by 0570039-035-AC).]

- NOx Compliance - Unit No. 3.  For Unit No. 3, compliance with the heat input weighted 30-day rolling average NOX emission limit of 0.12 lb NOx/MMBtu shall be demonstrated using CEMS data every 30 boiler operating days.  [Permit No. 0570039-022-AC (amended by 0570039-035-AC).]

- SO2 and NOx CEMS and COMS.  For Unit Nos. 1, 2 and 3, the permittee shall operate, calibrate, and maintain a continuous monitoring system for continuously monitoring opacity.  For Unit Nos. 1 - 3, the permittee shall also operate calibrate, and maintain a continuous monitoring system for continuously monitoring nitrogen oxides (expressed as NO2).  In addition, the permittee shall operate calibrate, and maintain a continuous monitoring system for continuously monitoring sulfur dioxide for Unit Nos. 1, 2, and 3 in a manner sufficient to demonstrate compliance with the emission limits of this permit.  Performance specifications, location of monitor, data requirements, data reduction and reporting requirements shall conform with the requirements of 40 CFR Part 51, Appendix P, adopted and incorporated by reference in Rule 62-204.800(2), F.A.C., and 40 CFR Part 60, Appendix B, adopted by reference in Rule 62-204.800(7), F.A.C. [Rule 62-296.405(1)(f), F.A.C.]

- O2/CO2 Continuous Monitoring System.  An oxygen or carbon dioxide continuous monitoring system shall be operated for Unit Nos. 1 - 3.  Measurements of oxygen or carbon dioxide in the flue gas shall be utilized to convert nitrogen oxides and sulfur dioxide continuous emission monitoring data to units of pounds per million BTU heat input for proof of compliance.  [Rule 62-296.405(1)(f)1.d., F.A.C.]

- Continuous Monitor Performance Specifications.  If continuous monitoring systems are required by rule or are elected by the permittee to be used for demonstrating compliance with the standards of the Department, they must be installed, maintained and calibrated, either:

a.	in accordance with the EPA performance specifications listed below.  These performance specifications are contained in 40 CFR 60, Appendix B, and are adopted by reference in Rule 62-204.800, F.A.C.

(1)	Performance Specification 1--Specifications and Test Procedures for Opacity Continuous Emission Monitoring Systems in Stationary Sources.

(2) 	Performance Specification 2--Specifications and Test Procedures for SO2 Continuous Emission Monitoring Systems in Stationary Sources.

(3)	Performance Specification 3--Specifications and Test Procedures for CO2 Continuous Emission Monitoring Systems in Stationary Sources.  Or,

b.	in accordance with the applicable requirements of 40 CFR 75, Subparts B and C.  Excess emissions pursuant to Rule 62-210.700, F.A.C., shall be determined using the 40 CFR part 75 CEMS.

[Rule 62-297.520, F.A.C.; 40 CFR 75; and, Applicant Request.]

Test Methods and Procedures

- Test Methods.  Required tests shall be performed in accordance with the following reference method(s):

| Method(s) | Description of Method(s) and Comment(s) |
| --- | --- |
| EPA Methods 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| EPA Methods 5, 5B, 5F or 17 | Methods for Determining Particulate Matter Emissions |
| EPA Methods 6, 6A, 6B or 6C | Methods for Determining Sulfur Dioxide Emissions |
| Method 7, 7A, 7C, 7D or 7E | Determination of Nitrogen Oxide Emissions |
| DEP Method 9 | Visual Determination of the Opacity of Emissions |
| EPA conditional test method (CTM-027), EPA Method 320 | Methods for Determining Ammonia (NH3) Emissions |

The above methods are described in Chapter 62-297, F.A.C. and/or 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Chapter 62-297, F.A.C.]

- Annual Compliance Test.  During each federal fiscal year (October 1st to September 30th), Emissions Unit ID Nos. -001, -002 and -003 shall be tested to demonstrate compliance with the emission limitations and standards for VE, VE-SB (VE while soot blowing), PM, particulate matter while soot blowing (PM-SB), NOX and SO2.  The NOX and SO2 certified CEMS and annual RATA test data shall satisfy the requirements of the annual compliance requirements.  The annual compliance tests will be used in lieu of the compliance test prior to renewal.The NOX and SO2 RATA test data may be used to demonstrate compliance with the annual test requirement, provided the testing requirements (notification, procedures and reporting) of Chapter 62-297, F.A.C. are met.  [Rule 62-297.310(7), F.A.C.]

- Compliance Test Prior To Renewal.  Prior to permit renewal, Emissions Unit ID Nos. -001, -002 and -003 shall be tested to demonstrate compliance with the emission limitations and standards for VE, VE-SB, PM and PM-SB.  [Rule 62-297.310(7)(a)3., F.A.C.]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- Visible Emissions.  The test method for visible emissions shall be DEP Method 9, incorporated in Chapter 62-297, F.A.C.  A transmissometer may be used and calibrated according to Rule 62-297.520, F.A.C.  [Rule 62-296.405(1)(e)1., F.A.C.]

- DEP Method 9.  The provisions of EPA Method 9 (40 CFR 60, Appendix A) are adopted by reference with the following exceptions:

a.	EPA Method 9, Section 2.4, Recording Observations.  Opacity observations shall be made and recorded by a certified observer at sequential fifteen second intervals during the required period of observation.

b.	EPA Method 9, Section 2.5, Data Reduction.  For a set of observations to be acceptable, the observer shall have made and recorded, or verified the recording of, at least 90 percent of the possible individual observations during the required observation period.  For single-valued opacity standards (e.g., 20 percent opacity), the test result shall be the highest valid six-minute average for the set of observations taken.  For multiple-valued opacity standards (e.g., 20 percent opacity, except that an opacity of 40 percent is permissible for not more than two minutes per hour) opacity shall be computed as follows:

(1)	For the basic part of the standard (i.e., 20 percent opacity) the opacity shall be determined as specified above for a single-valued opacity standard.

(2)	For the short-term average part of the standard, opacity shall be the highest valid short-term average (i.e., two-minute, three-minute average) for the set of observations taken.

In order to be valid, any required average (i.e., a six-minute or two-minute average) shall be based on all of the valid observations in the sequential subset of observations selected, and the selected subset shall contain at least 90 percent of the observations possible for the required averaging time.  Each required average shall be calculated by summing the opacity value of each of the valid observations in the appropriate subset, dividing this sum by the number of valid observations in the subset, and rounding the result to the nearest whole number.  The number of missing observations in the subset shall be indicated in parenthesis after the subset average value.  [Rule 62-297.405, F.A.C.]

- Particulate Matter.  The test methods for particulate emissions shall be EPA Methods 17, 5, 5B, or 5F, incorporated by reference in Chapter 62-297, F.A.C.  The minimum sample volume shall be 30 dry standard cubic feet.  EPA Method 5 may be used with filter temperature no more than 320 degrees Fahrenheit.  For EPA Method 17, stack temperature shall be less than 375 degrees Fahrenheit.  The owner or operator may use EPA Method 5 to demonstrate compliance.  EPA Method 3 or 3A with Orsat analysis shall be used when the oxygen based F-factor, computed according to EPA Method 19, is used in lieu of heat input.  Acetone wash shall be used with EPA Method 5 or 17.  [Rules 62-296.405(1)(e)2. and 62-297.405, F.A.C.]

- Sulfur Dioxide.  The test methods for sulfur dioxide emissions shall be EPA Methods 6, 6A, 6B, or 6C, incorporated by reference in Chapter 62-297, F.A.C.  Fuel sampling and analysis may be used as an alternate sampling procedure if such a procedure is incorporated into the operation permit for the emissions unit.  If the emissions unit obtains an alternate procedure under the provisions of Rule 62-297.620, F.A.C., the procedure shall become a condition of the emissions unit’s permit.  The Department will retain the authority to require EPA Method 6 or 6C if it has reason to believe that exceedences of the sulfur dioxide emissions limiting standard are occurring.  Results of an approved fuel sampling and analysis program shall have the same effect as EPA Method 6 test results for purposes of demonstrating compliance or noncompliance with sulfur dioxide standards.  [Rules 62-213.440, 62-296.405(1)(e)3. and 62-297.405, F.A.C.]

- When burning Liquid Fuel - Compliance with Sulfur Limit.  The permittee may use the EPA test methods, referenced above, to demonstrate compliance; however, as an alternate sampling procedure authorized by permit, the permittee elected to demonstrate compliance by accepting a liquid fuel sulfur limit that will be verified with a fuel analysis provided by the vendor or the permittee upon each fuel delivery.  [Rules 62-213.440, 62-296.405(1)(e)3. and 62-297.405, F.A.C.]

- Sulfur Content Sampling Methods.  The fuel sulfur content, percent by weight, for liquid fuels shall be evaluated using either ASTM D2622-92, ASTM D4294-90, or both ASTM D4057-88 and ASTM D129-91, or the respective successor ASTM method(s).  [Rules 62-213.440, 62-296.405(1)(e)3., 62-296.405(1)(f)1.b. and 62-297.440, F.A.C.]

- Ammonia (NH3) Slip Compliance.  Compliance with the ammonia (NH3) slip limit shall be determined using EPA conditional test method (CTM-027), EPA Method 320, or other methods approved by the Department.  [Rule 62-4.070(1) & (3), F.A.C.; and, Permit Nos. 0570039-022-AC (amended by 0570039-035-AC) and 0570039-024-AC.]

- Determination of Heat Input.  The heat input shall be calculated as the product of the gross heat rate (Btu/kWh) and gross power output (MW).   The gross power output shall be measured on a 4-hour rolling averagean arithmetic average during the compliance demonstration test.  The gross unit heat rate will use a 3-month rolling "seasonal" average based on calculated monthly heat rates.  These rates shall be determined by the tons of coal bunkered, composite coal analyses and gross power output for the month.  The composite fuel samples shall be collected by on-site personnel in accordance with ASTM industry standards practices.  [Rule 62-213.440, F.A.C.]

Special Testing Requirements

- PM and VE Compliance Testing.  Unit Nos. 1, 2 and 3 shall each be individually stack tested for particulate matter and visible emissions, under both sootblowing and non-sootblowing operation conditions.  Unit Nos. 1 and 2 shall each be stack tested for particulate matter and visible emissions in the common stack (CS0W1), either while both units are in operation or while individual units are in operation.  Particulate matter emissions determined in the common stack shall demonstrate compliance with the emissions standards (lb/MMBtu) for each unit.  The mass emission rates (lb/hr) determined in the common stack shall be prorated based on the heat input rate contribution from a given unit to demonstrate compliance for that unit.  Exceedences of the visible emissions standards from the common stack shall be attributed to both units unless COMS data can clearly indicate which unit is operating in excess of the standards.  [Rules 62-297.310(7)(a)2. & 4, F.A.C.; and, Permit No 0570039-053-AC, Condition 6.]

- PM and VE Compliance Testing.  Compliance testing for particulate matter emissions and visible emissions may be conducted either:  (a) without fly ash re-injections occurring, or (b) while fly ash collected by the electrostatic precipitator is being re-injected into the boiler at a rate which is representative of the maximum anticipated fly ash re-injection rate.  If the most recent particulate and visible emission compliance tests were conducted without fly ash re-injection occurring, and fly ash re-injection occurs for any reason other than a malfunction, then the results from new particulate and visible emissions compliance tests, conducted while fly ash collected by the precipitator is being re-injected into the boiler at a rate which is representative of the maximum anticipated fly ash re-injection rate, shall be submitted to the EPCHC within 60 days of the date that such fly ash re-injection occurred.  The EPCHC may, for good cause shown, grant an extension of the 60-day time limit on a case-by-case basis.(a) with fly ash re-injections or (b) without fly ash re-injection.  If the maximum fly ash re-injection rate or percent of feed is exceeded, the unit shall be retested at the new maximum fly ash re-injection rate or percent feed.  The results of the retest shall be submitted to the Department within 90 days of the exceedance.  If a higher fly ash re-injection rate or percent of feed is required, the permittee shall notify the Department and retest to establish the revised maximum re-injection rate or percent of feed.  The test results shall be submitted to the Department.  [Rules 62-297.310(7)(a)2. & 4., and 62-4.070(1) & (3), F.A.C.]

Recordkeeping and Reporting Requirements

- Reporting Schedule.  The following report shall be submitted to the Compliance Authority:

| Report | Reporting Deadline(s) | Related Condition(s) |
| --- | --- | --- |
| Quarterly Excess Emissions Rule 62-296.405(1)(g), F.A.C. | Every 3 months (quarterly) | A.574,A.585 |
| Quarterly SO2 Emissions | Every 3 months (quarterly) | A.596. |
| Quarterly NOX Emissions | Every 3 months (quarterly) | A.6057. |

[Rule 62-296.405(1)(g), F.A.C.]

- Reporting of Excess Emissions Due to Malfunctions.  In the case of excess emissions resulting from malfunctions, each owner or operator shall notify the Department or the appropriate Local Program in accordance with Rule 62-4.130, F.A.C.  A full written report on the malfunctions shall be submitted in a quarterly report, if requested by the Department or the appropriate Local Program.  [Rule 62-210.700(6), F.A.C.]

- Quarterly Excess Emissions Report.  Submit to the Department a written report of emissions in excess of emission limiting standards as set forth in Rule 62-296.405(1), F.A.C., for each calendar quarter.  The nature and cause of the excess emissions shall be explained.  This report does not relieve the owner or operator of the legal liability for violations.  All recorded data shall be maintained on file by the source for a period of five years.  [Rules 62-213.440 and 62-296.405(1)(g), F.A.C.]

- Quarterly SO2 Report.  The permittee shall submit a quarterly SO2 report to the Department and the EPCHC within 30 days following each calendar quarter.  The quarterly SO2 report shall consist of:

a.	2-hour average SO2 emissions for each Unit Nos. 1, 2 and 3 in lb/MMBtu;

b.	3-hour average SO2 emissions for Unit Nos. 1 - 3 combined in ton per hour;

c.	24-hour average SO2 emissions for Unit Nos. 1 - 3 combined in tons per hour; and,

d.	24-hour average SO2 emissions for Unit Nos. 1 - 2 combined and Unit 3 in tons per hour;

e.	daily SO2 removal efficiency for Unit Nos. 1 - 3;

f.	30-day rolling average SO2 emissions for each Unit Nos. 1 - 3 in lb/MMBtu; and,

g.	a statement of CEMS and/or boiler malfunction, start-up, shutdown or abnormal events.

[Rules 62-213.440(1) (Monitoring) and 62-4.070(1) & (3), F.A.C.]

- Quarterly NOX Report.  The permittee shall submit a quarterly NOX report to the Department and the EPCHC within 30 days following each calendar quarter.  This report shall contain the heat input weighted 30-day NOX rolling average, all time periods of boiler operation as well as a statement of CEMS and/or boiler malfunction, start-up, shutdown or abnormal events.  [Rules 62-296.405(1)(g) and 62-4.070(1) & (3), F.A.C.]

- Records of Operation.  The owner or operator shall make and maintain a daily record of operation of each emissions unit showing the date, fuel(s) used, whether flue gas was directed to the FGD system, and the duration of all startups, shutdowns and malfunctions.  Records of fuel bunkering and petcokepetroleum coke usage (weight percent of petcokepetroleum coke fired) shall also be made on at least a daily basis.  Data that verifies compliance with the percentage limitation on petcokepetroleum coke usage shall be submitted with the annual operating report.  [Rules 62-213.440(1) (Monitoring) and 62-4.070(1) & (3), F.A.C.]

- Records.  For Unit Nos. 1 - 3, gravimetric instrument data verifying that the 20.0% maximum petroleum coke content by weight has not been exceeded shall be maintained for two years and submitted to the Department and the EPCHC with each annual operating report (AOR).  Also to be maintained and available for inspection shall be a record of operation showing the date, fuel used, and the duration of all startups, shutdowns, malfunctions and abnormal events.  [Rules 62-213.440(1) (Monitoring) and 62-4.070(1) & (3), F.A.C.]

- Continuous Emission Monitoring Network and Alarms.  To demonstrate compliance with emission limits that are protective of ambient air quality standards (AAQS), data inputs will consist of hourly CEMS data from the SO2, flow and CO2 monitors for Unit Nos. 1 - 3 at Big Bend Station.  The permittee shall use CEMS data from common stack CS0W1 to represent unit compliance with the emission limitations for each Unit 1 and Unit 2.  In the event any monitor fails, the permittee will comply with 40 CFR 75, Subpart D - Missing Data Substitution Procedures.  [Rules 62-213.440(1) (Monitoring) and 62-4.070(1) & (3), F.A.C.; and, Applicant Request.]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440, F.A.C.]

Other Requirements

- Compliance Plan - Unfinished Work and/or Activities for Unit Nos. 1 - 3.  The actions applicable to Unit Nos. 1 - 3 specified in Appendix CP-1 have not yet been completed under the Consent Decree.  [Rule 62-213.440(2), F.A.C.; Permit No. 0570039-024-AC; and, Consent Decree (U.S. vs. TEC) dated February 29, 2000, including the amendments dated October 23, 2000 and June 12, 2009.]

The specific conditions in this section apply to the following emissions units:

| E.U. ID No. | ## Brief Description |
| --- | --- |
| -004 | Fossil Fuel Fired Steam Generator Unit No. 4 |

Fossil Fuel Fired Steam Generator Unit No. 4 is a 4330 MMBTU/hour, dry-bottom tangentially fired utility boiler manufactured by Combustion Engineering.  The generator nameplate capacity is 486 MW.  Particulate matter emissions generated during the operation of the unit are controlled by a dry electrostatic precipitator (ESP) manufactured by Belco.  The control efficiency of the ESP is 99.7%.  Sulfur dioxide emissions from Unit No. 4 are controlled by wet flue gas desulfurization (FGD) equipment installed in 1995 and manufactured by Research-Cottrell.  NOX emissions from Unit No. 4 are controlled by low NOX burners (LNB), a separate overfire air system (SOFA) and its own selective catalytic reduction (SCR) system.  The SCR system on Unit No. 4 was installed in 2007.  The fuel fired in Unit No. 4 consists of coal, or a coal/petroleum coke blend containing a maximum of 20% petroleum coke by weight, or coal blended with coal residual generated from the Polk Power Station, or a coal/petroleum coke blend further blended with coal residual generated from the Polk Power Station.  Unit No. 4 began commercial operation in 1985.  The Unit No. 4 stack (stack identification BB-004) parameters are:  height, 490 feet: diameter, 24.0 feet; exit temperature, 127 degrees F; and, actual stack gas flow rate, 1,614,250 acfm.

{Permitting note(s):  Fossil Fuel Fired Steam Generator Unit No. 4 is regulated under the federal Acid Rain Program for Phase II SO2 and NOX;  Rule 62-296.405(2), F.A.C., Fossil Fuel Steam Generators with More than 250 million Btu per Hour Heat Input; NSPS - 40 CFR 60, Subpart Da, Standards of Performance for Electric Utility Steam Generating Units for Which Construction is Commenced After September 18, 1978, adopted and incorporated by reference in Rule 62-204.800(8)(b)2., F.A.C.; Rule 212.400(5), F.A.C., Prevention of Significant Deterioration [PSD-FL-040]; Power Plant Siting Certification [PA 79-12]; Rule 62-296.700(6), F.A.C., RACT PM - O&M Plan; Compliance Assurance Monitoring (CAM), adopted and incorporated by reference in Rule 62-204.800, F.A.C.; and, Rule 62-296.470, F.A.C., Clean Air Interstate Rule (CAIR).  This emissions unit is also regulated under a Consent Final Judgment (DEP vs. TEC) dated December 16, 1999.}

Essential Potential to Emit (PTE) Parameters

- Hours of Operation.  This emissions unit may operate continuously (8,760 hours/year).  [Rule 62-210.200 (Definitions - Potential to Emit (PTE), F.A.C.]

- Design Capacity.  The design heat input rate is as follows:

| Unit No. | MMBtu/hr Heat Input |
| --- | --- |
| 4 | 4,330 |

This design heat input rate is based on the original design of the unit for firing coal with a certain lower heating value (LHV) that was used to design the boiler.  At any given time, the actual heat input rate is a function of the actual demand load, the coal mass firing rate, and the fuel properties of the coal being fired at that time.  Although the above design capacity is not intended as an operational restriction, the permittee shall obtain the appropriate air construction permits before making any physical or operational changes that would increase the actual heat input rate capability of the unit.  [Rules 62-4.160(2), 62-210.200 (Definitions – Modification, Potential to Emit (PTE)); and, 62-296.405(1), 62.210.300 & 62-213.440, F.A.C.; and, Permit Nos. 0570039-014-AC (Unit Nos. 1 - 4) & 0570039-053-AC)

{Permitting Note:  For purposes of the Acid Rain program, the actual heat input rate of each of the unit is reported based on the measured exhaust gas flow rate.  According to the applicant the Acid Rain CEMS at this site have historically predicted higher heat input rates than methods based on the mass flow and fuel properties of coal.}

- Emissions Unit Operating Rate Limitation During Testing.  Testing of emissions shall be conducted with the emissions unit operating at or above 90% of the design capacity specified in this permit.  The values above represent design values which, in some cases, may be exceeded as the unit is operated at full load for stack testing.  The heat input values are to be measured during stack testing to within +/- 10% of its true value using the methods/procedures contained in Specific Condition B.53.  If it is impracticable to test at this rate, an emissions unit may be tested at less than 90% of the design capacity; in this case, subsequent emissions unit operation is limited to 110% of the test rate until a new test is conducted.  Once the unit is so limited, operation at higher capacities is allowed for no more than 15 consecutive days for the purpose of additional compliance testing to regain the authority to operate at the design capacity.  See the related testing provisions in Appendix TR, Facility-wide Testing Requirements.  [Rules 62-297.310(2) & 62-213.440, F.A.C.]

- Methods of Operation.

a.  	Fuels - Normal Operation.  The only fuels allowed to be burned in Unit Nos. 1, 2 and 34 shall consist of coal, or a coal/petroleum coke blend, or coal blended with raw coal residual, or a coal/petroleum coke blend further blended with raw coal residual.  In any case, the petroleum coke content of any fuel blend shall not exceed 20% by weight.

b.  	Fuels - Startup, Shutdown, Flame Stabilization.  In addition to the fuels allowed to be burned during normal operation, each unit may also burn new No. 2 fuel oil during startup, shutdown, flame stabilization, and during the start of an additional solid fuel mill on an already operating unit.

c.  	Other Operation.

(1)	Boiler Chemical Cleaning Waste.  Evaporation of up to 150,000 gallons per year, total at the facility, is allowed of non-hazardous, but potentially hazardous air pollutant (HAP)-emitting, mineral acid solution boiler chemical cleaning waste which was generated on site.

- (2)  Raw Coal Residual.  The total amount of raw coal residual fired at Big Bend Station (all Unit Nos. 1 - 4 combined) shall be limited to 200 tons per day.  The raw coal residual is a by-product of the gasification of coal at the Polk Power Station.  The permittee shall only fire raw coal residual in the event of a gasification process malfunction at the Polk Power Station that results in raw coal residual that has some remaining fuel value.  The permittee shall document all gasification process malfunctions and record the amount of raw coal residual, if any, fired at Big Bend Station.  These records should be kept on site at Big Bend and made readily available to the Department and the Environmental Protection Commission of Hillsborough County upon request.

- (3)  Supplemental Material Injection.  The following materials may be injected as needed for boiler conditioning and energy recovery purposes:

(a)	Magnesium Oxide, Limestone and Fluxing Agents may be injected as needed for boiler conditioning.  Supplemental injection of liquid magnesium oxide as needed to reduce upper furnace pluggage.

(b)	Fluxing.  Supplemental injection of iron ore to assist in lowering the ash fusion temperature.

(b)	(c)  Fly Ash.  Reinjection of on-site generated flyash for energy recoveryUnit 4 flyash for energy recovery.

(d)	Limestone.  Mixed with the fuel in-feed as needed to optimize coal blend.

d.	Daily Log.  The permittee shall maintain a daily log of the amounts and types of fuels used and copies of fuel analyses containing information on sulfur content, ash content and heating values.

e.	Control Devices.  All air pollution control devices shall be in operation according to manufacturer’s recommendations whenever the boilers are in operation.  Note:  under current permitted ductwork configuration, none of the air pollution control devices can be physically bypassed.  In the event of a control device malfunction resulting in excess emissions beyond the allowable periods established for these units, Unit 4 shall be removed from service until such time that the control device resumes normal operation.

[Permit No. 0570039-06653-AC, Condition 4.]

{Permitting note:  “Flame stabilization” is defined as the use of No. 2 fuel oil to stabilize a flame during times of unexpected poor coal quality or equipment failure such as coal piping pluggage.  Flame stabilization due to poor coal quality occurs when coal is wet or does not provide the necessary heat to maintain a stable flame.  In this situation, No. 2 fuel oil is combusted to provide the additional required heat input to maintain a stable flame.  Flame stabilization due to equipment failure occurs when coal piping is plugged, or equipment is otherwise damaged, that results in an inconsistent amount of coal reaching the burners.  Under certain conditions, this may result in the burners intermittently seeing large amounts of fuel at one time, causing a potentially explosive flame “puff”.  In this situation, No. 2 fuel oil must be used for stabilization to prevent flame “puffing” and ensure safe operation. Combustion of No. 2 fuel oil is also necessary during periods of load change to initialize and stabilize the flame until coal flow to the burners reaches steady state.  As defined in 62-210.700(3), F.A.C., load change occurs when the operational capacity of a unit is in the 10 to 100 percent capacity range, other than startup or shutdown, which exceeds 10 percent of the unit's rated capacity and which occurs at a rate of 0.5 percent per minute or more.}

Air Pollution Control Technologies and Measures

- Operating Procedures.  Operating procedures shall include good operating practices and proper training of all operators and supervisors.  The good operating practices shall meet the guidelines and procedures as established by the equipment manufacturers.  All operators (including supervisors) of air pollution control devices shall be properly trained in plant specific equipment.  [Permit No. 0570039-020-AC (amended by 0570039-026, -031 & -036-AC).]

- Circumvention.  The owner or operator shall not circumvent or operate the air pollution control equipment nor operate the SCR system equipment in such a manner which would violate allowable emission rates established for this unit.  [Rule 62-210.650, F.A.C.; and, Permit Nos. 0570039-020-AC (amended by 0570039-026, -031 & -036-AC) & 0570039-06653-AC, Condition 5.]

- Future Actual Emissions Reporting.  The permittee shall maintain and submit to the Department on an annual basis for a period of 5 years from the date the duct work separation initiative is placed in operation, information demonstrating in accordance with Rule 62-212.300(1)(e), F.A.C., using the emissions computation and reporting procedures in Rule 62-210.370, F.A.C., that the implementation of the initiative did not result in an emissions increase of SO2 that would equal or exceed the respective significant emission rate as defined in Rule 62-210.200, F.A.C.  [Permit No. 0570039-020-AC (amended by 0570039-026, -031 & -036-AC); and, Rule 62-212.300(1)(e), F.A.C.]

- Low NOX Burners (LNB).  Unit No. 4 shall be operated using the low NOX burners and in accordance with the operational procedures that have been developed to minimize NOX emissions.  [Permit No. 0570039-014-AC.]

- Separate Overfire Air System (SOFA).  Unit 4 shall be operated using the separate over fire air system (SOFA) and in accordance with the operational procedures that have been developed to minimize NOX emissions.  [Permit No. 0570039-014-AC.]

- LNB and SOFA Systems.  The permittee shall adhere to good combustion practices to achieve the BACT CO emissions limits.  [PSD-FL-390/Permit No. 0570039-027-AC (amended by PSD-FL-390A/Permit No. 0570039-042-AC).]

- Selective Catalytic Reduction (SCR) System.  The permittee shall operate and maintain the selective catalytic reduction (SCR) systems for nitrogen oxides (NOX) control on Unit No. 4.  [Permit No. 0570039-020-AC (amended by 0570039-026, -031 & -036-AC).]

{Permitting Note:  A selective catalytic reduction (SCR) system commenced operationhas been installed under the following schedule:

  - Unit No. 4 – May 26, 2007, as authorized by Permit No. 0570039-020-AC (amended by 0570039-026, -031 & -036-AC).}

- SCR System Operation.  The permittee shall operate and maintain the SCR system in accordance with the SCR system supplier’s recommendations or in accordance with methods established by the owner/operator through site-specific testing, including operating the SCR system between minimum and maximum operating temperatures, which have been demonstrated by the applicant to assure compliance with the applicable emissions limits.  [Permit Nos. 0570039-020-AC (amended by 0570039-026, -031 & -036-AC) & 0570039-053-AC, Condition 5.]

- SCR System.  The partial SCR system maintenance bypass duct shall be normally closed except during maintenance periods.  [Permit No. 0570039-020-AC (amended by 0570039-026, -031 & -036-AC).]

Emission Limitations and Standards

Unless otherwise specified, the averaging times for Specific Conditions B.14. - B.24. are based on the specified averaging time of the applicable test method.

Visible Emissions (VE)

- VE.  Visible emissions from Unit No. 4 shall not exceed 20 percent opacity (6-minute average), except for one 6-minute period per hour of not more than 27 percent opacity.  [Rules 62-204.800(8)(b)2., and 62-296.405(2)(a), F.A.C.; 40 CFR 60.42Da(b); and PSD-FL-040; and, Rule 62-296.405(2)(a), F.A.C.]

Particulate Matter (PM) Emissions

- PM Emissions.  Particulate matter emissions shall not exceed 0.01 pounds per million Btu heat input when burning solid or liquid fuel.  This standard applies at all times except during periods of startup, shutdown, or malfunction.  [Permit No. 0570039-060-AC.]

{Permitting Note:  This PM limit originating from the Consent Final Judgment and/or the Consent Decree as amended; supersedes the NSPS 40 CFR 60 Subpart Da PM limit of 0.03 pounds per million Btu heat input.}

- PM Emissions.  The maximum particulate matter emission rate for this unit is as follows:

| Unit No. | lbs./hour | tons/yr |
| --- | --- | --- |
| 4 | 43.3 | 189.7 |

In the event that the design heat input rate for this unit is reduced, the maximum permitted particulate matter emission rate for this unit shall also be reduced accordingly.  [Rule 62-296.700(4)(b)1. (PM RACT - lbs./hour & tons/yr), F.A.C.; and, Permit No. 0570039-060-AC.]

- PM Emissions - Unit Nos. 1 - 4.  In order to provide reasonable assurance that a significant net emission rate increase will not occur as a result of combusting raw and beneficiated coal residual at Big Bend, the combined emissions from Fossil Fuel Fired Steam Generator Unit Nos. 1 - 4 shall not exceed an annual emissions cap of 2,767 tons/year of PM/PM10.  This cap corresponds to the average emissions of the years 1999 and 2000.  Any relaxation in this limit that increases the facility’s potential to emit by at least 1 ton of pollutant per year will result in a reevaluation of PSD applicability for the facility as though construction had not yet commenced at the facility.  [Rule 62-212.400 (escape Prevention of Significant Deterioration (PSD)), F.A.C.; and, Permit No. 0570039-012-AC.]

Sulfur Dioxide (SO2) Emissions

- SO2 Emissions.  Sulfur dioxide emissions from Unit No. 4 when combusting solid fuel shall not exceed 0.82 lb/million Btu heat input and 10 percent of the potential combustion concentration (90 percent reduction).  Based upon a heat input of 4,330 million Btu/hour, SO2 emissions shall not exceed 3,551 lb/hr and 15,553.4 tons/yr.  [Rule 62-204.800(8)(b)2., F.A.C.; 40 CFR 60.43Da(a)(1); PSD-FL-040; and, Rules 62-296.405(2)(c) and 62-213.440(1), F.A.C.;]

- SO2 Emissions.  Compliance with the sulfur dioxide emission limitations and percent reduction requirements is determined on a 30-day rolling average basis.  [Rule 62.204.800(8)(b)2., F.A.C.; 40 CFR 60.43Da(g).]

- SO2 Emissions - Unit Nos. 1 - 4.  In order to provide reasonable assurance that a significant net emission rate increase will not occur as a result of combusting raw and beneficiated coal residual at Big Bend, the combined emissions from Fossil Fuel Fired Steam Generator Unit Nos. 1 - 4 shall not exceed an annual emissions cap of 71,810 tons per year of SO2.  This cap corresponds to the average emissions of the years 1999 and 2000.  Any relaxation in this limit that increases the facility’s potential to emit by at least 1 ton of pollutant per year will result in a reevaluation of PSD applicability for the facility as though construction had not yet commenced at the facility.  [Rule 62-212.400, F.A.C.; and, Permit No. 0570039-012-AC.]

Nitrogen Oxides (NOX) Emissions

- Nitrogen Oxides (NOX) Emissions - Unit 4.  Unit No. 4 when combusting solid fuel, shall not emit more than 0.10 of a pound of nitrogen oxides per million Btu heat input based upon a 30-day rolling average basis {calculated equivalent NOX emissions are 433 lb/hr and 1,896.5 TPY}.  [Consent Final Judgment (DEP vs. TEC) dated December 16, 1999; Consent Decree (U.S. vs. TEC) dated February 29, 2000, amendment dated June 12, 2009; E-mail memorandum from EPA received on September 15, 2005; Rule 62-204.800(8)(b)2., F.A.C.; 40 CFR 60.44Da(a); 40 CFR 60.44Da(c); Permit No. 0570039-020-AC (amended by 0570039-026, -031 & -036-AC and revised by Permit No. 0570039-0660-AC); and, PSD-FL-040.]

{Permitting Note:  The NOX limits from the Consent Final Judgment and/or the Consent Decree as amended; are sufficient to also comply with the PSD and NSPS 40 CFR 60 Subpart Da NOX limit of 0.60 pounds per million Btu heat input from 40 CFR 60.44a(a).}

- Ammonia Slip.  Ammonia slip, measured at the stack downstream of all emissions control systems, shall not exceed 10 parts per million by volume (ppmv).  Annual testing of ammonia slip shall be conducted and corrective measures taken if measured values exceed 5 ppmv.  [Permit No. 0570039-020-AC (amended by 0570039-026, -031 & -036-AC).]

Nitrogen Oxides (NOx) and Sulfur Dioxide (SO2) Emissions

- Calculation of Emission Rate.  A "30-day rolling average emission rate” for NOX and SO2 shall be herein defined as the emission rate expressed as lb/MMBtu and calculated in accordance  with the following procedure:  first, sum the total pounds of the pollutant in question emitted from the Unit during an operating day and the previous twenty-nine (29) operating days; second, sum the total heat input to the Unit in MMBtu during the operating day and the previous twenty-nine (29) operating days; and third, divide the total number of pounds of the pollutant emitted during the thirty (30) operating days by the total heat input during the thirty (30) operating days.  A new 30-day rolling average emission rate shall be calculated for each new operating day. The 30-day rolling average emission rate:

- Shall include all emissions and heat input in MMBtu commencing from the time the Unit is synchronized with a utility electric distribution system through the time that the unit ceases to be synchronized with such utility electric distribution  system;

- May exclude emissions of NOX and heat input in MMBtu occurring during the fifth and subsequent “Cold Start Up” period(s) that occur in any 30-day period if inclusion of such emissions would result in a violation of any applicable 30-day rolling average emission rate. A "Cold Start Up Period" occurs whenever there has been no fire in the boiler of a Unit (no combustion of any fossil fuel) for a period of six hours of more.  The emissions to be excluded  during the fifth and subsequent Cold Start Up Period(s) shall be the lesser of: (1) those NOX emissions emitted during the eight hour period commencing when the Unit is synchronized with a utility electric distribution  system and concluding eight hours later, or (2) those emitted prior to the time that the flue gas has achieved the SCR operational temperature as specified by the catalyst manufacturer; and (4) may exclude NOX emissions and heat input in MMBtu occurring during any period of malfunction  (as defined at 40 C.F.R. 60.2) of the SCR; and

- Shall use the methodologies and procedures set forth in 40 CFR Part 75, Appendix F.

[Consent Final Judgment (DEP vs. TEC) dated December 16, 1999; Consent Decree (U.S. vs. TEC) dated February 29, 2000, amendment dated June 12, 2009; and, Permit No. 0570039-060-AC.]

Carbon Monoxide (CO) Emissions

- Carbon Monoxide (CO) Emissions - Unit No. 4.  CO emissions from Unit 4 shall not exceed 0.20 pounds per million Btu heat input (lb/MMBtu) on a heat input weighted 30-boiler operating day rolling average as demonstrated by the required CO CEMS {calculated equivalent CO emissions are 866 lb/hr and 3,793.1 TPY}.  [PSD-FL-390/Permit No. 0570039-027 (amended by PSD-FL-390A/Permit No. 0570039-042-AC); and, CO Optimization Study dated December 18, 2008.]

Excess Emissions

Rule 62-210.700 (Excess Emissions), F.A.C., cannot vary any requirement of a NSPS, NESHAP or Acid Rain provision.

- Excess Emissions Allowed - Startup, Shutdown or Malfunction.  Excess emissions resulting from startup, shutdown or malfunction shall be permitted providing (1) best operational practices to minimize emissions are adhered to and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C.]

- Best Operational Practices to Minimize Excess Emissions.  The permittee shall follow the best operational practices to minimize excess emissions during startup and shutdown as described in Appendix BOP, Best Operational Practices for Start up and Shutdown.  [Rules 62-210.700(2) and 62-213.440(1) (Operational Requirements that Assure Compliance), F.A.C.; and, Proposed by the Applicant in the Renewal Application.]

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C.]

Monitoring Requirements

{Permitting Note:  In accordance with the Acid Rain Phase II requirements, the following continuous monitors are installed on this unit:  opacity, SO2, NOX, CO2 and stack gas flow.}

- Continuous Monitoring Systems.  This emissions unit shall operate and maintain continuous monitoring systems for monitoring opacity, SO2, NOX, CO1 and CO2.  [Rules 62-4.070(1) & (3) and 62-213.440(1) (Monitoring), F.A.C.; and, 1 PSD-FL-390/Permit No. 0570039-027 (amended by PSD-FL-390A/Permit No. 0570039-042-AC).]

- Operation and Maintenance Plan.  An Operation and Maintenance Plan required under RACT for PM is attached and a part of this permit pursuant to Rule 62-296.700(6), F.A.C.  All activities shall be performed as scheduled and recorded data made available to the Department upon request.  Records shall be maintained on file for a minimum of five (5) years.  Appendix O&M, Operation and Maintenance Plan under RACT for PM, is attached as part of this permit.  [Rule 62-296.700(6), F.A.C.]

- Continuous Monitoring Systems.  The permittee shall calibrate, maintain, and operate a continuous monitoring system, and record the output of the system, for measuring the oxygen and/or carbon dioxide content of the flue gases at each location where sulfur dioxide or nitrogen oxides emissions are monitored.  The sulfur dioxide, nitrogen dioxide, oxygen and/or carbon dioxide, and opacity monitoring devices shall meet the applicable requirements of Rule 62-214, F.A.C., 40 CFR 60.47Da., and 40 CFR 75. ).  The opacity monitor shall be placed in the duct work between the electrostatic precipitator and the FGD scrubber.  The continuous monitoring system will measure sulfur dioxide emissions at the inlet of each unit and outlet of the FGD system and from the Unit 4 No. 4 stack (BB004), while emissions of nitrogen oxides, oxygen and/or carbon dioxide, and opacity shall be measured in the Unit No. 4 ducts prior to the FGD system.  The emissions of nitrogen oxides and opacity shall be measured in the Unit 4 duct prior to the FGD system. The emissions of carbon dioxide and sulfur dioxide are both measured in the inlet and outlet ducts.  [Rule 62-204.800(8)(b)2., F.A.C.; 40 CFR 60.47Da(d); and, PA 79-12D.]

- CAM Plan.  These emissions units are subject to the Compliance Assurance Monitoring (CAM) requirements contained in the attached Appendix CAM for the controlled emissions of particulate matter.  Failure to adhere to the monitoring requirements specified does not necessarily indicate an exceedance of a specific emissions limitation; however, it may constitute good reason to require compliance testing pursuant to Rule 62-297.310(7)(b), F.A.C.  [40 CFR 64; Rules 62-204.800 and 62-213.440(1)(b)1.a., F.A.C.]

- Use of CO CEMS For Continuous Compliance.  Pursuant to 40 CFR 64.2(b)(1)(vi), the applicant has elected to use the existing certified CO continuous emissions monitoring system (CEMS) for continuous compliance in order to be exempt from the Compliance Assurance Monitoring (CAM) requirements contained in 40 CFR 64.  [40 CFR 64.2(b)(vi); and, Applicant Request.]

- Emission Control Equipment Monitoring.  The permittee shall submit to the Department a standardized plan or procedure that will allow the permittee to monitor emission control equipment efficiency and enable the permittee to return malfunctioning equipment to proper operation as expeditiously as possible.  [Rules 62-4.070(1) & (3) and 62-213.440(1) (Monitoring), F.A.C.; and, PA 79-12.]

Continuous Emissions Monitoring Systems (CEMS)

- CEMS.  The continuous emissions monitoring systems shall meet the quality assurance requirements and performance specifications contained in 40 CFR 75.  [Rules 62-4.070(1) & (3) and 62-213.440(1) (Monitoring), F.A.C.]

- SO2 Compliance by CEMS.  The permittee shall demonstrate compliance with the sulfur dioxide limits by means of continuous emissions monitoring systems (CEMS).  In addition to any other requirements associated with the operation and maintenance of these CEMS (i.e., Acid Rain requirements), operation of the CEMS shall be in accordance with the requirements listed in this permit.  The annual calibration RATA associated with these CEMS may be used in lieu of the required annual EPA Reference Method 6, as long as all of the requirements of Rule 62-297.310, F.A.C., are met, i.e., prior test notification, proper test result submittal, etc.  [Rules 62-4.070(1) & (3) and 62-213.440(1) (Monitoring), F.A.C.; and, Applicant Request.]

- NOX Compliance by CEMS.  Nitrogen oxides (NOX) emissions shall be continuously monitored to confirm compliance, using the Unit’s existing continuous emissions monitoring system (CEMS).  Compliance is determined by calculating the heat input weighted average of all hourly emission rates for NOX for the 30 successive boiler operating days, except for data obtained during startup, shutdown, malfunction, or abnormal events.  "Abnormal events" are defined as an unanticipated interruption, malfunction, or failure of the pipeline or associated equipment utilized to supply ammonia to the Big Bend Station for use in the operation of the selective catalytic reduction control system.  Excess emissions occurring from operation of the boilers during an abnormal event are authorized provided that best operational practices are employed to minimize the amount and duration of the emissions during an abnormal event.  Emissions data collected during “abnormal events” may be excluded from the 30-day rolling compliance averages in accordance with this condition.  For the purpose of calculating a 30-day rolling average, a boiler operating day is defined as a 24-hour period (between 12:01 a.m. and 12:00 midnight) during which fossil fuel is combusted in a steam operating unit for the entire 24-hours.  [Rules 62-297.310(7)(a)2. and 4., and 62-4.070(1) & (3), F.A.C.); 40 CFR 60.46a(g); and, Permit Nos. 0570039-020-AC (amended byand 0570039-026, -031 & -036-AC).]

- NOX Compliance.  Compliance with the heat input weighted 30-day rolling average NOX emission limit of 0.10 lb NOX/MMBtu shall be demonstrated using CEMS data every 30 boiler operating days.  [Permit No. Permit No. 0570039-020-AC (amended by 0570039-026, -031 & -036-AC).]

- CO Compliance by CEMS.  Compliance with the 30-day rolling average CO emission limit shall be demonstrated using data collected from the required CO CEMS.  [PSD-FL-390/Permit No. 0570039-027 (amended by PSD-FL-390A/Permit No. 0570039-042-AC).]

- CO CEMS - Appendix CEMS.  Additional requirements applicable to the CO CEMS are given in the attached Appendix CEMS, which is a part of this permit.  [PSD-FL-390/Permit No. 0570039-027 (amended by PSD-FL-390A/Permit No. 0570039-042-AC).]

- SO2 and NOX CEMS and COMS.  The permittee shall operate, calibrate, and maintain a continuous monitoring system for continuously monitoring opacity.  The permittee shall also operate calibrate, and maintain a continuous monitoring system for continuously monitoring nitrogen oxides (expressed as NO2).  In addition, the permittee shall operate calibrate, and maintain a continuous monitoring system for continuously monitoring sulfur dioxide in a manner sufficient to demonstrate compliance with the emission limits of this permit.   Performance specifications, location of monitor, data requirements, data reduction and reporting requirements shall conform with the requirements of 40 CFR Part 51, Appendix P, adopted and incorporated by reference in Rule 62-204.800(2), F.A.C., and 40 CFR Part 60, Appendix B, adopted by reference in Rule 62-204.800(7), F.A.C.  [Rules 62-4.070(1) & (3) and 62-213.440(1) (Monitoring), F.A.C.]

- O2/CO2 Continuous Monitoring System.  An oxygen or carbon dioxide continuous monitoring system shall be operated.  Measurements of oxygen or carbon dioxide in the flue gas shall be utilized to convert nitrogen oxides and sulfur dioxide continuous emission monitoring data to units of pounds per million BTU heat input for proof of compliance.  [Rules 62-4.070(1) & (3) and 62-213.440(1) (Monitoring), F.A.C.]

- Continuous Monitor Performance Specifications.  If continuous monitoring systems are required by rule or are elected by the permittee to be used for demonstrating compliance with the standards of the Department, they must be installed, maintained and calibrated, either:

a.	in accordance with the EPA performance specifications listed below.  These performance specifications are contained in 40 CFR 60, Appendix B, and are adopted by reference in Rule 62-204.800, F.A.C.

(1)	Performance Specification 1--Specifications and Test Procedures for Opacity Continuous Emission Monitoring Systems in Stationary Sources.

(2)	Performance Specification 2--Specifications and Test Procedures for SO2 Continuous Emission Monitoring Systems in Stationary Sources.

(3)	Performance Specification 3--Specifications and Test Procedures for CO2 Continuous Emission Monitoring Systems in Stationary Sources.  Or,

b.	in accordance with the applicable requirements of 40 CFR 75, Subparts B and C.  Excess emissions pursuant to Rule 62-210.700, F.A.C., shall be determined using the 40 CFR part 75 CEMS.

[Rule 62-297.520, F.A.C.; and 40 CFR 75; and, Applicant Request.]

Test Methods and Procedures

- Test Methods.  Required tests shall be performed in accordance with the following reference method(s):

| Method(s) | Description of Method(s) and Comment(s) |
| --- | --- |
| EPA Methods 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| EPA Methods 5, 5B, 5F or 17 | Methods for Determining Particulate Matter Emissions |
| EPA Methods 6, 6A, 6B or 6C | Methods for Determining Sulfur Dioxide Emissions |
| Method 7, 7A, 7C, 7D or 7E | Determination of Nitrogen Oxide Emissions |
| EPA Method 10 | Determination of Carbon Monoxide Emissions |
| EPA Method 9 | Visual Determination of the Opacity of Emissions |
| EPA conditional test method (CTM-027),or EPA Method 320 | Methods for Determining Ammonia (NH3) Emissions |

The above methods are described in Chapter 62-297, F.A.C. and/or 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Chapter 62-297, F.A.C.]

- Annual Compliance Test.  During each federal fiscal year (October 1st to September 30th), Emissions Unit ID No. -004 shall be tested to demonstrate compliance with the emission limitations and standards for VE, PM, NOX and SO2.  The NOX and SO2 RATA test data may be used to demonstrate compliance with the annual test requirement, provided the testing requirements (notification, procedures and reporting) of Chapter 62-297, F.A.C. are met.  The NOX and SO2 certified CEMS and annual RATA test data shall satisfy the requirements of the annual compliance requirements.  [Rule 62-297.310(7), F.A.C.]

- Compliance Test Prior To Renewal.  Prior to permit renewal, Emissions Unit ID No. -004 shall be tested to demonstrate compliance with the emission limitations and standards for VE and PM.  [Rule 62-297.310(7)(a)3., F.A.C.]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- CO Stack Testing.  The CO stack test shall be one-time only unless a special test is required. [PSD-FL-390/Permit No. 0570039-027 (amended by PSD-FL-390A/Permit No. 0570039-042-AC).]

- Visible Emissions.  The test method for visible emissions shall be EPA Method 9, incorporated in Chapter 62-297, F.A.C.  A transmissometer may be used and calibrated according to Rule 62-297.520, F.A.C.  [Rules 62-4.070(1) & (3) and 62-213.440(1) (Monitoring), F.A.C.]

- Particulate Matter.  The test methods for particulate emissions shall be EPA Methods 17, 5, 5B or 5F, incorporated by reference in Chapter 62-297, F.A.C.  The minimum sample volume shall be 30 dry standard cubic feet.  EPA Method 5 may be used with filter temperature no more than 320 degrees Fahrenheit.  For EPA Method 17, stack temperature shall be less than 375 degrees Fahrenheit.  The owner or operator may use EPA Method 5 to demonstrate compliance.  EPA Method 3 or 3A with Orsat analysis shall be used when the oxygen based F-factor, computed according to EPA Method 19, is used in lieu of heat input.  Acetone wash shall be used with EPA Method 5 or 17.  [Rules 62-4.070(1) & (3) and 62-213.440(1) (Monitoring), F.A.C.]

- Sulfur Dioxide.  The test methods for sulfur dioxide emissions shall be EPA Methods 6, 6A, 6B, or 6C, incorporated by reference in Chapter 62-297, F.A.C.  Fuel sampling and analysis may be used as an alternate sampling procedure if such a procedure is incorporated into the operation permit for the emissions unit.  If the emissions unit obtains an alternate procedure under the provisions of Rule 62-297.620, F.A.C., the procedure shall become a condition of the emissions unit’s permit.  The Department will retain the authority to require EPA Method 6 or 6C if it has reason to believe that exceedences of the sulfur dioxide emissions limiting standard are occurring.  Results of an approved fuel sampling and analysis program shall have the same effect as EPA Method 6 test results for purposes of demonstrating compliance or noncompliance with sulfur dioxide standards.  [Rules 62-4.070(1) & (3) and 62-213.440(1) (Monitoring), F.A.C.]

- When burning Liquid Fuel - Compliance with Sulfur Limit.  The permittee may use the EPA test methods, referenced above, to demonstrate compliance; however, as an alternate sampling procedure authorized by permit, the permittee elected to demonstrate compliance by accepting a liquid fuel sulfur limit that will be verified with a fuel analysis provided by the vendor or the permittee upon each fuel delivery.  [Rules 62-4.070(1) & (3) and 62-213.440(1) (Monitoring), F.A.C.]

- Sulfur Content Sampling Methods.  The fuel sulfur content, percent by weight, for liquid fuels shall be evaluated using either ASTM D2622-92, ASTM D4294-90, or both ASTM D4057-88 and ASTM D129-91, or the respective successor ASTM method(s).  [Rules 62-213.440 and 62-297.440, F.A.C.]

- Ammonia (NH3) Slip Compliance.  Compliance with the ammonia (NH3) slip limit shall be determined using EPA conditional test method (CTM-027), EPA Method 320, or other methods approved by the Department.  [Permit No. 0570039-020-AC (amended by 0570039-026, -031 & -036-AC).]

- Determination of Heat Input.  The heat input shall be calculated as the product of the gross heat rate (Btu/kWh) and gross power output (MW).  The gross power output shall be measured on a 4-hour rolling averagean arithmetic average during the compliance demonstration test.  The gross unit heat rate will use a 3-month rolling "seasonal" average based on calculated monthly heat rates.  These rates shall be determined by the tons of coal bunkered, composite coal analyses and gross power output for the month.  The composite fuel samples shall be collected by on-site personnel in accordance with ASTM standardsindustry standard practices.  [Rule 62-213.440, F.A.C.]

Recordkeeping and Reporting Requirements

- Reporting Schedule.  The following report shall be submitted to the Compliance Authority:

| Report | Reporting Deadline(s) | Related Condition(s) |
| --- | --- | --- |
| Quarterly NOX Emissions | Every 3 months (quarterly) | B.546. |
| Quarterly CO Report | Every 3 months (quarterly) | B.557. |
| NSPS Excess Emissions and Monitoring System Performance | Every 6 months (semi-annually), except when more frequent reporting is specifically required | B.5760 and B61. |

[Rule 62-210.700(6), F.A.C.; and, 40 CFR 60, Subpart A.]

- Quarterly NOX Report.  The permittee shall submit a quarterly NOX report to the Department and the EPCHC within 30 days following each calendar quarter.  This report shall contain the heat input weighted 30-day NOX rolling average, all time periods of boiler operation as well as a statement of CEMS and/or boiler malfunction, start-up, shutdown or abnormal events.  [Rules 62-4.070(1) & (3) and 62-213.440(1) (Monitoring), F.A.C.]

- Quarterly CO Report.  Within 30 days following the end of each calendar-quarter, the permittee shall submit a report to the Department and the EPCHC summarizing periods of CO emissions in excess of the BACT permit standard following the NSPS format in 40 CFR 60.7(c), Subpart A.  In addition, the report shall summarize the CO CEMS system monitor availability for the previous quarter.  [PSD-FL-390/Permit No. 0570039-027 (amended by PSD-FL-390A/Permit No. 0570039-042-AC).]

- Recordkeeping.  Gravimetric instrument data verifying that the 20.0% maximum petroleum coke content by weight has not been exceeded shall be maintained for five years and submitted to the Department and the EPCHC with each annual operating report.  Also to be maintained and available for inspection shall be a daily record of operation showing the date, fuel used, mode of operation (integrated/non-integrated), and the duration of all startups, shutdowns and malfunctions. The permittee shall maintain copies of fuel analyses containing information on sulfur content, ash content, and heating values.  [PSD-FL-040; Rules 62-4.070(1) & (3), 62-213.440(1)(b)2.b., F.A.C.; and, PA 79-12.]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440, F.A.C.]

Other Requirements

- NSPS Requirements - Subpart A.  This emissions unit shall comply with all applicable requirements of 40 CFR 60, Subpart A, General Provisions, including:

40 CFR 60.7, Notification and Recordkeeping

40 CFR 60.8, Performance Tests

40 CFR 60.11, Compliance with Standards and Maintenance Requirements

40 CFR 60.12, Circumvention

40 CFR 60.13, Monitoring Requirements

40 CFR 60.19, General Notification and Reporting Requirements,

which have been adopted by reference in Rule 62-204.800(8)(d), F.A.C., except that the Secretary is not the Administrator for purposes of 40 CFR 60.4, 40 CFR 60.8(b)(2) and (3), 40 CFR 60.11(e)(7) and (8), 40 CFR 60.13(g), (i) and (j)(2), and 40 CFR 60.16.  This emissions unit shall comply with Appendix 40 CFR 60 Subpart A included with this permit.  [Rule 62-204.800(8)(d), F.A.C.]

- NSPS Requirements - Subpart Da.  Except as otherwise provided in this permit, this emissions unit shall comply with all applicable provisions of 40 CFR 60, Subpart Da, Standards of Performance for Electric Utility Steam Generating Units for Which Construction is Commenced After September 18, 1978, adopted by reference in Rule 62-204.800(8)(b)2., F.A.C., except that the Secretary is not the Administrator for purposes of 40 CFR 60.47a.  This emissions unit shall comply with Appendix 40 CFR 60 Subpart Da included with this permit.  [Rule 62-204.800(8)(b)2., F.A.C.]

- Stack Height.  The height of the boiler exhaust stack for Unit No. 4 (BB004) shall not be less than 490 ft. above grade.  [Rule 62-210.550(3) (Good Engineering Practice (GEP) stack height), F.A.C.; and, PA 79-12.]

Reserved.

The specific conditions in this section apply to the following emissions units:

| E.U. ID No. | ## Brief Description |
| --- | --- |
|  | Combustion Turbine |
| -007 | Combustion Turbine No. 1 |

Reserved

Combustion Turbine No. 1 removed from service on 10/26/2010.

Section reserved to preserve numbering. (will be removed at next renewal)

The specific conditions in this section apply to the following emissions units:

| E.U. ID No. | ## Brief Description |
| --- | --- |
|  | Flyash Handling and Storage - Silo Nos. 1 and 2 |
| -008 | Fly Ash Silo No. 1 Baghouse |
| -018 | Fly Ash Silo No. 1 Truck Loadout |
| -009 | Fly Ash Silo No. 2 Baghouse |
| -019 | Fly Ash Silo No. 2 Truck Loadout |
| -026 | Fly Ash Handling and Storage Fugitive Emissions (all except silos) |

These emissions units consist of Fly Ash Silo Nos. 1 and 2, which handle fly ash from Steam Generator Unit Nos. 1, 2 and/or 3, as described below.

Fly Ash Silo No. 1 handles fly ash from Steam Generator Units No. 1 and No. 2.  Fly ash is pneumatically conveyed from the individual electrostatic precipitators to Silo No. 1.  Also, the fly ash may be pneumatically conveyed from tanker trucks to and/or from Silo No. 2 to Silo No. 1.  The sum total loading rate to the silo for all the processes combined is 44.5 tons per hour.  Fly ash from Silo No. 1 is discharged in either a wet or dry state.  The dry fly ash is pneumatically conveyed to the beneficiation facility and/or gravity fed by tubing into totally enclosed tanker trucks.  Fly ash is chemically or physically processed through a pugmill and then the wet ash unloaded into dump trucks.  Particulate matter emissions generated by silo loading and silo unloading to a tanker truck are controlled by a 20,081 dscfm Flex Kleen Model No. 84 UDTR-640 baghouse in addition to reasonable precautions.  Fly Ash Silo No. 1 truck loadout is an insignificant activity since it occurs infrequently only during emergency conditions when flyash is unable to be transferred to the beneficiation facility. All fly ash handled is generated on-site.

Fly Ash Silo No. 2 handles fly ash from Steam Generator Units Nos. 1, 2 and/or 3.  Fly ash is pneumatically conveyed in a series of pipes from the individual unit precipitators (Units 1, 2 and/or 3, only two units at any time) to the silo for temporary storage.  Fly ash from Silo No. 2 is discharged in either a wet or dry state.  From the silo, the dry fly ash is pneumatically conveyed to the beneficiation facility and/or gravity fed by tubing into closed tanker trucks and transported to an off-site consumer.  The wet fly ash is processed through a pugmill and then unloaded into a dump truck to be transported to an off-site consumer.  Particulate matter emissions generated during silo loading operation and from the tanker truck loadout chutes are controlled by a 20,081 dscfm Flex Kleen, Model No. 84 UDTR-640 baghouse in addition to reasonable precautions.  Fly Ash Silo No. 2 truck loadout is an insignificant activity since it occurs infrequently only during emergency conditions when flyash is unable to be transferred to the beneficiation facility.

{Permitting note(s):  These emissions units are regulated under Rule 1-3.52, Rules of the Environmental Protection Commission (EPC) of Hillsborough County and Rules 62-210.300 (Permits Required) and 62.296.711 Reasonably Available Control Technology (RACT) PM (Materials Handling, Sizing, Screening, Crushing and Grinding Operations) F.A.C., Permits Required.}

Essential Potential to Emit (PTE) Parameters

- Hours of Operation.  These emissions units may operate continuously (8,760 hours/year).  [Rule 62-210.200 (Definitions - Potential to Emit (PTE), F.A.C.]

- Permitted Capacity.  The maximum permitted loading rate for all Fly Ash Silo No. 1 processes combined is 44.5 tons per hour.  The maximum permitted loading rate for all Fly Ash Silo No. 2 processes combined is 44.5 tons per hour.  [Rules 62-4.160(2), 62-210.200 (Definitions - PTE); and, AOC29-194516.]

Emission Limitations and Standards

Unless otherwise specified, the averaging times for Specific Conditions D.3. - D.4. are based on the specified averaging time of the applicable test method.

- Particulate Matter Emissions.  Total maximum allowable emissions of particulate matter from the each silo baghouse shall not exceed 0.03 gr/dscf, 5.16 lbs/hr and 22.62 tons/yr based on a design flow rate of 20,081 dscfm.  [Rules 62-4.160(2) and 62-296.711(2)(b), F.A.C.; AO29-160255 and AO29-161082]

- Visible Emissions.  Visible emissions from the flyash handling system and flyash silos are limited to 5% opacity.  [PA 79-12; and, Chapter 1-3.52, Rules of the EPC.]

- Unconfined Emissions of Particulate Matter.  All reasonable precautions shall be taken to prevent and control generation of unconfined emissions of particulate matter in accordance with the provisions in Rule 62-296.320(4), F.A.C.  These provisions are applicable to any source, including, but not limited to, vehicular movement, transportation of materials, construction, alterations, demolition or wrecking, or industrial related activities such as loading, unloading, storing and handling.  The following reasonable precaution shall be taken to control unconfined particulate matter emissions associated with the fly ash silo/truck operations.  Reasonable precautions shall include, but not limited to:

a.  	Fly ash transported by dump truck shall be adequately wetted and processed through the pugmill;

b.  	Dump trucks used to transport fly ash shall utilize tarps at all times except when loading/unloading;

c.  	Fly ash transported in a dry state shall be accomplished utilizing an enclosed tanker truck;

d.  	Fly ash spilled and/or leaked on plant grounds shall be adequately wetted and disposed of daily;

e.  	Fly ash collected from spills and/or leaks must be adequately wetted at all times;

f.  	Ensure the proper seating of the unloader chute onto the tanker inlet prior to loading;

g.  	Keep the dust extractor operational during loading;

h.  	Close the tanker's inlet as soon as practical after the loading process;

i.  	Extend the tubing from the silo into the closed tanker type trucks during loadout; and,

j.  	Periodic watering of plant roads.

[Rules 62-296.320(4)(c)2. and 62-4.070(1) & (3) (Reasonable Assurance), F.A.C.]

Excess Emissions

- Excess Emissions Allowed.  Excess emissions resulting from startup, shutdown or malfunction of any emissions unit shall be permitted providing (1) best operational practices to minimize emissions are adhered to and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C.]

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown, or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C.]

Test Methods and Procedures

- Test Methods.  Required tests shall be performed in accordance with the following reference methods:

| Method(s) | Description of Methods and Comments |
| --- | --- |
| EPA Methods 1 - 4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| EPA Method 5 | Methods for Determining Particulate Matter Emissions |
| EPA Method 9 | Visual Determination of the Opacity of Emissions |

The above methods are described in Chapter 62-297, F.A.C. and/or 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Chapter 62-297, F.A.C.]

- Annual Compliance Test.  Except as specified in Specific Condition D.11., during each federal fiscal year (October 1st to September 30th), Emissions Unit ID Nos. -008, and -009 shall be tested to demonstrate compliance with the emission limitations and standards for VE.  The annual compliance tests will be used in lieu of the compliance test prior to renewal.  [Rule 62-297.310(7), F.A.C.]

- Compliance Test Prior To Renewal.  Except as specified in Specific Condition D.13., prior to permit renewal, Emissions Unit ID Nos. -008, and -009 shall be tested to demonstrate compliance with the emission limitations and standards for VE.  [Rule 62-297.310(7)(a)3., F.A.C.]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- Visible Emissions Test.  Compliance with the visible emission limits of this permit shall be demonstrated by an annual compliance test using EPA Method 9.  The duration of the annual test shall be 30 minutes.  [Rules 62-4.070(3) and 62-297.310(4)(a)2., F.A.C.]

- Visible Emissions Test in Lieu of PM Stack Test.  The owner or operator is permitted to comply with the VE limit and the VE testing requirement in lieu of regularly demonstrating compliance with the PM limitation.  If the Department has reason to believe that the particulate matter limitation is not being met, it shall require compliance be demonstrated by conducting a particulate matter test in accordance with EPA Method 5 specified at 40 CFR 60 Appendix A.  [Rules 62-4.070(3) and 62-296.711(3)(c), F.A.C.]

- Testing Conditions.  Compliance testing for the silo and tanker truck loading operations shall be conducted under the following conditions:

a. 	All conveyance hoppers will be operational during the test.

b. 	All fly ash will be directed to the silo, no reinjection of fly ash to the boiler systems will occur during the test.

c. 	The boilers shall operate at the maximum capability of this unit under normal operating conditions during the test.

d. 	Two tanker trucks shall be loaded during the test.  The loading valve shall be open to allow 90%-100% of the maximum loading rate during testing.  Position of the valve during testing shall be recorded.

e. 	The visible emission test shall be at least 30 minutes in duration and the period of time during which truck loading occurred indicated on the test report.

[Rules 62-4.070(1) & (3) and 62-297.310, F.A.C.]

Recordkeeping and Reporting Requirements

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440, F.A.C.]

The specific conditions in this section apply to the following emissions units:

| E.U. ID No. | ## Brief Description |
| --- | --- |
| Flyash Handling and Storage - Silo No. 3 |  |
| -014 | Fly Ash Silo No. 3 Baghouse |
| -027 | Fly Ash Silo No. 3 Truck Loadout |
| -028 | Fly Ash Handling System Fugitive Emissions |

These emissions units consist of Fly Ash Silo No. 3, which handles fly ash from Steam Generator Unit No. 4. Also, fly ash may be pneumatically conveyed from tanker trucks to Silo No. 3.  The dry fly ash is pneumatically conveyed to a beneficiation facility and/or gravity fed by tubing into totally enclosed tanker trucks.  The sum total loading rate to the silo for all the processes combined is 44.5 tons per hour.  Fly ash can be chemically or physically processed through a pugmill and then the wet ash loaded into dump trucks.  Particulate matter emissions are controlled by a 1,200 dscfm Flex Kleen Model 84-WRTC-80-II-G baghouse.  Fly Ash Silo No. 3 truck loadout and handling system fugitives are insignificant activities since they occur infrequently only during emergency conditions when flyash is unable to be transferred to the beneficiation facility.

{Permitting note(s):  These emissions units are regulated under Rules 62.296.711 RACT PM (Materials Handling, Sizing, Screening, Crushing and Grinding Operations) and 62-212.400, F.A.C.,(Prevention of Significant Deterioration [PSD-FL-040]), F.A.C.; Power Plant Siting Certification [PA 79-12]; and Rule 1-3.52, Rules of the Environmental Protection Commission (EPC) of Hillsborough County.}

Essential Potential to Emit (PTE) Parameters

- Hours of Operation.  Thisese emissions units may operate continuously (8,760 hours/year).  [Rule 62-210.200 (Definitions - (PTE), F.A.C.]

Operational Requirements

- Negative Pressures.  The flyash handling system (including transfer and silo storage) shall be maintained at negative pressures and vented to a control system.  
[PSD-FL-040 and amended in Permit No. 0570039-066-AC (PSD-FL-040A)]

- System Pressure Monitoring.  The system pressure will be monitored quarterly to assess that the system is operating under negative pressure.  [Rule 62-213.440(1)(b)1.b. (Periodic Monitoring), F.A.C. {Resolution of objection from USEPA dated 12/14/2000.}]

Emission Limitations and Standards

Unless otherwise specified, the averaging times for Specific Conditions E.4. - E.5. are based on the specified averaging time of the applicable test method.

- Particulate Matter Emissions.  Particulate matter emissions from the flyash handling system and flyash silo baghouse shall not exceed 0.2 lb/hr.  
[PA 79-12; PSD-FL-040 and amended in Permit No. 0570039-066-AC (PSD-FL-040A)]

- Visible Emissions.  Visible emissions from the flyash handling system and the flyash silo baghouse are limited to 5% opacity.  When loading fly ash into trucks from fly ash silo No. 3 (E U -027) the reasonable precautions specified in Specific Condition D.5. to prevent and control generation of unconfined emissions of particulate matter shall be followed.  [Rule 62-296.711(3)(c), F.A.C.; PA 79-12; PSD-FL-040 and amended in Permit No. 0570039-066-AC (PSD-FL-040A); and, Chapter 1-3.52, Rules of the EPC.]

Excess Emissions

- Excess Emissions Allowed.  Excess emissions resulting from startup, shutdown or malfunction of any emissions unit shall be permitted providing (1) best operational practices to minimize emissions are adhered to and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C.]

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown, or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C.]

Test Methods and Procedures

- Test Methods.  Required tests shall be performed in accordance with the following reference method(s):

| Method(s) | Description of Method(s) and Comment(s) |
| --- | --- |
| EPA Methods 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| EPA Method 5 | Methods for Determining Particulate Matter Emissions |
| EPA Method 9 | Visual Determination of the Opacity of Emissions |

The above methods are described in Chapter 62-297, F.A.C. and/or 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Chapter 62-297, F.A.C.]

- Annual Compliance Test.  Except as specified in Specific Condition E.112., during each federal fiscal year (October 1st to September 30th), Emissions Unit ID No. -014 shall be tested to demonstrate compliance with the emission limitations and standards for VE.  The annual compliance tests will be used in lieu of the compliance test prior to renewal.  [Rules 62-297.310(7) and 62-213.440(1)(b)1.b. (Periodic Monitoring), F.A.C.]

- Compliance Test Prior To Renewal.  Except as specified in Specific Condition E.12., prior to permit renewal, Emissions Unit ID Nos. -014 shall be tested to demonstrate compliance with the emission limitations and standards for VE.  [Rule 62-297.310(7)(a)3., F.A.C.]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- Visible Emissions Test in Lieu of PM Stack Test.  The owner or operator is permitted to comply with the VE limit and the VE testing requirement in lieu of regularly demonstrating compliance with the PM limitation.  If the Department has reason to believe that the particulate matter limitation is not being met, it shall require compliance be demonstrated by conducting a particulate matter test in accordance with EPA Method 5 specified at 40 CFR 60 Appendix A.  [Rules 62-4.070(3) and 62-296.711(3)(c), F.A.C.]

Recordkeeping and Reporting Requirements

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440, F.A.C.]

Unless otherwise specified, the specific conditions in this section apply to the following emissions units:

| E.U. ID No. | ## Brief Description |
| --- | --- |
| Limestone Handling and Storage |  |
| -011 | Truck Limestone Unloading Receiving Hopper |
| -012 | Limestone Silo A with 2 Baghouses (2) |
| -013 | Limestone Silo B with 2 Baghouses (2) |
| -023 | Limestone Handling Conveyor LB/ to Conveyor LC with Baghouse |
| -050 | Limestone Handling Conveyor LD/ to Conveyor LE with Baghouse |
| -025 | Limestone Storage and Handling Fugitive Emissions |
| Limestone Handling for FGD System for Units 1 and 2 |  |
| -020 | Drops from Limestone Conveyors LE,/LF/ and LG/ and Silo C Belt Feeder with Baghouse |
| -021 | Silo C with one Baghouse |

Emissions Unit Description for E.U. ID Nos. -011, -012, -013, -023 and -050-025

Limestone is received by truck and conveyed to the limestone storage building.  From the storage building it is reclaimed and conveyed to the limestone silo A, B and/or C.  A fully enclosed bucket elevator and a portable hopper/conveyor system are used as backup system to provide limestone to Silo C.  The maximum annual tons of limestone handled is 1,471,680.

Particulate matter emissions generated by the transfer of limestone from Handling Conveyor LB to Conveyor LC are controlled by a Sternvent Model DKED18003 baghouse.  Particulate matter emissions generated by the transfer of limestone from Handling Conveyor LD to Conveyor LE are controlled by a Sternvent Model DKED 18003 baghouse.

{Permitting note(s):  These emissions units are regulated under Rule 212.400, F.A.C., Prevention of Significant Deterioration [PSD-FL-040]; Power Plant Siting Certification [PA 79-12]; and, Rule 1-3.52, Rules of the Environmental Protection Commission (EPC) of Hillsborough County.}

Emissions Unit Description for E.U. ID Nos. -020 and -021

Components of the limestone handling system provide limestone for the flue gas desulfurization (FGD) system.  The components are Silo C and its related rotary unloader, belt feeder and wet ball mill, and reversible belt conveyors LF and LG.  Conveyors LF and LG replace an existing bifurcated chute which feeds from conveyor LE to silos A and B.  Particulate matter emissions from drops from limestone handling conveyors LE, LF and LG and the silo C belt feeder are controlled by a baghouse:  American Air Filter Fabripulse - Model B, size 12-72-1155.  Particulate matter emissions from displaced air in silo C are controlled by a baghouse:  American Air Filter Fabripak, size 6-16-132.  The wet ball mill is a wet process with no expected particulate matter emissions.

{Permitting note(s):  These emissions units are regulated under Subpart OOO, Standards of Performance for Nonmetallic Mineral Processing Plants, adopted and incorporated by reference in Rule 62-204.800(8)(b)64., F.A.C.; Rule 62-296.711, F.A.C., Reasonably Available Control Technology (RACT) Particulate Matter (PM) - Materials Handling, Sizing, Screening, Crushing and Grinding Operations; and, Chapter 1-3.52, Rules of the Environmental Protection Commission (EPC) of Hillsborough County.}

Essential Potential to Emit (PTE) Parameters

- Hours of Operation.  These emissions units may operate continuously (8,760 hours/year).  [Rule 62-210.200 (Definitions - (PTE), F.A.C.]

Operational Requirements

- (This condition applies to Emissions Unit ID No. -023 and -050.) Enclosure of Equipment.  All conveyors and conveyor transfer points shall be enclosed to preclude particulate matter emissions.  [PSD-FL-040.]

- (This condition applies to Emissions Unit ID No. -023 and -050.) Best Operational Practices.  The conveyor system shall be inspected quarterly and maintenance shall be conducted as needed in accordance with best operational practices.  [Proposed by applicant; and, Rules 62-213.440, F.A.C.62-4.070(3) and 62-210.700(1), F.A.C.]

- (This condition applies to Emissions Unit ID Nos. -012, -013, and -023 and -050.) Operations.  The limestone handling conveyor transfer points and silos shall be maintained at negative pressures with the exhaust vented to a control system(s).  [PSD-FL-040.]

- (This condition applies to Emissions Unit ID Nos. -020 and -021.) Enclosure of Equipment.  All conveyors and conveyor transfer points shall be enclosed and exhaust from this equipment shall be directed to a baghouse to minimize particulate matter emissions.  [Rule 62-4.070(3, F.A.C. )PSD-FL-040]

- (This condition applies to Emissions Unit ID Nos. -020 and -021.) Operating Procedures.  Enclosures and baghouses for these emissions units shall be properly operated and maintained at all times in a condition to minimize particulate matter emissions.  All operators of air pollution control devices shall be properly trained in plant equipment.  The owner and operator shall ensure that all facility staff responsible for these emissions units are trained in their operation and maintenance in accordance with the guidelines and procedures as established by the equipment manufacturers.  [Rule 62-4.070(3)62-213.440, F.A.C.]

Emission Limitations and Standards

Unless otherwise specified, the averaging times for Specific Conditions F.7. - F.9. are based on the specified averaging time of the applicable test method.

- (This condition applies to Emissions Unit ID No. -023 and -050.) Particulate Matter and Visible Emissions.  Total combined particulate matter emissions from the limestone handling conveyors LB/LC and LD/LE baghouses shall not exceed 0.65 lb/hr.  Visible emissions are limited to 5% opacity.  Compliance testing for particulate matter emissions is not required provided the opacity limit is maintained.  [PSD-FL-040; PA 79-12; and, Chapter 1-3.52, Rules of the EPC.]

- (This condition applies to Emissions Unit ID Nos. -012 and -013.) Particulate Matter and Visible Emissions.  Total combined particulate matter emissions from the limestone silos baghouses shall not exceed 0.05 lb/hr. Visible emissions are limited to 5% opacity.  Compliance testing for particulate matter emissions is not required provided the opacity limit is maintained.  [PSD-FL-040; PA 79-12; and, Chapter 1-3.52, Rules of the EPC.]

- (This condition applies to Emissions Unit ID Nos. -020 and -021.) Particulate Matter and Visible Emissions.  No owner or operator shall cause or allow visible emissions from the baghouses controlling these emissions units in excess of 0.03 grains per dry standard cubic feet (gr/dscf) and 5% opacity.  [40 CFR 60.672(a)(1) and (2); Rules 62-4.070(3) and Rule 62-296.711(2)(b), F.A.C., Chapter 1-3.52, Rules of the EPC, and request of applicant (VE limit).]

{Permitting note(s):  The visible emission limit of this condition is more stringent than the limitations of 40 CFR 60.672(a)(2) and 60.672(f), and compliance with this limit will assure compliance with those requirements.}

Excess Emissions

- Excess Emissions Allowed.  Excess emissions resulting from startup, shutdown or malfunction of any emissions unit shall be permitted providing (1) best operational practices to minimize emissions are adhered to and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C.]

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown, or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C.]

Test Methods and Procedures

- Test Methods.  Required tests shall be performed in accordance with the following reference method(s):

| Method(s) | Description of Method(s) and Comment(s) |
| --- | --- |
| EPA Methods 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| EPA Method 5 | Methods for Determining Particulate Matter Emissions |
| EPA Method 9 | Visual Determination of the Opacity of Emissions |
| EPA Method 22 | Visual Determination of Fugitive Emissions from Material Sources |

The above methods are described in Chapter 62-297, F.A.C. and/or 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Chapter 62-297, F.A.C.]

- Annual Compliance Tests.  Except as specified in Specific Condition F.156., during each federal fiscal year (October 1st to September 30th), the emissions units with baghouses shall be tested to demonstrate compliance with the emission limitations and standards for visible emissions (VE).  The annual compliance tests will be used in lieu of the compliance test prior to renewal.  [Rule 62-297.310(7), F.A.C.]

- Compliance Tests Prior To Renewal.  Except as specified in Specific Condition F.16., the emissions units with baghouses shall be tested to demonstrate compliance with the emission limitations and standards for visible emissions (VE).  [Rule 62-297.310(7)(a)3., F.A.C.]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- (This condition applies to Emissions Unit ID Nos. -012, -013, -020, -021 and -023 and -050.) Visible Emissions Tests in Lieu of PM Stack Tests.  The owner or operator is permitted to comply with the VE limit and the VE testing requirement in lieu of regularly demonstrating compliance with the PM limitations of 40 CFR 60.672(a)(1) and (2).  If the Department has reason to believe that the particulate matter limitation is not being met, it shall require compliance be demonstrated by the test method specified by 40 CFR 60.675.  [Rules 62-4.070(3) and 62-296.711(3)(c), F.A.C.]

- (This condition applies to Emissions Unit ID Nos. -011, -012, -013, and -023 and -050.) Visible Emissions Tests.  The permittee shall perform an annual VE test to satisfy the periodic monitoring requirements of these conditions.  In addition, the system pressure will be monitored quarterly to assess that the system is operating under negative pressure.  [Rule 62-213.440(1)(b)1.b. (Periodic Monitoring), F.A.C. {Resolution of objection from USEPA dated 12/14/2000.}]

- (This condition applies to Emissions Unit ID Nos. -020 and -021.) Visible Emissions Tests.  Compliance with the visible emission limits of this permit shall be demonstrated by an annual compliance test using EPA Method 9.  The duration of initial tests shall be 3 (three) hours and the duration of subsequent annual tests shall be 30 (thirty) minutes.

{Permitting note(s):  The 3 (three) hour duration of initial tests complies with the requirements of the NSPS and the 30 (thirty) minute duration of subsequent tests complies with state rules.}

[Rules 62-4.070(3) and 62-297.310(4)(a)2., F.A.C.; and, 40 CFR 60.11(b)]

Recordkeeping and Reporting Requirements

- (This condition applies to Emissions Unit ID Nos. -020 and -021.) Records of Maintenance.  The owner or operator shall make and maintain records of maintenance on the enclosures and baghouses sufficient to demonstrate compliance with the operating procedures requirements of Specific Condition F.6.  [Rule 62-213.4404.070(3), F.A.C.]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440, F.A.C.]

# (These conditions apply to Emissions Unit ID Nos. -020 and -021.) NSPS 40 CFR 60 Requirements

- NSPS Requirements - Subpart A.  These emissions units shall comply with all applicable requirements of 40 CFR 60, Subpart A, General Provisions, including:

40 CFR 60.7, Notification and Recordkeeping

40 CFR 60.8, Performance Tests

40 CFR 60.11, Compliance with Standards and Maintenance Requirements

40 CFR 60.12,

40 CFR 60.13, Monitoring Requirements

40 CFR 60.19, General Notification and Reporting Requirements,

which have been adopted by reference in Rule 62-204.800(8)(d), F.A.C., except that the Secretary is not the Administrator for purposes of 40 CFR 60.4, 40 CFR 60.8(b)(2) and (3), 40 CFR 60.11(e)(7) and (8), 40 CFR 60.13(g), (i) and (j)(2), and 40 CFR 60.16.  These emissions units shall comply with Appendix 40 CFR 60 Subpart A included with this permit.  [Rule 62-204.800(8)(d), F.A.C.]

- NSPS Requirements - Subpart OOO.  These emissions units shall comply with all applicable requirements of 40 CFR 60, Subpart OOO, Standards of Performance for Nonmetallic Mineral Processing Plants, adopted and incorporated by reference in Rule 62-204.800(8)(b)64., F.A.C.  These emissions units/points shall comply with Appendix 40 CFR 60 Subpart OOO included with this permit.  [Rule 62-204.800(8)(b)64., F.A.C.]

The specific conditions in this section apply to the following emissions units:

| E.U. ID No. | ## Brief Description |
| --- | --- |
| Coal Bunkers with Roto-Clones |  |
| -015 | Unit No. 1 Coal Bunker with Roto-Clone |
| -016 | Unit No. 2 Coal Bunker with Roto-Clone |
| -017 | Unit No. 3 Coal Bunker with Roto-Clone |
| -039 | Unit No. 4 Coal Bunker with Roto-Clone |

These emissions units are Coal Bunkers for Steam Generator Unit Nos. 1 - 4 with an exhaust fan/cyclone collector (Roto-Clone) controlling dust emission from each unit’s respective bunker.  The annual coal throughput shall not exceed 4000 TPH per bunker.  Two moving transfer stations via their respective conveyor belts route coal through enclosed chutes to the various bunkers.  Coal Bunkers 1- 4 are each equipped with a 9400 acfm American Air Filter (AAF) Company Type D Roto-Clone to abate dust emissions during ventilation.  A number of vent pipes convey fresh air from each bunker to a Roto-Clone during particulate matter removal.  Particulate matter removed by the Roto-Clones is returned to the coal bunkers via a hopper and return line.  The Unit No. 1 Coal Bunker is situated west of Unit No. 2 Coal Bunker.  The Unit No. 3 Coal Bunker is situated east of Unit No. 2 Coal Bunker.  The Unit No. 4 Coal Bunker is located east of Unit No. 3.  The roto-clones share a common head space to maintain a safe working environment in the blending bin building.

{Permitting note(s):  These emissions units are regulated under Chapter 1-3.52, Rules of the Environmental Protection Commission (EPC) of Hillsborough County.  Each of these emissions units is exempt from the requirements of Rule 62-296.711, F.A.C., Reasonably Available Control Technology (RACT) - Materials Handling, Sizing, Screening, Crushing and Grinding Operations, pursuant to Rule 62-296.700(2)(c), F.A.C., because it has an allowable emission rate of less than one ton per year.}

Essential Potential to Emit (PTE) Parameters

- Hours of Operation.  The hours of operation for each bunker loading shall not exceed 4,167 hours per year.  [Rule 62-210.200 (Definitions - (PTE), F.A.C.; and, Applicant Request.]

Emission Limitations and Standards

Unless otherwise specified, the averaging times for Specific Conditions G.2. - G.3. are based on the specified averaging time of the applicable test method.

- Particulate Matter.  Particulate matter (PM) emissions shall not exceed 0.48 lbs/hr and 0.99 tons per year from each roto-clone exhaust.  [Rules 62-4.070(3) and 62-296.700(2)(c), F.A.C.; and, Applicant Request.]

{Permitting note(s):  This particulate matter limitation ensures that allowable emissions are less than one ton per year from each emissions unit.}

- Visible Emissions.  Visible emissions from each of these emissions units are limited to 5% opacity.  [Rule 62-297.620(1)-(3), F.A.C.; Permit No. ACO29-163788; and Chapter 1-3.52, Rules of the EPC; and, Applicant Request.]

Excess Emissions

- Excess Emissions Allowed.  Excess emissions resulting from startup, shutdown or malfunction of any emissions unit shall be permitted providing (1) best operational practices to minimize emissions are adhered to and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C.]

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown, or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C.]

Test Methods and Procedures

- Test Methods.  Required tests shall be performed in accordance with the following reference method(s):

| Method(s) | Description of Method(s) and Comment(s) |
| --- | --- |
| EPA Methods 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| EPA Method 5 | Methods for Determining Particulate Matter Emissions |
| EPA Method 9 | Visual Determination of the Opacity of Emissions |

The above methods are described in Chapter 62-297, F.A.C. and/or 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Chapter 62-297, F.A.C.]

- Annual Compliance Test.  During each federal fiscal year (October 1st to September 30th), one of the coal bunker roto-clone unitsEmissions Unit ID Nos. -015, -016, -017 and -039 shall be tested to demonstrate compliance with opacitythe emission limitations and standards for visible emissions (VE).  Each year a different roto-clone unit shall be tested in subsequent order (Unit 1, Unit 2. Etc.).  The annual compliance tests will be used in lieu of the compliance test prior to renewal.  [Rules 62-297.310(7) and 62-213.440(1)(b)1.b. (Periodic Monitoring), F.A.C. {Resolution of objection from USEPA dated 12/14/2000.}]

- Compliance Test Prior To Renewal.  Prior to permit renewal, Emissions Unit ID Nos. -015, -016, -017 and -039 shall be tested to demonstrate compliance with the emission limitations and standards for visible emissions (VE).  [Rule 62-297.310(7)(a)3., F.A.C.]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- Visible Emissions Test.  Compliance with the visible emission limits of this permit shall be demonstrated by an annual compliance test using EPA Method 9.  The duration of the annual test shall be 30 (thirty) minutes.  [Rules 62-4.070(3) and 62-297.310(4)(a)2., F.A.C.]

Recordkeeping and Reporting Requirements

- Records.  The permittee shall monitor the hours of operation of coal bunker loading.  [Rule 62-213.440(1)(b)1.b. (Periodic Monitoring), F.A.C. {Resolution of objection from USEPA dated 12/14/2000.}.]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440, F.A.C.]

The specific conditions in this section apply to the following emissions units:

| E.U. ID No. | ## Brief Description |
| --- | --- |
| Solid Fuel Yard |  |
| -010 | Fugitive Emissions from Fuel Unloading and Handling Operations |

This emissions unit consists of solid fuel handling and storage activities at the Big Bend Station as described in more detail below.

Solid fuel (consisting of coal and petcokepetroleum coke) is unloaded from ships and barges into the solid fuel yard, the blending bins or directly to the tripper room via belt conveyors.  Solid fuel may also be received/unloaded by railcar (see EU ID No. -047) and conveyed to the fuel yard.  Solid fuel from the piles is loaded onto belt conveyors using a rail mounted or mobile reclaimer.  The solid fuel is then belt conveyed to the blending bins (see EU ID No. -029), which consist of six storage bins, where the solid fuel may be blended for use at the plant, or transloaded into trucks for shipment off site (see EU ID No. -046).

{Permitting note(s):  These emissions units received a determination of Best Available Control Technology pursuant to are regulated under Rule 62-212.400(5), F.A.C., Prevention of Significant Deterioration [PSD-FL-040]; Therefore, Rule 62-296.70011, F.A.C., Reasonably Available Control Technology (RACT) Particulate Matter (PM) does not apply - Materials Handling, Sizing, Screening, Crushing and Grinding Operations; Rule 62-210.300, F.A.C., Permits Required; Power Plant Siting Certification [PA 79-12]; and, Chapter 1-3.52, Rules of the EPC, Rules of the Environmental Protection Commission (EPC) of Hillsborough County.}

Authorized Emissions Points

The emissions unit contained in this subsection is comprised of the following emissions points:

| E.U. ID No. -010: Solid Fuel Yard Unloading and Handling Operations |  |  |
| --- | --- | --- |
| Point ID | Brief Description of Emissions Point | Pollutant |
| Barge Unloading Operations |  |  |
| FH‐001 | Barge Clamshell to Conveyor D1 | Fugitive VE |
| FH‐002 | Barge Bucket Elevator to Conveyor A1 |  |
| FH‐003 | Conveyor A1 to Conveyor B1 |  |
| FH‐004 | Conveyor B1 to Conveyor D1 |  |
| FH‐005 | Self‐Unloading Barge to Conveyor D1 |  |
| Coal Conveying Operations |  |  |
| FH‐006 | Conveyor D1 to Conveyor E1 | --- |
| FH‐007 | Conveyor E1 to Conveyor Y or Conveyor F1 | --- |
| FH‐008a | Conveyor Y to Conveyor Z | --- |
| FH‐008b | Conveyor Z to West Emergency Pile | Fugitive VE |
| FH‐012 | Conveyor Z to Conveyor P | --- |
| FH‐013 | Conveyor P to Intermediate Conveyor | --- |
| FH‐014 | Intermediate Conveyor to North Stacker Conveyor (G2) |  |
| FH-015 | North Stacker Conveyor (G2) to North/Center Storage Pile | Fugitive VE |
| FH-017 | North Stacker Conveyor (G2) to Conveyor P | --- |
| FH‐022 | Conveyor F1 to South Stacker Conveyor (G1) | --- |
| FH‐023 | South Stacker Conveyor (G1) to South/Center Storage Pile | Fugitive VE |
| FH‐025 | South Reclaimer Conveyor (G1) to Conveyor F1 | --- |
| FH‐028 | Conveyor P to Conveyor J2 | Fugitive VE |
| FH‐029 | Conveyor J2 to Conveyor Q2 | --- |
| FH‐030 | Conveyor F1 to Conveyor J1 | --- |
| FH‐031 | Conveyor J1 to Conveyor Q1 | --- |
| FH‐052 | Conveyor U to East Emergency Storage Pile | Fugitive VE |
| FH‐055 | Conveyor W1 to Conveyor L1 | --- |
| FH‐056 | Conveyor W2 to Conveyor L2 | --- |
| FH‐059 - FH‐062 | Conveyors L1 & L2 to M1 & M2, and Conveyors M1 & M2 to Coal Bunkers (These enclosed conveyors are located inside an enclosed building and are not subject to emissions limits or testing requirements.) | --- |
| Coal Equipment & Storage |  |  |
| FH‐009 | Dozer Operations on West Emergency Storage Pile | Fugitive VE |
| FH‐010 | West Emergency Storage Pile |  |
| FH‐011a | Dozer Reclaim from West Emergency Pile to Portable Conveyor |  |
| FH‐011b | Portable Conveyor Feeds into Portable Hopper | --- |
| FH‐011c | Portable Hopper to Conveyor F | --- |
| FH‐016 | Mobile Reclaimer to North Stacker Conveyor (G2) |  |
| FH‐018 | Dozer Operations on North Storage Pile | Fugitive VE |
| FH‐019 | North Storage Pile |  |
| FH‐020 | Dozer Operations on Middle (Common) Storage Pile |  |
| FH‐021 | Fuel Storage ‐ Middle (Common) Storage Pile |  |
| FH‐024 | South Reclaimer to South Reclaimer Conveyor (G1) |  |
| FH‐026 | Dozer Operations on South Storage Pile |  |
| FH‐027 | South Storage Pile |  |
| FH‐036 - FH‐047 | Blending Bins to Conveyors T1, T2 | --- |
| FH‐050 | Crusher to Conveyor W1 | --- |
| FH‐051 | Crusher to Conveyor W2 | --- |
| FH‐053 | Dozer Operations on East Emergency Storage Pile | Fugitive VE |
| FH‐054 | East Emergency Storage Pile |  |
| FH‐057 | Dozer Reclaim from East Emergency Pile to "K" Feeders |  |
| FH‐058 | “K” Feeders to Conveyors L1 or L2 | --- |
| FH‐063 | Dozer Operations on Storage Pile | Fugitive VE |
| FH‐064 | Dozer Reclaim from Storage Pile to Loadout or Portable Conveyor |  |
| FH‐070 | Long Term Storage Pile |  |
| FH‐071 | Dozer Operations on Long Term Storage Pile |  |
| FH‐072 | Trucks, Full |  |
| FH‐073 | Trucks, Empty |  |

Essential Potential to Emit (PTE) Parameters

The handling capacity for the conveyors and equipment that comprise the solid fuel yard emissions points is not specifically limited; however, the design capacity for the majority of the handling equipment is 4,000 tons per hour.  The total annual solid fuel handling capacity is inherently limited by the amount of fuel that Boilers 1 – 4 can burn (5-6 million tons per year) plus the amount of solid fuel that can be transloaded for off-site shipment (1,428,030 tons per year, see E.U. ID No. -046).  In addition, permit No. 0570039-041-AC established an annual limit of 8 million tons per year of solid fuel that can be received by railcar (see E.U. ID No. -047).

- Methods of Operation – Materials Handling.  The materials that are allowed to be handled by these emissions units are coal, petroleum coke, slag and residual coal (generated at the TEC Polk Power Station).  [PA 79-12 and Permit No. 0570039-012-AC]

- Hours of Operation.  These emissions points may operate continuously (8,760 hours/year).  [Rule 62-210.200 (Definitions - Potential to Emit (PTE), F.A.C. and PA 79-12]

Control Technology

- PM Control Devices.  Particulate matter emissions shall be controlled by use of control devices.  
[PA 79-12.]

{Permitting Note:  This requirement is satisfied by complying with Specific Conditions H.4. – H.6.}

- Equipment Enclosure.  All conveyors and conveyor transfer points shall be enclosed to preclude particulate matter emissions excepting the coal handling stacker reclaimer, the tail end conveyor feeding the tripper and the barge unloading belt, which are exempted for feasibility considerations.  [PSD-FL-040]

- Water Sprays.  Water sprays for storage piles, handling equipment, etc., including the handling equipment exempted from the conveyor enclosure requirement (see Specific Condition H.4.), shall be applied during dry periods and as necessary to all unconfined emissions points to maintain opacity below 20%.  Water sprays and/or surfactants shall also be applied as necessary within the covered conveyors and drop points to maintain opacity below 5%.  [Rules 62-4.160(2), 62-213.440 and 62-296.320(4)(c), F.A.C.PSD-FL-040]

- Minimizing Wind Erosion - Coal Storage Piles.  Coal storage piles shall be shaped, compacted and oriented to minimize wind erosion.  [PSD-FL-040]

Emission Limitations and Standards

Unless otherwise specified, the averaging time for Specific Condition H.7. is based on the specified averaging time of the applicable test method.

- VE/Opacity Limits.  Pursuant to Chapter 1-3.52, Rules of the EPC, visible emissions shall not exceed 20% opacity for any unconfined emissions in the fuel yard.  Unconfined emissions, as defined in Rule 62-210.200, F.A.C., shall include the static fuel piles, etc.  Pursuant to Rule 62-296.711(2), F.A.C., visible emissions shall not exceed 5% opacity for the remaining confined emissions units in the fuel yard, as determined by opacity testing.  [Rules 62-296.320(4)(b)1., 62.296.711(2), F.A.C.; PA 79-12; and, Chapter 1-3.52, Rules of the EPC.]

{Permitting Note:  “Unconfined Emissions” are defined in Rule 62-210.200 as “Emissions which escape and become airborne from unenclosed operations or which are emitted into the atmosphere without being conducted through a stack.”  Based on this definition and the applicable requirements reflected in Specific Condition H.7., emissions from operations related to the open storage piles (i.e. movable conveyor drops to the storage piles, the open storage piles themselves, dozer operations on the storage piles, the movable coal handling stacker reclaimer, the tail end conveyor feeding the tripper and the barge unloading belt) are considered unconfined emissions subject only to the general 20% opacity standard and regular VE testing is not required.  The emission points that are enclosed (i.e. conveyors, conveyor transfer points and static conveyor drop points) are subject to Chapter 1-3.52, Rules of the EPC, and the PM RACT, standard of 5% opacity.  TEC is able to meet this limit by maintaining the required enclosures and by operating water sprays or applying surfactants as needed; therefore, additional add-on PM control devices are not needed.}

- Reasonable Precautions to Minimize Unconfined Particulate Matter - Fuel Pile Operations.  The fuel pile operations are subject to Rule 62-296.320(4)(c), F.A.C., Unconfined Emissions of Particulate Matter.  Reasonable precautions to minimize unconfined particulate matter shall be in accordance with Rule 62-296.320(4)(c), F.A.C.; and, may include, but shall not be limited to, the coating of roads and construction sites used by contractors and re-grassing or watering areas of disturbed fuel.  [Rule 62-296.320(4)(c) and PA 79-12.]

Excess Emissions

- Excess Emissions Allowed.  Excess emissions resulting from startup, shutdown or malfunction of any emissions unit shall be permitted providing (1) best operational practices to minimize emissions are adhered to and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C.]

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown, or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C.]

Test Methods and Procedures

- Test Methods.  Required tests shall be performed in accordance with the following reference method(s):

| Method(s) | Description of Method(s) and Comment(s) |
| --- | --- |
| EPA Method 9 | Visual Determination of the Opacity of Emissions |

The above methods are described in Chapter 62-297, F.A.C. and/or 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Chapter 62-297, F.A.C.]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- Annual Compliance Test.  During each federal fiscal year (October 1st to September 30th), VE tests shall be performed to demonstrate compliance with the opacity standards established for the emissions points within this emissions unit that are subject to the 5% opacity limit, as specified in Specific Condition H.7. and the associated permitting note.  [Rule 62-297.310(7), F.A.C., Chapter 1-3.52, Rules of the EPC and PA 79-12.]

- Compliance Test Prior To Renewal.  Prior to permit renewal, VE tests shall be performed to demonstrate compliance with the opacity standards established for the emissions points within this emissions unit that are subject to the 5% opacity limit, as specified in Specific Condition H.7. and the associated permitting note.  [Rule 62-297.310(7)(a)3., F.A.C. and Chapter 1-3.52, Rules of the EPC]

- Visible Emissions Test.  Compliance with the visible emission limits of this permit shall be demonstrated by an annual compliance test using EPA Method 9.  The duration of the annual tests shall be 30 minutes.  [Rule 62-297.310(4)(a)2., F.A.C.]

Recordkeeping and Reporting Requirements

- Daily Fuel Log.  The permittee shall maintain a daily log of the amounts and types of fuels used and copies of fuel analyses containing information on sulfur content, ash content and heating values.  [PA 79-12]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440, F.A.C.]

The specific conditions in this section apply to the following emissions units:

| E.U. ID No. | ## Brief Description |
| --- | --- |
| -032 | Surface Coating of Miscellaneous Metal Parts |

This emissions unit is for the surface coating of miscellaneous metal parts as defined in Rule 62-296.513, F.A.C.  These parts include such things as pumps, compressors, conveyor components, fans, blowers, transformers.

{Permitting note(s):  This emissions unit is regulated under Rule 62-296.500, F.A.C., Reasonably Available Control Technology (RACT) - Volatile Organic Compounds (VOC) and Nitrogen Oxides (NOx) Emitting Facilities; and, Rule 62-296.513, F.A.C., VOC RACT - Surface Coating of Miscellaneous Metal Parts and Products.}

Essential Potential to Emit (PTE) Parameters

- Hours of Operation.  At applicant request, miscellaneous metal parts surface coating operations are allowed to operate for a total of 3,500 hours/year.  [Rule 62-210.200 (Definitions - (PTE), F.A.C.]

- Capacity.  At applicant request, the total maximum coating usage shall not exceed 2 gallons per hour, on a 24-hr basis, and 7,000 gallons per year.  [Rule 62-210.200 (Definitions - (PTE), F.A.C.]

Emission Limitations and Standards

Unless otherwise specified, the averaging time for Specific Condition I.3. is based on the specified averaging time of the applicable test method.

- (This specific condition applies if this emissions unit emits more than 15 pounds of VOC in any one day and 3 pounds VOC in any one hour.)  VOC Emission Limits for Surface Coating of Miscellaneous Metal Parts.

a. 	No owner or operator of a coating line for miscellaneous metal parts and products shall cause, allow, or permit the discharge into the atmosphere of any volatile organic compounds in excess of:

(1)	4.3 pounds per gallon of coating (0.52 kilograms per liter), excluding water, delivered to a coating applicator that applies clear coatings;

(2)	3.5 pounds per gallon of coating (0.42 kilograms per liter), excluding water, delivered to a coating applicator in coating application system that is air dried or forced warm air dried at temperatures up to 194 degrees Fahrenheit (90 degrees Celsius);

(3)	3.5 pounds per gallon of coating (0.42 kilograms per liter), excluding water, delivered to a coating applicator that applies extreme performance coatings; or,

(4)	3.0 pounds per gallon of coating (0.36 kilograms per liter), excluding water, delivered to a coating applicator for all other coatings and coating application systems.

b.	If more than one emission limitation in specific condition I.3.(a) above applies to a specific coating, then the least stringent emission limitation shall be applied.

c. 	All volatile organic compound emissions from solvent washings shall be considered in the emission limitations in condition I.6.(a) above unless the solvent is directed into containers that prevent evaporation into the atmosphere.

[Rule 62-296.513(2), F.A.C.]

- (This specific condition applies if this emissions unit emits more than 15 pounds of VOC in any one day and 3 pounds VOC in any one hour.)  Control Technology.  The emission limits in specific condition I.3.(a) above shall be achieved by the application of low solvent coating technology.  [Rule 62-296.513(3), F.A.C.]

Excess Emissions

- Excess Emissions Allowed.  Excess emissions resulting from startup, shutdown or malfunction of any emissions unit shall be permitted providing (1) best operational practices to minimize emissions are adhered to and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C.]

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown, or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C.]

Test Methods and Procedures

- Test Methods.  Required tests shall be performed in accordance with the following reference method(s):

| Method(s) | Description of Method(s) and Comment(s) |
| --- | --- |
| EPA Method 24 | Determining VOC content |
| EPA Method 450/3-84-019 | Determining VOC content |

The above methods are described in Chapter 62-297, F.A.C. and/or 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Chapter 62-297, F.A.C.]

- Test Methods.  The VOC content shall be calculated using a percent solids basis (less water and exempt solvents) for adhesives, coating, and inks, using EPA Reference Method 24.  [Rule 62-296.500(2)(b)2., F.A.C.]

- (This specific condition applies if this emissions unit emits more than 15 pounds of VOC in any one day and 3 pounds VOC in any one hour.)  Test Methods and Procedures to Determine Low Solvent Technology.  The test method for volatile organic compounds shall be EPA Method 24 or EPA 450/3-84-019, incorporated and adopted by reference in Chapter 62-297, F.A.C.  Test procedures shall meet all applicable requirements of Chapter 62-297, F.A.C.  [Rules 62-296.513(4)(a) and (c), F.A.C.]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

Recordkeeping and Reporting Requirements

- Recordkeeping.  The permittee shall maintain daily records of operations for the most recent 5 year period.  The records shall be made available to the local, state, or federal air pollution agency upon request.  The records shall include, but not be limited to, the following:

a.	The rule number applicable to the operation for which the records are being maintained.

b. 	The application method and substrate type (metal, etc.).

c.	The amount and type of adhesive, coatings (including catalyst and reducer for multicomponent coatings), solvent, and/or graphic arts material used at each point of application, including exempt compounds.

d.	The VOC content as applied in each adhesive, coating, solvent, and/or graphic arts material.

e.	The date for each application of each adhesive, coating, solvent, and/or graphic arts material.

f. 	The amount of surface preparation, clean-up, wash-up of solvent (including exempt compounds) used and the VOC content of each.

[Rule 62-296.500(2)(b)1., F.A.C.]

- Reporting.  Annually, in accordance with a schedule and reporting format provided by the Department or EPCHC, The permittee shall provide EPCHC with proof of compliance with the limitations in this section.  [Rule 62-296.500(2)(c), F.A.C.]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440, F.A.C.]

The specific conditions in this section apply to the following emissions units:

| E.U. ID No. | ## Brief Description |
| --- | --- |
|  | Abrasive Blasting |
| -033 | Abrasive Blast Booth with Baghouse |
| -034 | Abrasive Blast Media Storage with Baghouse |

Reserved

These emissions units consist of abrasive blasting related activities.  The abrasive blast booth is used to prepare miscellaneous metal parts for surface coating.  Particulate matter emissions from the abrasive blast booth are controlled by a Torit Model No. DFT 4-16 pulse jet baghouse with an inlet flow rate of 7,500 acfm.  Particulate matter emissions from the abrasive blast media storage are controlled by a pulse jet baghouse with an inlet air flow rate of 800 acfm.

{Permitting note(s):  These emissions units are regulated under Rule 62-296.712, F.A.C., PM RACT -  Miscellaneous Manufacturing Process Operations.}

Essential Potential to Emit (PTE) Parameters

- Hours of Operation.  These emissions units may operate continuously (8,760 hours/year).  [Rule 62-210.200 (Definitions - (PTE), F.A.C.]

Operational Requirements

- Used and Waste Oils.  No used or waste oils shall be burned in the diesel compressors.  [Rule 62-070(3), F.A.C.]

Emission Limitations and Standards

Unless otherwise specified, the averaging times for Specific Conditions J.3. - J.4. are based on the specified averaging time of the applicable test method.

- Particulate Matter and Visible Emissions.  The particulate matter emissions from each baghouse shall not exceed 0.03 gr/dscf, or any visible emissions (VE) greater than 5% opacity.  However, the permittee may exceed these emission limits if a pollution control device for particulate matter is utilized that has an actual particulate matter collection efficiency of at least 98 percent.  The opacity standard for the emissions units shall be the average opacity level achieved during the initial compliance test which established compliance with the standard, plus 5% opacity.  [Rule 62-296.712(2), F.A.C.]

- Particulate Matter Emissions.  Particulate matter emissions from the abrasive blasting operations shall not exceed 15 tons for any 12 consecutive month period.  [Rule 62-212.400 (escape Prevention of Significant Deterioration (PSD), F.A.C.]

Excess Emissions

- Excess Emissions Allowed.  Excess emissions resulting from startup, shutdown or malfunction of any emissions unit shall be permitted providing (1) best operational practices to minimize emissions are adhered to and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C.]

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown, or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C.]

Test Methods and Procedures

- Test Methods.  Required tests shall be performed in accordance with the following reference method(s):

| Method(s) | Description of Method(s) and Comment(s) |
| --- | --- |
| EPA Methods 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| EPA Method 5 | Methods for Determining Particulate Matter Emissions |
| EPA Method 9 | Visual Determination of the Opacity of Emissions |

The above methods are described in Chapter 62-297, F.A.C. and/or 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Chapter 62-297, F.A.C.]

- Annual Compliance Test.  Except as specified in Specific Condition J.13., during each federal fiscal year (October 1st to September 30th), these emissions units shall be tested to demonstrate compliance with the emission limitations and standards for VE.  An annual PM test is not required provided the VE limit is met in accordance with Rule 62-296.712, F.A.C.  [Rules 62-297.310(7) & 62-296.712, F.A.C.]

- Compliance Test Prior To Renewal.  Prior to permit renewal, these emissions units shall be tested to demonstrate compliance with the emission limitations and standards for VE.  A renewal PM test is not required provided the VE limit is met in accordance with Rule 62-296.712, F.A.C. [Rules 62-297.310(7)(a)3. & 62-296.712, F.A.C.]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- Test Methods and Procedures.

a.	The test method for visible emissions shall be EPA Method 9, incorporated and adopted by reference by reference in Chapter 62-297, F.A.C.

b.	The test method for particulate matter emissions shall be EPA Method 5, incorporated and adopted by reference in Chapter 62-297, F.A.C. The minimum sample volume shall be 30 dry standard cubic feet.

c.	A visible emissions test indicating no visible emissions (5% (percent) opacity) may be submitted in lieu of a particular matter stack test for materials handling emissions subject to this rule, where the emissions unit is equipped with a baghouse.

d.	Test procedures shall meet all applicable requirements of Chapter 62-297, F.A.C.

[Rule 62-296.712(3), F.A.C.]

- VE Test Observation Point.  The observation point for the blasting operation tests shall be at the point of maximum opacity leaving the enclosure.  [Rule 62-070(3), F.A.C.]

- VE Testing Not Required.  By this permit, annual emissions compliance testing for VE is not required for these emissions units when operating for less than 400 hours per year.  See Specific Condition TR7.  [Rule 62-297.310(7)(a)4., F.A.C.]

Recordkeeping and Reporting Requirements

- Monthly Records.  The permittee shall maintain monthly records on the type and amount of abrasive blasting material used.  A rolling 12-month total shall be kept as well.  [Rule 62-070(3), F.A.C.]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440, F.A.C.]

The specific conditions in this section apply to the following emissions unit:

| EU ID No. | ## Brief Description |
| --- | --- |
| -035 | Surface Coating of Ships |

Reserved

This emissions unit is for the surface coating maintenance of ships.

{Permitting note(s):  This emissions unit is regulated under 40 CFR 63, Subpart II, National Emission Standards for Hazardous Air Pollutants (NESHAP) from Shipbuilding and Ship Repair (Surface Coating) adopted in Rule 62-204.800(11)(b), F.A.C.; and, Rule 62-296.500, F.A.C., Reasonably Available Control Technology (RACT) - Volatile Organic Compounds (VOC) and Nitrogen Oxides (NOX) Emitting Facilities.  There is no specific VOC RACT category for this type of emissions unit within Rule 62-296.500, F.A.C.}

# The following requirements apply to the emissions unit listed above:

Essential Potential to Emit (PTE) Parameters

- Hours of Operation.  This emissions unit may operate continuously (8,760 hours/year).  [Rule 62-210.200 (Definitions - Potential to Emit (PTE)), F.A.C.]

Test Methods and Procedures

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

Recordkeeping and Reporting Requirements

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440, F.A.C.]

NESHAP 40 CFR 63 Requirements

- NESHAP 40 CFR 63 Requirements - Subpart A.  This emissions unit shall comply with all applicable requirements of 40 CFR 63, Subpart A, General Provisions, which have been adopted by reference in Rule 62-204.800(11)(d)1., F.A.C., except that the Secretary is not the Administrator for purposes of 40 CFR 63.5(e), 40 CFR 63.5(f), 40 CFR 63.6(g), 40 CFR 63.6(h)(9), 40 CFR 63.6(j), 40 CFR 63.13, and 40 CFR 63.14.  This emissions unit shall comply with Appendix 40 CFR 63 Subpart A included with this permit.  [Rule 62-204.800(11)(d)1., F.A.C.]

- NESHAP 40 CFR 63 Requirements - Subpart II.  This emissions unit shall comply with all applicable requirements of 40 CFR 63, Subpart II, National Emission Standards for Hazardous Air Pollutants from Shipbuilding and Ship Repair (Surface Coating), which have been adopted by reference in Rule 62-204.800(11)(b), F.A.C., except that the Secretary is not the Administrator for purposes of 40 CFR 63.789(c)(1) through (4).  This emissions unit shall comply with Appendix 40 CFR 63 Subpart II included with this permit.  [Rule 62-204.800(11)(b), F.A.C.]

The specific conditions in this section apply to the following emissions units:

| E.U. ID No. | ## Brief Description |
| --- | --- |
| -022 | Lime Silo for Wastewater Treatment Plant with one Baghouse |

This emissions unit is comprised of a lime silo with one baghouse (Griffin Environmental 36-LS Filter Vent) which supplies limestone to the wastewater treatment plant for the FGD chloride bleed stream.  This plant will serve the FGD systems.  Particulate matter emissions from displaced air from periodically filling the lime silo will be controlled with the related baghouse.

{Permitting note(s):  This emissions unit is regulated under Chapter 1-3.52, Rules of the EPC, Rules of the Environmental Protection Commission (EPC) of Hillsborough County.  This emissions unit is exempt from the requirements of Rule 62-296.711, F.A.C., Reasonably Available Control Technology (RACT) - Materials Handling, Sizing, Screening, Crushing and Grinding Operations, pursuant to Rule 62-296.700(2)(c), F.A.C., because it has an allowable emission rate of less than one ton per year.}

Essential Potential to Emit (PTE) Parameters

- Hours of Operation.  This emissions unit may operate continuously (8,760 hours/year).  [Rule 62-210.200 (Definitions - (PTE), F.A.C.]

Operational Requirements

- Operating Procedures.  The baghouse for this emissions unit shall be properly operated and maintained at all times in a condition to minimize particulate matter emissions.  All operators of air pollution control equipment shall be properly trained in plant equipmentThe owner and operator shall ensure that all facility staff responsible for these emissions units are trained in their operation and maintenance in accordance with the guidelines and procedures as established by the equipment manufacturers.  [Rule 62-213.44062-4.070(3), F.A.C.]

Emission Limitations and Standards

Unless otherwise specified, the averaging time for Specific Condition L.3. is based on the specified averaging time of the applicable test method.

- Particulate Matter (PM) and Visible Emissions.  No owner or operator shall cause or allow PM and visible emissions (VE) from the baghouse controlling this emissions unit in excess of 0.03 gr/dscf and 5% opacity.  [Rules 62-4.070(3) and 62-296.700(2)(c), F.A.C., Chapter 1-3.52, Rules of the EPC; and, Applicant Request.]

{Permitting note(s):  The particulate matter limitation will ensure that allowable emissions are less than one ton per year for this emissions unit.}

Excess Emissions

- Excess Emissions Allowed.  Excess emissions resulting from startup, shutdown or malfunction of any emissions unit shall be permitted providing (1) best operational practices to minimize emissions are adhered to and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C.]

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown, or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C.]

Test Methods and Procedures

- Test Methods.  Required tests shall be performed in accordance with the following reference method(s):

| Method(s) | Description of Method(s) and Comment(s) |
| --- | --- |
| EPA Methods 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| EPA Method 5 | Methods for Determining Particulate Matter Emissions |
| EPA Method 9 | Visual Determination of the Opacity of Emissions |

The above methods are described in Chapter 62-297, F.A.C. and/or 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Chapter 62-297, F.A.C.]

- Annual Compliance Test.  Except as specified in Specific Condition L.10., during each federal fiscal year (October 1st to September 30th), this emissions unit shall be tested to demonstrate compliance with the emission limitations and standards for visible emissions (VE).  The annual compliance tests will be used in lieu of the compliance test prior to renewal.   [Rule 62-297.310(7), F.A.C.]

- Compliance Test Prior To Renewal.  Prior to permit renewal, this emissions unit shall be tested to demonstrate compliance with the emission limitations and standards for visible emissions (VE).  [Rule 62-297.310(7)(a)3., F.A.C.]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- Visible Emissions Test in Lieu of PM Stack Test.  The owner or operator is permitted to comply with the VE limit and the VE testing requirement in lieu of regularly demonstrating compliance with the PM limitation.  If the Department has reason to believe that the particulate matter limitation is not being met, it shall require compliance be demonstrated by conducting a particulate matter test in accordance with EPA Method 5 specified at 40 CFR 60 Appendix A.  [Rules 62-4.070(3) and 62-296.711(3)(c), F.A.C.]

- Visible Emissions Test.  Compliance with the visible emission limits of this permit shall be demonstrated by an annual compliance test using EPA Method 9.  The duration of the annual test shall be 30 minutes.  [Rules 62-4.070(3) and 62-297.310(4)(a)2., F.A.C.]

Recordkeeping and Reporting Requirements

#### Records of Maintenance.  The owner or operator shall make and maintain records of maintenance on the baghouse sufficient to demonstrate compliance with the operating procedures requirements of Specific Condition L.2.  [Rule 62-213.44062-4.070(3), F.A.C.]

#### Records.  Tampa Electric shall keep records of facility staff training, and shall maintain, on site, an Operations and Maintenance Plan for the baghouse that details how it shall be properly operated and maintained at all times.  Tampa Electric shall also take quarterly pressure readings from the baghouse pressure-sensing device.  [Rule 62-213.440(1)(b)1.b. (Periodic Monitoring), F.A.C.]

#### Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440, F.A.C.]

The specific conditions in this section apply to the following emissions units:

| E.U. ID No. | ## Brief Description |
| --- | --- |
|  | Coal Residual Storage and Transfer from the Polk Power Station |
| -037 | Coal Residual Storage Facility |
| -038 | Coal Residual Transfer System |

These emissions units consist of the storage and handling of coal residual received from the Polk Power Station.  A nominal 25-ton dump truck empties a load of material into the building, and a bulldozer either pushes the material into a vacant area of the building, or it pushes the material directly into the dozer trap in the rear of the building.  The dozer trap is a hopper that is partially below grade, and is used to feed the conveyor, which is capable of transferring up to 200 tons of material per hour.  The conveyor is fully enclosed to prevent fugitive dust emissions, and to also prevent wetting of the material.  Material inside the building shall be sprayed with water as necessary to minimize dust within the building.

{Permitting note(s):  These emissions units are regulated under Rule 62-210.300, F.A.C., Permits Required; Permit No. 0570039-012-AC; and, Rule 1-3.52, Rules of the Environmental Protection Commission (EPC) of Hillsborough County; and Rule 62-296.711, F.A.C., Reasonably Available Control Technology (RACT) Particulate Matter (PM) - Materials Handling, Sizing, Screening, Crushing and Grinding Operations.}

Essential Potential to Emit (PTE) Parameters

- Hours of Operation.  These emissions units may operate continuously (8,760 hours/year).  [Rule 62-210.200 (Definitions - (PTE), F.A.C.]

- Capacity.  The maximum conveyor transfer rate shall be 200 tons per hour and 255,500 tons per year of coal residual that has been generated at the Polk Power Station gasification process.  [Permit No. 0570039-012-AC.]

Operational Requirements

- Enclosure of Equipment.  All conveyors and conveyor transfer points shall be enclosed to minimize particulate matter emissions.  The coal residual shall be stored in an enclosed facility.  Open storage of coal residual is prohibited.  [Rule 62-296.320(4)(c), F.A.C., and Permit No. 0570039-012-AC.]

Emission Limitations and Standards

Unless otherwise specified, the averaging times for Specific Condition M.4. is based on the specified averaging time of the applicable test method.

- Visible Emissions.  Visible emissions shall not exceed 5% opacity in lieu of particulate matter sampling.  [Rule 62-296.711(3)(c), F.A.C., Permit No. 0570039-012-AC; and, Chapter 1-3.52, Rules of the EPC.]

Excess Emissions

- Excess Emissions Allowed.  Excess emissions resulting from startup, shutdown or malfunction of any emissions unit shall be permitted providing (1) best operational practices to minimize emissions are adhered to and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C.]

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown, or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C.]

Test Methods and Procedures

- Test Methods.  Required tests shall be performed in accordance with the following reference method(s):

| Method(s) | Description of Method(s) and Comment(s) |
| --- | --- |
| EPA Method 9 | Visual Determination of the Opacity of Emissions |

The above methods are described in Chapter 62-297, F.A.C. and/or 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Chapter 62-297, F.A.C.]

- Annual Compliance Test.  Unless otherwise specified by this permit, during each federal fiscal year (October 1st to September 30th), these emissions units shall be tested to demonstrate compliance with the emission limitations and standards for VE.  The annual compliance tests will be used in lieu of the compliance test prior to renewal.  [Rule 62-297.310(7), F.A.C.]

- Compliance Test Prior To Renewal.  Prior to permit renewal, these emissions units shall be tested to demonstrate compliance with the emission limitations and standards for VE.  [Rule 62-297.310(7)(a)3., F.A.C.]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- VE Testing Sites.  Sites to be tested shall be determined by EPCHC.  [Permit No. 0570039-012-AC.]

Recordkeeping and Reporting Requirements

- Records.  The permittee shall keep records of the following parameters for each specific month/day/year:

a.	Amount of raw coal residual charged (tpd); and,

b.	Amount of refined/beneficiated coal residual charged (tpd).

[Permit No. 0570039-012-AC.]

- Records.  The permittee shall also keep records of:

a.	Annual amount of raw coal residual charged (tpy);

b.	Annual amount of refined/beneficiated coal residual charged (tpy); and,

c.	Annual VE tests.

[Permit No. 0570039-012-AC.]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440, F.A.C.]

The specific conditions in this section apply to the following emissions unit:

| E.U. ID No. | ## Brief Description |
| --- | --- |
|  | Diesel Generators (Engines) |
| -043 | SCCT Black Start Diesel Engine, 1,000 ekW |
| -044 | Coal Field Diesel Generator |

This section is comprised of two diesel compression ignition type engines.  The 1,000 ekW, SCCT black start (diesel engine) is only used to start SCCT Units 4A and 4B, Emission Unit ID Nos. -041 and -042.  Air pollutant emissions from both engines are uncontrolled.

| Identification | In-service date | Manufacturer name | Horsepower (HP) | Applicable Requirement(s) for Compression Ignition Type Engines |
| --- | --- | --- | --- | --- |
| SCCT Black Start Diesel Engine, 1,000 ekW | 08/2009 | Kohler | 1,495 | 40 CFR 63, Subparts A and ZZZZ and 40 CFR 60, Subparts A and IIII This generator is a “new unit.” |
| Coal Field Diesel Generator | 1999 | Caterpillar | 349 | 40 CFR 63, Subparts A and ZZZZ and 40 CFR 60, Subparts A and IIII Manufacture date 1999; purchased 10/2009. This generator is an “existing unit”. |

{Permitting note(s):  These emissions units are regulated under 40 CFR 63, Subpart ZZZZ, National Emission Standards for Hazardous Air Pollutants (NESHAP) for Stationary Reciprocating Internal Combustion Engines (RICE) also referred to as the “RICE Maximum Achievable Control Technology (MACT)” adopted in Rule 62-204.800(11)(b), F.A.C.

The Diesel Emergency Black Start Generator is classified as an emergency generator according to 40 CFR 63.6675:

“Emergency stationary RICE means any stationary RICE that operates in an emergency situation.  Examples include stationary RICE used to produce power for critical networks or equipment (including power supplied to portions of a facility) when electric power from the local utility is interrupted, or stationary RICE used to pump water in the case of fire or flood, etc.  Emergency stationary RICE may be operated for the purpose of maintenance checks and readiness testing, provided that the tests are recommended by the manufacturer, the vendor, or the insurance company associated with the engine.  Required testing of such units should be minimized, but there is no time limit on the use of emergency stationary RICE in emergency situations and for routine testing and maintenance.  Emergency stationary RICE may also operate an additional 50 hours per year in non-emergency situations.”}

# The following requirements apply to the emissions unit listed above:

Essential Potential to Emit (PTE) Parameters

- Hours of Operation.  The SCCT Black Start Diesel Engine is allowed to operate for no more than 500 hours per year in accordance with Rule 62-210.200, F.A.C.  [Rule 62-210.200 (Definitions - Emergency Generator, F.A.C.; and, Permit No. 0570039-040-AC.]

- Hours of Operation.  The SCCT Black Start Diesel Engine excluding emergency conditions is allowed to operate for no more than 100 hours per year (approximately two hours per week) for routine testing and maintenance purposes.  [Permit No. 0570039-040-AC.]

- Sulfur Content.  The SCCT Black Start Diesel Engine shall be fired with ultra low sulfur diesel fuel (ULSD).  The ULSD shall contain a maximum sulfur content of 0.0015 percent (%), by weight.  [Permit No. 0570039-040-AC.]

Reporting Requirements

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440, F.A.C.]

NESHAP 40 CFR 63 Requirements

- NESHAP 40 CFR 63 Requirements - Subpart A.  These emissions units shall comply with all applicable requirements of 40 CFR 63, Subpart A, General Provisions, which have been adopted by reference in Rule 62-204.800(11)(d)1., F.A.C., except that the Secretary is not the Administrator for purposes of 40 CFR 63.5(e), 40 CFR 63.5(f), 40 CFR 63.6(g), 40 CFR 63.6(h)(9), 40 CFR 63.6(j), 40 CFR 63.13, and 40 CFR 63.14.  These emissions units shall comply with Appendix 40 CFR 63 Subpart A included with this permit.  [Rule 62-204.800(11)(d)1., F.A.C.]

- “RICE MACT” 40 CFR 63 Requirements - Subpart ZZZZ.  These emissions units shall comply with all applicable requirements of 40 CFR 63, Subpart ZZZZ, National Emission Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines (RICE), which have been adopted by reference in Rule 62-204.800(11)(b), F.A.C.  These emissions units shall comply with Appendix 40 CFR 63 Subpart ZZZZ included with this permit.  [Rule 62-204.800(11)(b), F.A.C.]

NESHAP 40 CFR 63 Reporting and Recordkeeping Requirements

- Notification Requirements.  In accordance with 40 CFR 63.6590(b) each engine is subject to the notification requirements of this Subpart.  New stationary RICE (the diesel emergency black start generator) that operate exclusively as emergency units are subject only to initial notification requirements.  [Rule 62-204.800(11), F.A.C.; and, 40 CFR 63.6590(b)]

- Recordkeeping Requirement for Applicability Determinations.  In accordance with 40 CFR 63.10 (b)(3) the owner or operator must keep a record of each applicability determination on site at the source for a period of five (5) years after the determination, or until the source changes its operations to become an affected source subject to the relevant standards, whichever comes first.  [Rule 62-204.800(11), F.A.C.; and, 40 CFR 63.10(b)(3)]

NSPS 40 CFR 60 Requirements

- NSPS Requirements - Subpart A.  The SCCT Black Start Diesel Engine shall comply with all applicable requirements of 40 CFR 60, Subpart A, General Provisions, including:

40 CFR 60.7, Notification and Recordkeeping

40 CFR 60.8, Performance Tests

40 CFR 60.11, Compliance with Standards and Maintenance Requirements

40 CFR 60.12, Circumvention

40 CFR 60.13, Monitoring Requirements

40 CFR 60.19, General Notification and Reporting Requirements,

which have been adopted by reference in Rule 62-204.800(8)(d), F.A.C., except that the Secretary is not the Administrator for purposes of 40 CFR 60.4, 40 CFR 60.8(b)(2) and (3), 40 CFR 60.11(e)(7) and (8), 40 CFR 60.13(g), (i) and (j)(2), and 40 CFR 60.16.  This emissions unit shall comply with Appendix 40 CFR 60 Subpart A included with this permit.  [Rule 62-204.800(8)(d), F.A.C.]

- NSPS “4-I” or “CI-ICE” 40 CFR 60, Subpart IIII.  Pursuant to 40 CFR 63.6590(c), the permittee has elected to comply with the RICE MACT for the SCCT Black Start Diesel Engine by meeting the requirements of the NSPS 40 CFR 60, Subpart IIII, attached as Appendix 40 CFR 60 Subpart IIII, to this permit.  Pursuant to 40 CFR 63.6590(c), no further requirements apply to the engine under 40 CFR 63 Subpart ZZZZ.  [Rules 62-204.800(11) & (8), F.A.C.]

- NESHAP 40 CFR 63, Subpart ZZZZ.  The Coal Field Diesel Generator shall comply with the applicable requirements of the NESHAP 40 CFR 63, Subpart ZZZZ, attached as Appendix 40 CFR 63, Subpart ZZZZ, to this permit.  [Rule 62-204.800(11), F.A.C.]

The specific conditions in this section apply to the following emissions unit(s):

| E.U. ID No. | Brief Description |
| --- | --- |
| -041 | SCCT 4A with a common electric generator that it shares with SCCT 4B |
| -042 | SCCT 4B with a common electric generator that it shares with SCCT 4A |

These emissions units consist of one PWPS FT8-3® SwiftPac® Aeroderivative simple cycle combustion turbine (SCCT)-generator peaking unit.  SCCT 4A and SCCT 4B are coupled to one common generator having a nominal gross generation capacity of 62 MW.  Each SCCT is equipped with water injection to minimize NOX emissions and an oxidation catalyst to minimize CO and VOC emissions.  Each SCCT may only be operated in the simple cycle mode.  Each SCCT is allowed to fire pipeline-quality natural gas (NG) containing no more than 2.0 grains of total sulfur per one hundred standard cubic feet (gr S/100 scf) and ultra low sulfur diesel fuel (ULSD) containing  a maximum sulfur content of 0.0015 percent by weight.

{Permitting Notes:  Nitrogen Oxides (NOX) emissions from units -041 and -042 are controlled by steam or water injection.  Carbon monoxide emissions are controlled by an oxidation catalyst system.  Units -041 and -042 began commercial operation on August 15, 2009.  The generator nameplate rating for units -041 and -042 is 31 MW each, 62 MW total.  Each unit has a separate, but identical, stack with the following parameters:  Stack height = 60 feet; exit diameter = 9.5 feet; exit temperature = 893º F; and, actual volumetric flow rate = 430,737 actual cubic feet per minute (acfm).  In addition to the requirements listed below, these emissions units are also subject to the standards and requirements contained in the Acid Rain Part of this permit (see Section IV).}

Essential Potential to Emit (PTE) Parameters

- Permitted Capacity.  The maximum allowable heat input rate is as follows:

| Unit No. | MMBtu/hr Heat Input | Fuel Type |
| --- | --- | --- |
| -041, -042 -041, -042 | 342.7 302.7 | Natural Gas (NG) Ultra Low Sulfur Diesel |

Heat input rates are based on 100% load with evaporative cooling, 59o F ambient temperature, 52o F compressor inlet air temperature, and the higher heating value (HHV) of the fuel.  Heat input rates will vary depending upon turbine characteristics, ambient conditions and evaporative cooling.  The permittee shall have provided manufacturer’s performance curves (or equations) that correct for site conditions to the Permitting and Compliance Authorities within 45 days of completing the initial compliance testing.  The manufacturer’s curves shall be reestablished and resubmitted to DEP within 45 days following the replacement of any combustion turbine components or major turbine tuning session that could reasonably affect the performance of the turbine.  Operating data may be adjusted for the appropriate site conditions in accordance with the performance curves and/or equations on file with the Department.  [Rules 62-4.160(2), 62-204.800, 62-210.200(PTE), 62-213.440, F.A.C.; and, Permit No. 0570039-040-AC, Specific Condition 7.]

- Emissions Unit Operating Rate Limitation After Testing.  See the related testing provisions in Appendix TR, Facility-wide Testing Requirements.  [Rule 62-297.310(2), F.A.C.]

- Methods of Operation.

a.	Fuels.  The fuels that are allowed to be burned in these units are:

(1)	NG, Primary Fuel.  The NG shall contain no more than 2.0 grains of sulfur per 100 standard cubic feet (2.0 gr S/100 scf).

(2)	ULSD.  The ULSD shall contain a maximum sulfur content of 0.0015%, by weight.

b.	Simple Cycle Mode.  Each SCCT shall operate only in the simple cycle mode not to exceed the permitted hours of operation allowed by this permit (See Specific Condition O.4.).  This restriction is based on the permittee’s request, which formed the basis of the PSD applicability and emission standards specified in this permit.  For any request to convert these units to combined cycle operation by installing/connecting to heat recovery steam generators, including changes to the fuel or quantity related to combined cycle conversion that may cause an increase in short or long-term emissions, the permittee shall submit a full PSD permit application complete with a proposed best available control technology (BACT) determination as if the SCCT peaking units had never been built.

c.	Simulated Facility Black Start Testing.  Subject to the CEMS data exclusions specified in Specific Condition O.15.e., below, TEC may operate simple cycle combustion turbines 4A and 4B at low loads for extended periods of time in order to simulate the conditions experienced following a facility-wide shutdown.  These simulated periods may be used to develop facility black start protocols and to perform periodic operator training exercises.  [Rule 62-213.410, F.A.C.; and Permit Nos. 0570039-040-AC, Specific Conditions 3, 8 & 9 and 0570039-053-AC, Specific Condition 9.]

- Hours of Operation.  SCCT 4A and SCCT 4B are allowed to operate in the peaking service mode for no more than 3,500 hr/calendar year each, including no more than 500 hr/calendar year each on ULSD.  Any hour used to fire ULSD will decrease an hour that could have been used to fire NG.  [Rule 62-210.200(PTE), F.A.C. and Permit No. 0570039-040-AC, Specific Condition 6.]

Control Technology

- Wet Injection.  The permittee shall adjust, operate, and maintain a water injection system to reduce NOX emissions from each SCCT.  The water injection system shall be maintained and adjusted in accordance with the manufacturer’s recommendations or determined best practices to minimize emissions.  [Rule 62-4.070(3), F.A.C. and Permit No. 0570039-040-AC, Specific Condition 4.]

- Oxidation Catalyst.  The permittee shall operate and maintain an oxidation catalyst system to reduce CO and VOC emissions from each SCCT.  The system shall be maintained and operated in accordance with the manufacturer’s recommendations or determined best practices to minimize emissions.  [Rule 62-4.070(3), F.A.C. and Permit No. 0570039-040-AC, Specific Condition 5.]

Emission Limitations and Standards

{Permitting Note:  The attached Table 1, Summary of Air Pollutant Standards, summarizes information for convenience purposes only.  This table does not supersede any of the terms or conditions of this permit.}

Unless otherwise specified, the averaging times for Specific Conditions O.7. - O.11. are based on the specified averaging time of the applicable test method.

The mass emission rate standards are based on a turbine inlet temperature condition of 59 °F, evaporative cooling on, and using the higher heating value (HHV) of the fuel.  Mass emissions rates may be adjusted to actual test conditions in accordance with the performance curves and/or equations on file with the Department.  The emissions limits listed in Specific Conditions O.7. - O.11. are for each SCCT, not combined.

- Visible Emissions.  Visible emissions from each unit shall not exceed 10 percent opacity, as determined by annual testing.  [Permit No. 0570039-040-AC, Specific Condition 10.]

- Nitrogen Oxide (NOX).  NOX emissions from each unit shall not exceed the following:

  - When Firing Natural Gas.

(1)	25 ppmvd @ 15% oxygen (O2) (NSPS) or,

(2)	32.0 lb/hr/SCCT (SIP).{Permitting Note:  For informational purposes, the NOX limit equates to 32 lb/hour/CT.}

  - When Firing Ultra Low Sulfur Diesel.

(1)	42.0 ppmvd @ 15 O2 (SIP) or,

(12)74 ppmvd @ 15 O2 (NSPS) or,

(3)	51.3 lb/hr/SSCT (SIP).

  - When operating at less than 75% of peak load.

- 96 ppmvd @ 15@ oxygen (NSPS)

  - c.  When Firing Both NG and ULSD.  Compliance with the NSPS limit is ensured by complying with either the NSPS limit, for NG, or the SIP limit, for ULSD, depending on the contribution of the fuels of the total heat input:  if the total heat input contribution is equal to or greater than 50 percent from NG, you must meet the corresponding limit for a NG-fired turbine when you are burning that fuel; similarly, when your total heat input contribution is greater than 50 percent from ULSD, you must meet the corresponding limit for ULSD for the duration of the time that you burn that particular fuel.

  - d.  Demonstration of Compliance.  Continuous compliance shall be demonstrated with the concentration-based (ppmvd) NOX emissions limits (4-hour rolling average) for each fuel type by data collected from the required continuous emissions monitoring system (CEMS).  Compliance with the mass-based (lb/hour) NOX emissions limits (3-run average) shall be demonstrated by data collected during the required annual Relative Accuracy Test Audit (RATA).  When firing ULSD, compliance with the SIP limit ensures compliance with the NSPS limit of 74 ppmvd @ 15% O2.

[40 CFR 60, Subpart KKKK and Permit No. 0570039-04066-AC, Specific Condition 10.]

- Carbon Monoxide (CO).  CO emissions from each unit shall not exceed the following:

  - When Firing Natural Gas.

(1)	21.0 ppmvd @ 15% O2 (SIP) or,

(2)	9.1 lb/hr/SCCT (SIP).{Permitting Note:  For informational purposes, the CO limit equates to 9.1 lb/hour/CT.}

  - When Firing Ultra Low Sulfur Diesel.

(1)	5.1 ppmvd @ 15% O2 (SIP) or,

(2)	2.1 lb/hr/SCCT (SIP).{Permitting Note:  For informational purposes, the CO limit equates to 2.1 lb/hour/CT.}

  - Demonstration of Compliance.  Continuous compliance shall be demonstrated with the concentration-based (ppmvd) CO emissions limits (3-hour rolling average) for each fuel type by data collected from the required continuous emissions monitoring system (CEMS).  Compliance with the mass-based (lb/hour) CO emissions limits (3-run average) shall be demonstrated by data collected during the required annual Relative Accuracy Test Audit (RATA).

[Permit No. 0570039-04066-AC, Specific Condition 10.]

{Permitting Note:  CO is used as a surrogate for VOC emissions as a demonstration of good combustion.}

- Particulate Matter (PM).  PM emissions are minimized by complying with the fuel sulfur specifications, combined with the efficient combustion design and operation of the turbines (good combustion).  [Permit No. 0570039-040-AC, Specific Condition 10.]

{Permitting Note:  Compliance with the fuel specifications, CO standards, and visible emissions standards shall serve as indicators of good combustion.  No PM emissions limits or compliance demonstrations are imposed.  Maximum expected PM/PM10 emissions from each turbine are approximately 2.5 and 7.5 lb/hr for NG and ULSD, respectively.}

- Sulfur Dioxide (SO2).  SO2 emissions from each unit shall not exceed the following:

  - When Firing Natural Gas.

(1)	2.0 grains (gr) of Sulfur (S)/100 standard cubic feet (scf) of natural gas (SIP) or,

(2)	0.90 lb/megawatt hour (MWh)/SCCT gross output (NSPS) or,

(3)	0.060 lb/MMBtu/SCCT heat input (NSPS).

  - When Firing Ultra Low Sulfur Diesel.

(1)	0.0015% S content, by weight (SIP) or,

(2)	0.90 lb/MWh/SCCT gross output (NSPS) or,

(3)	0.060 lb/MMBtu/SCCT heat input (NSPS).

  - Demonstration of Compliance.  The fuel sulfur specifications effectively limit the potential emissions of SO2 (and essentially sulfuric acid mist).  For compliance purposes, the permittee elected to demonstrate that the fuel combusted will not exceed the potential sulfur emissions of 0.060 lb SO2/MMBtu heat input (see Appendix 40 CFR 60, Subpart KKKK of the permit).

[40 CFR 60, Subpart KKKK and Permit No. 0570039-040-AC, Specific Conditions 8 & 10.]

Excess Emissions

Rule 62-210.700 (Excess Emissions), F.A.C. cannot vary any requirement of an NSPS, NESHAP or Acid Rain program provision.

- Definitions.  Rule 62-210.200(Definitions), F.A.C., defines the following terms:

- Startup is defined as the commencement of operation of any emissions unit which has shut down or ceased operation for a period of time sufficient to cause temperature, pressure, chemical or pollution control device imbalances, which result in excess emissions.

- Shutdown is the cessation of the operation of an emissions unit for any purpose.

- Malfunction is defined as any unavoidable mechanical and/or electrical failure of air pollution control equipment or process equipment or of a process resulting in operation in an abnormal or unusual manner.

[Permit No. 0570039-040-AC, Specific Condition 21.]

- Excess Emissions Allowed.  Excess emissions resulting from startup, shutdown or malfunction of any emissions unit shall be permitted providing (1) best operational practices to minimize emissions are adhered to and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C. and Permit No. 0570039-040-AC, Specific Condition 22.]

- Excess Emissions Prohibited.  Excess emissions caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure that may reasonably be prevented during startup, shutdown or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C. and Permit No. 0570039-040-AC, Specific Condition 23.]

- Allowable SIP CO and NOX Data Exclusions.  Provided that best operational practices to minimize emissions are adhered to and the duration of excess emissions are minimized, CO and NOX CEMS data collected during periods of startup, shutdown and malfunction may be excluded from the 3-hr rolling average and 4-hr rolling average, respectively, for compliance demonstrations only in accordance with the following requirements.  All periods of data excluded shall be consecutive for each such episode and only data obtained during the described episodes (startup, shutdown, malfunction, tuning and facility black start testing) may be excluded.  As provided by the authority in Rule 62-210.700(5), F.A.C., the following conditions replace the provisions in Rule 62-210.700(1), F.A.C.

  - Startup.  In accordance with the procedures described in the CEMS Data Requirements of this section, no more than the first 15 minutes of CEMS data indicating exceedences of emission limits shall be excluded for each gas turbine startup.  For startups of less than 15 minutes in duration, only those minutes of exceedences attributable to startup shall be excluded.  The total duration of a startup event is not limited.

  - Shutdown.  In accordance with the procedures described in the CEMS Data Requirements of this section, no more than the first 15 minutes of CEMS data indicating exceedences of emission limits shall be excluded for each gas turbine shutdown.  For shutdowns less than 15 minutes in duration, only those minutes of exceedences attributable to shutdown shall be excluded.  The total duration of a shutdown event is not limited.

  - Malfunction.  In accordance with the procedures described in the CEMS Data Requirements of this section, no more than 120 minutes of CEMS data shall be excluded in a 24-hour period for each gas turbine due to malfunctions.  Within one (1) working day of occurrence, the owner or operator shall notify the Compliance Authority of any malfunction resulting in the exclusion of CEMS data.

  - Tuning.  “Tuning” means adjusting the combustors in accordance with the manufacturer’s recommendations (or industry standards) or modifying the water-to-fuel ratio to affect a change in the post-combustion air emissions.  Such tuning sessions are infrequent.  Excess CEMS emissions data collected during tuning may be excluded from the compliance averages.

  - Simulated Facility Black Start Testing and Facility Black Start Events.  Up to 8 hours of CEMS data indicating exceedences of emission limits may be excluded from the compliance demonstration periods for the two simple cycle gas turbines when operating at less than full load for extended periods in relation to simulated or actual facility black start conditions.

The permittee shall notify the Compliance Authority within one working day of discovering any emissions in excess of a CEMS standard subject to the specified averaging period.  All such reasonably preventable emissions shall be included in any CEMS compliance determinations.  All valid emissions data (including data collected during startup, shutdown malfunction and tuning) shall be used to report annual emissions for the Annual Operating Report.  [Rules 62-210.370(3), 62-210.700(5) and 62-213.440, F.A.C.; and, Permit Nos. 0570039-040-AC, Specific Condition 24 & 0570039-053-AC, Specific Condition 10.]

- Excess Emissions NSPS – NOX.  See 40 CFR 60.4350 and 4380 in Appendix KKKK (NSPS Subpart KKKK Requirements for Stationary Combustion Turbines) of this permit.  [40 CFR 60.4350 and 60.4380; and, Permit No. 0570039-040-AC, Specific Condition 25.]

- Excess Emissions NSPS - SO2.  See 40 CFR 60.4385 in Appendix 40 CFR 60 KKKK (NSPS Subpart KKKK Requirements for Stationary Combustion Turbines) of this permit.  [40 CFR 60.4385 and Permit No. 0570039-040-AC, Specific Condition 26.]

Continuous Monitoring Requirements

- Continuous Emissions Monitoring Systems (CEMS).  The permittee shall calibrate, maintain and operate the diluent CEMS to measure CO2 emissions and CEMS to measure and record the emissions of CO and NOX from each gas turbine in a manner sufficient to demonstrate continuous compliance with the emission standards of this section.

- NOX Monitor.  Each NOX monitor shall be certified pursuant to the specifications of 40 CFR 75.  Quality assurance procedures shall conform to the requirements of 40 CFR 75, Appendix B.  The annual and required Relative Accuracy Test Audit (RATA) tests required for the NOX monitor shall be performed using EPA Method 7E or 20 in 40 CFR 60, Appendix A.

- CO Monitor.  Each CO monitor shall be certified pursuant to 40 CFR 60, Appendix B, Performance Specification 4 or 4A.  Quality assurance procedures shall conform to the requirements of 40 CFR 6075, Appendix FB.  The annual and required RATA tests required for the CO monitor shall be performed using EPA Method 10 in 40 CFR 60, Appendix A, and shall be based on a continuous sampling train.  The CO monitor span values shall be set appropriately, considering the allowable methods of operation and corresponding emission standards.

- SO2 Monitoring.  SO2 monitoring will be in accordance with 40 CFR 75, Appendix D and, Appendix TR requirements (using sulfur content and fuel flow rates).

- Diluent Monitor.  The carbon dioxide (CO2) content of the flue gas shall be monitored at the location where CO and NOX are monitored to correct the measured emissions rates to 15% oxygen.  The oxygen content of the flue gas shall be calculated using F-factors that are appropriate for the fuel fired.  Each monitor shall comply with the performance and quality assurance requirements of 40 CFR 75, Appendix B.

[Rule 62-297.520, F.A.C.; 40 CFR 75; Permit No. 0570039-04066-AC, Specific Condition 27.; and, Appendix CEMS for EU 41 and 42 of this permit.]

- CEMS Data Requirements.  The CEMS shall be calibrated, maintained and operated in the gas turbine stacks to measure and record the emissions of CO and NOX in a manner sufficient to demonstrate compliance with the CEMS-based emission limits of this section.  The CEMS shall express the results in units of ppmvd corrected to 15% oxygen.  Upon request by the Department, the CEMS emission rates shall be corrected to ISO conditions to demonstrate compliance with the applicable NOX standards of 40 CFR 60, Subpart KKKK, Table 1.  The permittee shall be in compliance with the terms and conditions contained in Appendix CEMS for EU 41 and 42, Standard Continuous Monitoring Requirements, of this permit.  [Permit No. 0570039-040-AC, Specific Condition 28.]

- CEMS Annual Emissions Requirement:  The owner or operator shall use data from the NOX and CO CEMS when calculating annual emissions for purposes of computing actual emissions, baseline actual emissions, and net emissions increase, as defined at Rule 62-210.200, F.A.C., and for purposes of computing emissions pursuant to the reporting requirements of Rule 62-210.370(3), F.A.C., Annual Operating Report.  In computing the emissions of a pollutant, the owner or operator shall account for the emissions during periods of startup and shutdown of the emissions unit.  [Rules 62-210.200(Definitions) and 62-210.370(3), F.A.C.; and, Permit No. 0570039-040-AC, Specific Condition 29.]

- CEMS - Appendix CEMS for EU 41 and 42.  Additional requirements applicable to the CEMS are given in the attached Appendix CEMS for EU 41 and 42, which is a part of this permit.  [Permit No. 0570039-040-AC)]

Test Methods and Procedures

{Permitting Note:  The attached Table 2, Summary of Compliance Requirements, summarizes information for convenience purposes only.  This table does not supersede any of the terms or conditions of this permit.}

- Test Methods.  Required tests shall be performed in accordance with the following reference methods:

| Method | Description of Method and Comments |
| --- | --- |
| 1-4 | Methods for Determining Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content: These methods shall be performed as necessary to support other methods. |
| 5 | Method for Determining Particulate Matter Emissions |
| 7E | Determination of NOX Emissions from Stationary Sources (Instrumental) |
| 6 or 6C | Determination of SO2 Emissions from Stationary Sources |
| 8 | Determination of SAM and SO2 Emissions from Stationary Sources |
| 9 | Visual Determination of Opacity of Emissions from Stationary Sources |
| 10 | Determination of Carbon Monoxide Emissions from Stationary Sources |
| 18 | Measurement of Gaseous Organic Compound Emissions by Gas Chromatography {Note: EPA Method 18 may be used (optional) concurrently with EPA Method 25A to deduct emissions of methane and ethane from the measured VOC emissions.} |
| 19 | Determination of Sulfur Dioxide Removal Efficiency and Particulate Matter, Sulfur Dioxide, and Nitrogen Oxide Emissions Rates |
| 20 | Determination of NOX, SO2, and Diluent Emissions from Stationary Combustion Turbines |
| 25A | Determination of Total Gaseous Organic Concentrations Using a Flame Ionization Analyzer |

The methods are described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used for compliance testing unless prior written approval is received from the Administrator of the Department’s Emissions Monitoring Section in accordance with an alternate sampling procedure pursuant to Rule 62-297.620, F.A.C.  [40 CFR 60, Appendix A; Rule 62-204.800, F.A.C.; and, Permit No. 0570039-040-AC, Specific Condition 13.]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- Annual Compliance Testing.  During each federal fiscal year (October 1st to September 30th), each SCCT shall be tested to demonstrate compliance with the emission standard for opacity if the SCCT fired ULSD fuel more than 400 hours/year.  Unless specifically requested by the Compliance Authority pursuant to Rule 62-297.310(7)(b), F.A.C., periodic opacity tests are not required when firing natural gas.  annual compliance tests for visible emissions shall be conducted.  For each visible emissions test, Eemissions of CO and NOx recorded by the CEMS shall also be reported.  [Rules 62-297.310(7)(a) and (b), F.A.C. and Permit No. 0570039-04066-AC, Specific Condition 16.]

- Compliance Tests Prior To Renewal.  See Specific Condition O.24.  Any SCCT that did not fire ULSD fuel for more than 400 hours/year shall conduct a visible emissions compliance test once per each five-year period, coinciding with the term of its air operation permit. [Rules 62-210.300(2)(a) and 62-297.310(7)(a)(8), F.A.C.]

- Visible Emissions.  The test method for visible emissions shall be EPA Method 9, incorporated in Chapter 62-297, F.A.C.  [Rule 62-297.401, F.A.C. and Permit No. 0570039-040-AC, Specific Condition 13.]

- CO Compliance.  Continuous compliance shall be demonstrated with the 3-hour rolling average CO emission limits by data collected by the required CEMS.  CO will be used as a surrogate for VOC emissions as a demonstration of good combustion.  [Rule 62-4.070(3), F.A.C. and Permit No. 0570039-040-AC, Specific Condition 13.]

- Nitrogen Oxide.  The permittee shall conduct an annual Relative Accuracy Test Audit (RATA) on each SCCT to demonstrate compliance with the short-term NOX emission limits (ppmvd @ 15% O2 and lb/hr (mass emissions)) per fuel type.  Continuous compliance shall be demonstrated with the 4-hour rolling average NOX emission limits by data collected from the required continuous emissions monitoring system (CEMS).  When firing ULSD, compliance with the SIP limit ensures compliance with the NSPS limit of 74 ppmvd @ 15% O2.  When firing both NG and ULSD, compliance with the NSPS limit is ensured by complying with either the NSPS limit, for NG, or the SIP limit, for ULSD, depending on the contribution of the fuels of the total heat input:  if the total heat input contribution is equal to or greater than 50 percent from NG, you must meet the corresponding limit for a NG-fired turbine when you are burning that fuel; similarly, when your total heat input contribution is greater than 50 percent from ULSD, you must meet the corresponding limit for ULSD for the duration of the time that you burn that particular fuel.  [40 CFR 60.4350(g) and Permit No. 0570039-040-AC, Specific Condition 13.]

- NSPS Compliance Demonstrations for NOX.  See 40 CFR 60.4400 and 4405 in Appendix 40 CFR 60, Subpart KKKK, Standards of Performance for Stationary Combustion Turbines of this permit for the compliance demonstration requirements for NOX.  [40 CFR 60.4400 and 60.4405; and Permit No. 0570039-040-AC, Specific Condition 17.]

- NSPS Compliance Demonstrations for Sulfur.  See 40 CFR 60.4415 in Appendix 40 CFR 60, Subpart KKKK, Standards of Performance for Stationary Combustion Turbines of this permit for the compliance demonstration requirements for SO2.  A one-time compliance test on one SCCT was conducted for SO2 mass emissions in order to satisfy compliance with the mass limit and the quality of the NG and ULSD.  Afterwards, the use of NG and ULSD in accordance with the permit and 40 CFR 60.4415 will be used as a surrogate for SO2 emissions.  [40 CFR 60.4415 and Permit No. 0570039-040-AC, Specific Condition 18.]

- Continuous Compliance.  The permittee shall demonstrate continuous compliance with the 3-hour rolling average CO emissions standards and with the 4-hour rolling average NOX emission standards based on data collected by the required CEMS.  Within 45 days of conducting any RATA on a CEMS that represents the annual compliance test, the permittee shall submit a report to the Compliance Authority summarizing results of the RATA.  If the RATA on a CEMS was not conducted as an annual compliance test, then the results can be submitted with the SIP Quarterly or Semiannual Report.  Compliance with the CO emission standards also serves as an indicator of efficient fuel combustion, which also reduces emissions of PM.  [Rules 62-4.070(3) and 62-297.310(7)(a) and (b), F.A.C.; and, Permit No. 0570039-040-AC, Specific Condition 19.]

Recordkeeping and Reporting Requirements

- Reporting Schedule.  The following reports and notifications shall be submitted to the Compliance Authority:

| Report | Reporting Deadline | Related Conditions |
| --- | --- | --- |
| CEMS RATA Reports | 15 days prior to RATA | O.384. |
| Excess Emissions Reporting | Various | O.395. |
| Notification of Tuning | One day prior to tuning | O.40. |

[Rule 62-213.440, F.A.C.]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.

- CEMS RATA Reports.  At least 15 days prior to conducting any RATA on a CEMS, the permittee shall notify the Compliance Authority of the schedule (letter, email, fax, or phone call).  A summary of the RATA reports shall be provided upon written request of the Compliance Authority and in the SIP Excess Emissions Report as specified in Specific Condition O.39.  [Rule 62-4.070(3), F.A.C.]

- Excess Emissions Reporting.

- Malfunction Notification.  If emissions in excess of a standard (subject to the specified averaging period) occur due to malfunction, the permittee shall notify the Compliance Authority within (1) working day of:  the nature, extent, and duration of the excess emissions; the cause of the excess emissions; and the actions taken to correct the problem.  In addition, the Department may request a written summary report of the incident.

- SIP Excess Emissions Report.  Within 30 days following the end of each calendar quarter, the permittee shall submit a report to the Compliance Authority of the following for each gas turbine using the NSPS format in 40 CFR 60.7(c), Subpart A:  a summary of the 4-hour rolling average NOX compliance periods for the quarter; a summary of the 3-hour rolling average CO compliance periods for the quarter; a summary of NOX and CO data excluded for the quarter; a summary of any RATA tests performed during the quarter; and a summary of the CEMS systems monitor availability for the quarter.

(1)	If four consecutive quarterly reports demonstrate compliance with the CEMS-based emissions standards, the reporting frequency may be reduced to semiannual reporting.  As part of the fourth consecutive satisfactory quarterly report, the permittee shall provide written notification of its intent to reduce the reporting frequency to a semiannual basis.  The notification shall include a statement that the units were in full compliance during the four consecutive quarters and that reporting will be reduced to a semiannual basis.  Semiannual reports shall include all of the above information required for each quarter in the semiannual period.  The permittee shall continue to comply with all other record keeping and monitoring provisions.

(2)	If reports are being submitted on a semiannual basis and a unit is not in compliance with the CEMS-based emissions standards, the permittee shall immediately (within one day of detection) notify the Compliance Authority of the compliance status and reestablish quarterly reporting beginning with the current quarter.  If compliance is reestablished for four consecutive quarters, semiannual reporting may resume as specified above.

- NSPS Reporting.  For each affected unit required to continuously monitor parameters or emissions, or to periodically determine the fuel sulfur content under 40 CFR 60, Subpart KKKK, the owner or operator must submit reports of excess emissions and monitor downtime, in accordance with 40 CFR 60.7(c).  Excess emissions must be reported for all periods of unit operation, including start-up, shutdown and malfunction.

{Note:  If there are no periods of excess emissions as defined in 40 CFR 60, Subpart KKKK, a statement to that effect may be submitted with the SIP Quarterly Report to suffice for the NSPS Semiannual Report.}

[40 CFR 60.7 and 60.4375; Rules 62-4.130, 62-204.800 and 62-210.700(6); and, Permit No. 0570039-040-AC, Specific Condition 36.]

- Notification of Tuning.  If emissions in excess of a standard could reasonably be expected to occur due to a planned tuning activity, the permittee shall notify the Compliance Authority at least one working day prior to the expected activity of the nature, extent, and duration of the planned tuning activity.  In addition, the Department may request a written summary report of the extent and duration of the resulting excess emissions.  [Rule 62-213.440, F.A.C.]

- Test Reports.  The permittee shall prepare and submit reports for all required tests in accordance with the requirements specified in Appendix TR, Facility-Wide Testing Requirements of this permit.  [Rule 62-297.310(8), F.A.C. and Permit No. 0570039-040-AC, Specific Condition 30.]

- Monitoring and Recording of Capacity.  The permittee shall monitor and record the heat input of each SCCT on a daily average basis, considering the number of hours of operation during each day (including the times of startup, shutdown and malfunction).  This shall be achieved through monitoring daily rates of consumption and heat content of each allowable fuel in accordance with the provisions of 40 CFR 75, Appendix D, and recording the data using a monitoring component of the CEMS required above (see Appendix CEMS for EU 41 and 42 of this permit).  [Permit No. 0570039-040-AC, Specific Condition 31.]

- Monthly Operations Summary.  By the 15th calendar day of each month, the permittee shall record the following for each fuel in a written or electronic log for the combustion turbine for the previous month of operation:  fuel consumption, hours of operation and the updated calendar year totals for each.  Information recorded and stored as an electronic file shall be available for inspection and printing within at least three days of a request by the Department.  [Permit No. 0570039-040-AC, Specific Condition 32.]

- Fuel Sulfur Records.  The permittee shall demonstrate compliance with the fuel sulfur limits specified in this permit by maintaining the following records of the sulfur contents.

- Natural Gas Sulfur Limit:  Compliance with the fuel sulfur limit for natural gas shall be demonstrated by keeping reports obtained from the vendor indicating the average sulfur content of the natural gas being supplied from the pipeline for each month of operation.  A representative sample shall be collected using ASTM D5287.  Methods for determining the sulfur content of the natural gas shall be ASTM methods D1072, or alternatively D3246, D4084, D4468, D4810, D6228, D6667, or Gaseous Processors Association Standard 2377, or more recent versions, or through provisions listed in 40 CFR 60, Subpart KKKK that allows alternate NG fuel sulfur monitoring.

- ULSD Fuel Sulfur Limit:  Compliance with the fuel sulfur limit for ULSD fuel shall be demonstrated by keeping each bill of lading report obtained from the vendor indicating the sulfur content, percent by weight, of the ULSD fuel being delivered.  A representative sample shall be collected using ASTM D5287.  Methods for determining the sulfur content of the ULSD fuel shall be ASTM methods D1072, or alternatively D3246, D4084, D4468, D4810, D6228, D6667, or Gaseous Processors Association Standard 2377, or more recent versions, or through provisions listed in 40 CFR 60, Subpart KKKK that allows alternate sulfur monitoring for ULSD.

The above methods shall be used to determine the fuel sulfur content in conjunction with the provisions of 40 CFR 60.4415 contained in Appendix 40 CFR 60, Subpart KKKK, Standards of Performance for Stationary Combustion Turbines of this permit.  [40 CFR 60.4415; Rules 62-4.070(3) and 62-4.160(15), F.A.C.; and Permit No. 0570039-040-AC, Specific Condition 33.]

- Combustion Turbine Replacements.  The SCCT may be replaced with a temporary equivalent “like-kind” overhauled or new SCCT while the existing SCCT is undergoing routine maintenance.  The replacement CT shall not increase the CT maximum heat input rate or actual emissions.  The replacement CT shall be designed and constructed to achieve the emissions standards specified in this permit. The replacement CT shall be deemed in compliance with all emissions standards by demonstrating compliance with the NOX and CO emission standards using data from the CO and NOX CEMS.  The permittee shall meet the following requirements:

  - Report.  The temporary SCCT shall only be used for a maximum of 3-months.  The permittee shall notify the Department within one day prior to replacing the CT with a temporary SCCT and when the original SCCT is back in operation.  The permittee shall notify the Department if additional time is needed for the replacement CT.

  - Recordkeeping.  The permittee shall maintain a log on-site to record the date of any CT replacement, the manufacturer, model number, and serial number of the CT that is replaced during the term of this permit, and the manufacturer, model number, serial number, and the installation and removal date of the replacement CT.  All records related to any testing shall be maintained on-site for five years and made available to the Department upon request.

  - Compliance Requirements.  The permittee shall comply with the requirements for notification, test methods, test procedures, and reporting required by this permit.

  - PSD Applicability.  If it is determined that the SCCTs actual emissions, heat input or capacity increased as a result of the maintenance performed, the applicant shall submit an application for an air construction permit within 30 days to evaluate PSD applicability resulting from the modification.

[Permit No. 0570039-066-AC]

The specific conditions in this section apply to the following emissions units:

| E.U. ID No. | ## Brief Description |
| --- | --- |
| Fuel Blending and Crushing |  |
| -029 | Fuel Blending Bin Cyclone Collectors (FH-032 through FH-035) |
| -030 | Fuel Mill Cyclone Collectors (FH-048 and FH-049) |

These emissions units consist of solid fuel crushing and blending activities as described in more detail below.

Solid fuel (consisting of coal and petcokepetroleum) is unloaded from ships and barges into the solid fuel yard (see EU ID No. -010), the blending bins or directly to the tripper room via belt conveyors.  Solid fuel may also be received/unloaded by railcar (see EU ID No. -047) and conveyed to the fuel yard.  Solid fuel from the storage piles is loaded onto belt conveyors using a rail mounted or mobile reclaimer.  The solid fuel is then belt conveyed to the blending bins, which consists of six storage bins, where the solid fuel may be blended for use at the plant, or transloaded into trucks for shipment off site (see EU ID No. -046).  Particulate matter (PM) emissions from the conveyors in the blending bins are controlled by 4 rotoclones.  One at the conveyor drop and 3 additional rotoclones (one for every 2 bins) control particulate matter from ventilation of the blending bins.  Blending bins can either feed the transloader, or solid fuel can be conveyed, via 2 parallel belts (T1, T2) to 2 crushers (each belt has a crusher), or diverted directly to the tripper room.  PM emissions from the 2 crushers and transfer tower are controlled by 2 rotoclones.  E.U. ID Nos. -029 and -030 began commercial operation in 1970.  The fuel blending bin cyclones collectors and the fuel mill cyclone collectors each have their own emissions points through the roof of the supporting structure with the following emissions parameters:  height, approximately 70 feet above grade; diameter, 1.67 feet; exit temperature, 77 degrees F; and, actual stack gas flow rate, 9,400 acfm.

{Permitting note(s):  These emissions units are regulated under Rule 212.400(5), F.A.C., Prevention of Significant Deterioration [PSD-FL-040]; Rule 62-296.711, F.A.C., Reasonably Available Control Technology (RACT) Particulate Matter (PM) - Materials Handling, Sizing, Screening, Crushing and Grinding Operations; Rule 62-210.300, F.A.C., Permits Required; Power Plant Siting Certification [PA 79-12]; and, Chapter 1-3.52, Rules of the EPC, Rules of the Environmental Protection Commission (EPC) of Hillsborough County.}

Authorized Emissions Points

The emissions units contained in this subsection are comprised of the following emissions points, which are enclosed conveyors and drop points located within an enclosed building:

| E.U. ID No. -029: Fuel Blending Bin Rotoclone Collectors |  |
| --- | --- |
| Point ID | Description of Emissions Point |
| FH‐032-FH035 | Conveyors Q1 and Q2 to Blending Bins |

| E.U. ID No. -030: Fuel Mill Rotoclone Collectors |  |
| --- | --- |
| Point ID | Description of Emissions Point |
| FH‐048 | Conveyor T1 to Crusher #1 |
| FH‐049 | Conveyor T2 to Crusher #2 |

Essential Potential to Emit (PTE) Parameters

{Permitting Note:  The handling capacity for the conveyors and equipment that comprises the solid fuel yard emissions points is not specifically limited; however, the design capacity for the majority of the handling equipment is 4,000 tons per hour.  The total annual solid fuel handling capacity is inherently limited by the amount of fuel that Boilers 1 – 4 can burn (5-6 million tons per year) plus the amount of solid fuel that can be transloaded for off-site shipment (1,428,030 tons per year, see E.U. ID No. -046).  In addition, permit No. 0570039-041-AC established an annual limit of 8 million tons per year of solid fuel that can be received by railcar (see E.U. ID No. -047).}

- Methods of Operation – Materials Handling.  The materials that are allowed to be handled by these emissions units are coal, petroleum coke, slag and residual coal (generated at the TEC Polk Power Station).  [PA 79-12 and Permit No. 0570039-012-AC]

- Hours of Operation.  These emissions units may operate continuously (8,760 hours/year).  [Rule 62-210.200 (Definitions - Potential to Emit (PTE), F.A.C. and PA 79-12]

Control Technology

- PM Control Devices.  Particulate matter emissions shall be controlled by use of control devices.  [PA 79-12.]

{Permitting Note:  This requirement is satisfied by the use of rotoclone collectors on the blending bins and fuel mill.}

Emission Limitations and Standards

{Permitting Note:  The attached Table 1, Summary of Air Pollutant Standards, summarizes information for convenience purposes only.  This table does not supersede any of the terms or conditions of this permit.}

Unless otherwise specified, the averaging times for Specific Conditions P.4. and P.5. are based on the specified averaging time of the applicable test method.

- VE/Opacity Limit.  As determined by annual compliance tests, visible emissions shall not exceed 5% opacity.  [Rule 62.296.711(2), F.A.C.; Chapter 1-3.52, Rules of the EPC; and, Rule 62-297 (7) (c ) F.A.C PA 79-12]

- Particulate Matter (PM).  Compliance with the visible emissions limitation satisfies the intent of the applicable RACT rules.  [Rules 62-296.711(2)(b), F.A.C. and PA 79-12; and, Permit No. 0570039-053-AC, Specific Condition 7.]

Excess Emissions

- Excess Emissions Allowed.  Excess emissions resulting from startup, shutdown or malfunction of any emissions unit shall be permitted providing (1) best operational practices to minimize emissions are adhered to and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C.]

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown, or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C.]

Test Methods and Procedures

{Permitting Note:  The attached Table 2, Summary of Compliance Requirements, summarizes information for convenience purposes only.  This table does not supersede any of the terms or conditions of this permit.}

- Test Method  Required test shall be performed in accordance with the following reference method(s):

| Method | Description of Method and Comment |
| --- | --- |
| EPA Method 9 | Visual Determination of the Opacity of Emissions |

The above method is described in Chapter 62-297, F.A.C. and/or 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other method may be used unless prior written approval is received from the Department.  [Chapter 62-297, F.A.C.]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- Annual Compliance Tests.  During each federal fiscal year (October 1st to September 30th), a VE tests shall be performed to demonstrate compliance with the standards specified in Specific Condition P.4.  (EU 029) one of the fuel blending bin roto-clones (FH-032 – FH-035) and (EU 030) one of the fuel mill roto-clones (FH-048 and FH-049) Emissions Unit ID Nos. -015, -016, -017 and -039shall be tested to demonstrate compliance with opacitythe emission limitations and standards for visible emissions (VE).Each year a different fuel blending bin roto-clone shall be tested in subsequent order (FH-032, FH-033, etc.) and each year a different fuel mill roto-clone will be tested.  The annual compliance tests will be used in lieu of the compliance test prior to renewal. [Rules 62-297.310(7), F.A.C. and 62-4.070(1) & (3) (Reasonable Assurance), F.A.C.; and, PA 79-12.]

- Compliance Test Prior To Renewal.  Prior to permit renewal, a VE tests shall be performed to demonstrate compliance with the standards specified in Specific Conditions P.4.  [Rule 62-297.310(7)(a)3., F.A.C.]

- Visible Emissions Test.  Compliance with the visible emission limits of this permit shall be demonstrated by an annual compliance test using EPA Method 9.  The duration of the annual test shall be 30 minutes.  [Rules 62-4.070(3), 62-296.711(3)(a) and 62-297.310(4)(a)2., F.A.C.]

- Reserved.

Recordkeeping and Reporting Requirements

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440, F.A.C.]

- Fuel Daily Log.  The permittee shall maintain a daily log of the amounts and types of fuels used and copies of fuel analyses containing information on sulfur content, ash content and heating values.  [PA 79-12]

The specific conditions in this section apply to the following emissions units:

| E.U. ID No. | ## Brief Description |
| --- | --- |
|  | Solid Fuel Yard |
| -046 | Transloading and Off-site Transfer of Solid Fuels and Slag (by truck, rail and barge) |

This emissions unit is housed within the solid fuel yard and is comprised of transfer and loading equipment designed to take material from the blending bins (E.U. ID No. -029) and/or the storage piles in the fuel yard (E.U. ID No. -010) and, using mobile equipment tofront-end loaders, load it onto trucks, railcars and bargesor trains for shipment to off-site locations.  The material that is allowed to be loaded for off-site shipment is coal, petcokepetroleum coke and slag.  The main purpose of the transloading operation is to provide coal and petcokepetroleum coke to the Tampa Electric Company Polk Power Station; however, the permittee is authorized to operate as a fuel and slag supplier to other non-Tampa Electric Company facilities, as well.  The coal orand petcokepetroleum coke is treated with a chemical surfactant prior to arriving at the Big Bend Station.  The slag has minimal dust potential due to its glassine properties and therefore does not need to be treated with a chemical surfactant.

{Permitting note(s):  This emissions unit is regulated under Rule 62-210.300, F.A.C., Permits Required; Rule 62-296.711320(4)(b), F.A.C., General Visible Emissions Standard; and, 62-296.320(4)(c), F.A.C., Unconfined Emissions of Particulate Matter Reasonably Available Control Technology (RACT) Particulate Matter (PM) - Materials Handling, Sizing, Screening, Crushing and Grinding Operations; and Power Plant Siting Certification [PA 79-12]; and, Chapter 1-3.52, Rules of the EPC, Rules of the Environmental Protection Commission (EPC) of Hillsborough County.}

Authorized Emissions Points

Emissions unit ID No. -046 is comprised of the following emissions points:

| Point ID | Brief Description of Emissions Point |
| --- | --- |
| FH-065 | Loadout Conveyor to Rail Transfer Conveyor |
| FH-066 | Railcar Loading |
| FH-067 | Non-TEC Fuel Stockpile to Loadout Conveyor |
| FH-068 | Non-TEC Fuel Truck Loading |
| FH-069 | Polk Fuel Truck Loading |
| FH-074a | Reclaim from PetcokePetroleum Coke Storage Pile to Trucks |
| FH-074b | Reclaim from Coal Storage Pile to Trucks |
| FH 074c | Reclaim from Slag Storage Pile to Trucks |
| FH-075a | Truck Traffic (paved roads, empty trucks) |
| FH-075b | Truck Traffic (paved roads, full trucks) |
| FH-076a | Truck Traffic (unpaved roads, empty trucks) |
| FH-076b | Truck Traffic (unpaved roads, full trucks) |
| FH-080a | Truck Traffic to Barge Transloading (paved roads, empty trucks) |
| FH-080b | Truck Traffic to Barge Transloading (paved roads, full trucks) |
| FH-081a | Truck Traffic to Barge Transloading (unpaved roads, empty trucks) |
| FH-081b | Truck Traffic to Barge Transloading (unpaved roads, full trucks) |

Essential Potential to Emit (PTE) Parameters

- Permitted Capacity.  The maximum solid fuels/slag transloading rate for EU 046 shall not exceed 4,000 tons/hour on a 24-hour average and a total of 1,853,030 tons/year for all solid fuel and slag materials transloaded onto trucks, railcars and barges for shipment off-site.  [PA 79-12C and Application No. 0570039-059-AC]

a.	Hourly Limit.  From each fuel transloading source/emissions point (i.e., off-loading and loading of fuel/slag for export from Big Bend Station), the maximum hourly transloading transfer of fuel shall not exceed 4,000 tons, 24-hour rolling average.  [PA 79-12; PA 79-12C and D; and Permit No. 0570039-025-AC]

b.	Annual Limits.

(1)	The maximum solid fuel/slag transloading rates for these emissions points shall not exceed 1,428,030 tons per year.  [PA 79-12; PA 79-12C and D; and Permit No. 0570039-025-AC]

(2)	The maximum annual transloading rates for Emissions Points FH-74a – FH-76b shall not exceed 150,000 tons per year for each material (coal, petcoke, slag) and 450,000 tons per year for all three materials combined; and, only one material shall be transloaded at a time.  [Permit No. 0570039-025-AC]

- Emissions Unit Operating Rate Limitation After Testing.  See the related testing provisions in Appendix TR, Facility-wide Testing Requirements.  [Rule 62-297.310(2), F.A.C.]

- Methods of Operation.

a.	Materials Allowed.  The materials that are allowed to be handled by the emissions points that comprise this emissions unit are coal, petroleum coke and slag.

b.	Material Not Allowed.  The emission points listed above as FH-074a, b and c, FH-075a and b, and FH-076a and b are not allowed to transload residual coal.

[PA 79-12 and Permit No. 0570039-025-AC]

- Hours of Operation.  This emissions unit may operate continuously (8,760 hours/year).  [Rule 62-210.200(PTE), F.A.C. and Permit No. 0570039-025-AC]

Control Technology

- Controls of Particulate Matter.  The emissions related to the transloading activities is fugitive in nature resulting from unconfined emissions.  Reasonable precautions to prevent unconfined emissions of particulate matter from the transloading-related emissions points include:

- Paving and maintenance of roads, parking areas and yards where possible.

- Application of water or chemicals to control emissions as needed.

- Removal of particulate matter from roads and other paved areas under the control of the owner or operator of the facility to prevent re-entrainment, and from buildings or work areas to prevent particulate from becoming airborne.

- Landscaping or planting of vegetation.

- Use of hoods, fans, filters, and similar equipment to contain, capture and/or vent particulate matter.

- Confining abrasive blasting where possible.

- Maintaining enclosures or coverings of conveyor systems and transfer points where possible.

- Trucks used to transport coal, petcoke or slag shall utilize tarps at all times except when loading/unloading.

[Rules 62-296.320(4)(c) and Permit No. 0570039-025-AC]

- Reasonable Precautions to Prevent Unconfined Particulate Matter Emissions.  The transloading, from storage piles of solid fuels (petroleum coke or coal) or slag, to trucks, railcars and barges by mobile equipment (e.g. front end loaders) is subject to the facility-wide general visible emission standard of 20%; however, annual visible emissions compliance testing is not required for these sources of fugitive emissions.  The solid fuels and slag transloading operations shall be controlled under existing management practices at the facility for minimizing fugitive dust (e.g., watering open storage areas and roads sufficient to minimize entrained dust).  Fugitive emissions of particulate matter associated with transloading these solid materials shall be minimized using reasonable precautions such as paving and maintenance of roads, parking areas or yards, or application of water or dust suppressant chemicals at each transloading emission point (e.g. FH-74a for reclaiming from petroleum coke storage pile to trucks, FH-74b for reclaiming from coal storage piles to trucks, and FH-074c for reclaiming from slag storage pile to trucks).  Fugitive particulate matter emissions shall also be controlled onsite using reasonable precautions (e.g., tarps, applications of water or chemicals for suppression of road dust) for fugitive emission points associated with transport vehicles on paved and unpaved roads (emission points FH-75a through FH-81b).  [Rule 62-296.320(4)(b)1., F.A.C.; and Permit No. 0570039-059-AC]

Emission Limitations and Standards

{Permitting Note:  The attached Table 1, Summary of Air Pollutant Standards, summarizes information for convenience purposes only.  This table does not supersede any of the terms or conditions of this permit.}

Unless otherwise specified, the averaging time for Specific Conditions Q.6. is based on the specified averaging time of the applicable test method.

- Visible Emissions.  Visible emissions generated by fugitive or unconfined particulate matter from this transloading operation shall not exceed 20% opacity.  [Rule 62-296.320(4)(b)1., F.A.C.; PA-79-12; and, Permit No. 0570039-025-AC.]

Excess Emissions

- Excess Emissions Allowed.  Excess emissions resulting from startup, shutdown or malfunction of any emissions unit shall be permitted providing (1) best operational practices to minimize emissions are adhered to and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C.]

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown, or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C.]

Test Methods and Procedures

- Test Methods.  Required tests shall be performed in accordance with the following reference methods:

| Method(s) | Description of Method(s) and Comment(s) |
| --- | --- |
| EPA Method 9 | Visual Determination of the Opacity of Emissions |

The above methods are described in Chapter 62-297, F.A.C. and/or 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Chapter 62-297, F.A.C.]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- Annual Compliance Test.  Annual testing shall be performed on emissions points FH-074a and FH-074b.  For the purpose of the VE test, the hourly transloading rate to trucks at the subject emissions points shall be as close to 144 tons per hour as practicable.  [Rules 62-204.800, 62-297.310(7)(a)4. and 62-297.400, F.A.C.; and, Permit No. 0570039-025-AC]

{Permitting note:  No annual testing is required for emission point FH-074c based on the initial visible emissions test conducted on May 2, 2007 indicating that slag handling has minimal emissions.}

- Compliance Test Prior To Renewal.  Prior to permit renewal, VE tests shall be conducted on emissions points FH-074a and FH-074b.  For the purpose of the VE test, the hourly transloading rate to trucks at the subject emissions points shall be as close to 144 tons per hour as practicable.  [Rule 62-297.310(7)(a)3., F.A.C. and Permit No. 0570039-025-AC]

- Visible Emissions Test.  Compliance with the visible emission limits of this permit shall be demonstrated by an annual compliance test using EPA Method 9.  The duration of the annual test shall be 30 minutes.  [Rules 62-4.070(3) and 62-297.310(4)(a)2., F.A.C.; and, Permit No. 0570039-025-AC]

Recordkeeping and Reporting Requirements

- Recordkeeping and Reporting.  The number of railcars, and trucks and barges, and the quantity and type of material loaded and transported off-site by each fuel transloading operation emissions point covered in this permit  (i.e., off-loading and loading of fuel or slag {for export from Big Bend Station}) shall be recorded, maintained, and kept on file for a minimum of five years.  The annual quantity of each transloaded material shall be submitted in the Annual Operation Report.  All reports and records required by this permit shall be kept for at least (5) years from the date the information was recorded.  [PA 79-12 and Permit No. 0570039-02566-AC]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440, F.A.C.]

The specific conditions in this section apply to the following emissions unit:

| E.U. ID No. | ## Brief Description |
| --- | --- |
|  | Solid Fuel Yard |
| -047 | Railcar Unloading and Conveying System |

As an alternative to receiving solid fuel or slag by ship and/or barge, these materials may be delivered by railcar in the railcar unloading building.  The railcar unloading building is an enclosed structure (except for the railcar entrance and exit openings), designed to receive material through a slow and controlled continuous unloading process.  The railcar will drop the material as each railcar unit enters the unloading building and will continue to discharge the material from its tapered bottom chutes until the railcar reaches the exit end of the building.  Once the material is discharged from the railcars, it drops through a stationary safety screen and into collecting hoppers.  Each collecting hopper has tapered discharge chutes equipped with slide gates.  From the collecting hoppers, the material falls directly onto a variable speed belt which feeds to the series of conveyors that transfers the material to the existing P1 or F1 conveyors of the solid fuel yard (see E.U. ID No. -010).  The series of enclosed conveyors associated with the Railcar Coal Unloading System consist of conveyors C-10, C-11, C-12, C-13, C-14, C-15 and C-16.  The fugitive emission controls include covers on all belt conveyors, enclosures on all transfer/drop points, and a fog type dust suppression system utilizing misters and surfactants is used within the enclosures as needed.  The railcar unloading and conveying system is designed for a transport rate of 4,000 tons per hour (TPH) (24-hour rolling average).

The railcar coal unloading system consists of one railcar unloading building and a series of transfer conveyors. The railcar unloading building is an enclosed structure (except for the railcar entrance and exit openings) that unloads coal in a slow and controlled manner. As each railcar passes through the railcar unloading building, the coal is dropped through a stationary safety screen and into collecting hoppers. The coal is discharged from each collecting hopper through a series of slide gates to control the amount of coal dropped onto the variable speed belt conveyor.  A water spray & chemical surfactant dust suppression system is used to control fugitive emissions as coal is unloaded into the receiving hopper. The system also includes a secondary spray & chemical surfactant dust suppression system at the end of the variable speed belt conveyor to further minimize fugitive emissions.

A system of conveyors is used to transfer coal from the variable speed belt conveyor in the railcar unloading building to the P or F conveyors in the solid fuel yard. These transfer conveyors consist of conveyors C10, C-11, C-12, C-13, C-14, C-15 and C-16. The fugitive emissions are controlled by enclosed conveyors and totally enclosed drops points at the transfer structures.

{Permitting Note:  This emissions unit is regulated under Rule 62-210.300, F.A.C., Permits Required; and NSPS Subpart Y of 40 CFR 60}

Authorized Emissions Points

Emissions unit ID No. -047 is comprised of the following emissions points:

| Point ID | Brief Description of Emissions Point |
| --- | --- |
| RC-1 | Train Car Drop Unloading to Belt Feeder BF-1 |
| RC-2 | Transfer from BF-1 to Conveyor C-10 |
| RC-3 | Conveyor C-10 to Conveyor C-11 |
| RC-4 | Conveyor C-11 to Conveyor C-12 |
| RC-5 | Conveyor C-12 to Conveyor C-13 |
| RC-6 | Conveyor C-13 to Conveyor C-14 |
| RC-7 | Conveyor C-14 to Conveyor C-15 |
| RC-8 | Conveyor C-15 to Conveyor C-16 or Conveyor P |
| RC-9 | Conveyor C-16 Drop to Conveyor F |

{Permitting Note:  RC-1 (Train Car Drop Unloading to Belt Feeder BF-1, building vent) is the only emission point in the process, RC-2 through RC-9 is completely enclosed.}

Essential Potential to Emit (PTE) Parameters

- Permitted Capacity.  The maximum unloading rate is 4,000 tons per hour (24-hour rolling average).  The maximum annual transfer for the railcar unloading operations is 8,000,000 tons per year.  [Rule 62-210.200(PTE), F.A.C. and Permit No. 0570039-04166-AC]

- Emissions Unit Operating Rate Limitation After Testing.  See the related testing provisions in Appendix TR, Facility-wide Testing Requirements.  [Rule 62-297.310(2), F.A.C.]

- Methods of Operation.  The materials that are allowed to be handled in the Railcar Unloading and Conveying System are coal, petcokepetroleum coke and slag.  [Rule 62-213.440, F.A.C. and Permit No. 0570039-041-AC]

- Hours of Operation.  The hours of operation are not limited (8,760 hours per year).  [Rules 62-210.200 (PTE) and 62-213.440, F.A.C.]

Control Technology

- Railcar Coal Unloading Building.  The permittee shall utilize the water spray system or chemical dust suppression system in the railcar unloading building water/surfactant dust suppression system to control particulate matter emissions from the railcar unloading hopper.

[Rule 62-213.440, F.A.C. and Permit No. 0570039-04166-AC]

- Railcar Coal Unloading Conveying System.  The permittee shall utilize the water spray system or chemical dust suppression system in the railcar unloading building a water/surfactant dust suppression system to control particulate matter emissions from the railcar unloading conveying system. [Rule 62-213.440, F.A.C. and Permit No. 0570039-04166-AC]

Emission Limitations and Standards

{Permitting Note:  The attached Table 1, Summary of Air Pollutant Standards, summarizes information for convenience purposes only.  This table does not supersede any of the terms or conditions of this permit.}

Unless otherwise specified, the averaging time for Specific Conditions R.7. is based on the specified averaging time of the applicable test method.

- Opacity.  As determined by EPA Method 9, visible emissions from the railcar coal unloading system shall not exceed 20% opacity.  [40 CFR 60,NSPS Subpart Y of 40 CFR 60;(Standards of Performance for Coal Preparation Plants) and Permit No. 0570039-041-AC]

{Permitting Note: In addition, the requirements in 40 CFR 60, New Source Performance Standard (NSPS) Subpart Y for Coal Preparation Plants, have been proposed to be amended on April 28, 2008 and would be applicable to all sources addressed in this standard and constructed after that date.  These amended standards, including installing a baghouse on the railcar unloading building may become applicable to this project when these standards become final and are adopted in the Florida rules.}

Excess Emissions

Rule 62-210.700 (Excess Emissions), F.A.C. cannot vary any requirement of an NSPS, NESHAP or Acid Rain program provision.

- Excess Emissions Allowed.  Excess emissions resulting from malfunction shall be permitted provided that best operational practices to minimize emissions are adhered to and the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C.]

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C.]

Test Methods and Procedures

{Permitting Note:  The attached Table 2, Summary of Compliance Requirements, summarizes information for convenience purposes only.  This table does not supersede any of the terms or conditions of this permit.}

- Test Methods.  Required tests shall be performed in accordance with the following reference methods.

| Method | Description of Method and Comments |
| --- | --- |
| 1-4 | Methods for Determining Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content: These methods shall be performed as necessary to support other methods. (IF REQUIRED) |
| 5 | Method for Determining Particulate Matter Emissions (IF REQUIRED) |
| 9 | Visible Determination of the Opacity of EmissionsEmissions Test |

The methods are described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used for compliance testing unless prior written approval is received from the Administrator of the Department’s Emissions Monitoring Section in accordance with an alternate sampling procedure pursuant to Rule 62-297.620, F.A.C.  [Rule 62-204.800, F.A.C. and 40 CFR 60, Appendix A]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- Annual Compliance Tests.  During each federal fiscal year (October 1st to September 30th), the Railcar Unloading Building vents shall be tested to demonstrate compliance with the emissions standard for visible emissions.  [Rule 62-297.310(7)(a)4, F.A.C. and Permit No. 0570039-041-AC]

Reporting and Recordkeeping Requirements

- Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements.  [Rule 62-213.440, F.A.C.]

This permit addresses the following new emissions unit:

| E.U. ID No. | ## Brief Description |
| --- | --- |
| -048 | Supplemental Material Handling J3 Conveyor System |

This supplemental material handling conveyor system consists of a grizzly in-feed hopper, which feeds material onto a 72” covered belt conveyor, a 54” covered belt conveyor, and an enclosed hopper at the existing K feeders (FH-103) (which feed into the existing L1 and L2 conveyors).  The combination of the grizzly feeder, the 72” belt conveyor and the 54” belt conveyor will be collectively referred to as the J3 Conveyor System.  All static drop points within the new conveyors will be completely enclosed with no emissions to the atmosphere.

The J3 Conveyor System will serve as a supplemental conveyance system for coal, coal blends and coal supplemental additives (such as limestone, flux, magnesium oxide, petroleum coke, ecotherm) for use with the existing conveyance feed system.  In the event the use of an existing back up coal conveyor system or related equipment is warranted, the J3 Conveyor System will be available to operate continuously.  The maximum throughput rate is designed for 2,000 TPH of solid materials, which is about half of the feed rate of the primary (existing) conveyor systems.

{Permitting Note:  This new emissions unit and associated emissions points are subject to applicable requirements of 40 CFR 60, Subpart Y - Standards of Performance for Coal Preparation Plants, adopted by reference in Rule 62-204.800(8) (b)22., F.A.C.; and, to Rule 62-296.320(4)(c), F.A.C., Unconfined Emissions of Particulate Matter.  This emission unit and associated emissions points are also subject to the Hillsborough County Environmental Protection Commission (HCEPC) Rules, Chapter 1-3, Stationary Air Pollution Sources and Ambient Air Quality Standards; specifically Part 5, Rule 1-3.52, Visible Emissions.  In addition, this new emission unit and associated emissions points are subject to applicable requirement of Rule 62-296.700 Reasonable Available Control Technology (RACT) and RACT Rule 62-296.711 Materials Handling, Sizing, Screening, Crushing and Grinding Operations; because Rule 1-3.51, Particulate Matter Emissions of the HCEPC requires new emissions units to be subject to the Department RACT rule.}

The emissions unit contained in this subsection is comprised of the following:

| Point ID | Brief Description |
| --- | --- |
| FH‐100 | Dozer Stock Pile Operations (unconfined fugitive emissions) |
| FH‐101 | Dozer Operations to Grizzly Hopper (unconfined fugitive emissions) |
| FH‐102 | J3 Conveyor System (enclosed static drop point) |
| FH‐103 | J3 Conveyor System to “K” Feeders to L1 or L2 (enclosed static drop point) |

Performance Restrictions

- Permitted Capacity.  The maximum throughout rate for the J3 Conveyor System shall not exceed 2,000 tons/hour.  [Rules 62-210.200 (PTE), F.A.C.; and, Permit No. 0570039-057-AC]

- Methods of Operation – Materials Handling.  The materials that are allowed to be handled by this emissions unit are coal, coal blends and supplemental coal additives.  [Permit No. 0570039-057-AC]

{Permitting Note:  The materials that have been authorized by prior air construction permits to be handled at the Solid Fuel Yard are coal, petroleum coke, slag, beneficiated flyash, limestone and residual coal (generated at the TEC Polk Power Station).}

- Hours of Operation.  This emissions unit may operate as needed, up to 8,760 hours/year.  [Rule 62-210.200 (PTE), F.A.C. and Permit No. 0570039-057-AC]

Control Technology

- Equipment Enclosure.  All conveyors and conveyor static drop points shall be enclosed to preclude particulate matter emissions.  All covers shall remain in place when the system is in operation and reasonable precautions shall be followed to assure compliance with the opacity limits specified in Condition S.7.  [Permit No. 0570039-057-AC]

- Water Sprays.  Water sprays for storage piles, handling equipment, etc., shall be applied during dry periods and as necessary to all unconfined emissions points to maintain opacity below 20%.  
[Rules 62-4.160(2) & 62-296.320(4)(c), F.A.C.; and Permit No. 0570039-057-AC]

- Minimizing Wind Erosion - Storage Piles.  Best management practices shall be used to minimize unconfined fugitive emissions from coal, coal blends and supplemental coal additives during operation.  Best management practices for coal and supplemental material storage piles include (but are not limited to) shaping, compacting and orienting the piles to minimize wind erosion.  [Permit No. 0570039-057-AC]

Emissions Standards

- VE/Opacity Standards.  Visible emissions shall not exceed 20% opacity for the dozer operations on open storage piles (FH-100 and FH-101) and 5% opacity for the enclosed J3 Conveyor System operations (FH-102 and FH 103).  [Rule 62-296.320(4)(b)1., F.A.C.; and, Rules 1-3.52.1 and 1-3.52.2, Visible Emissions, HCEPC.]

{Permitting Note:  “Unconfined Emissions” are defined in Rule 62-210.200 F.A.C., and Rule 1.3.12 HCEPC, as “Emissions which escape and become airborne from unenclosed operations or which are emitted into the atmosphere without being conducted through a stack.”  Based on this definition, emissions from operations related to the open storage piles (i.e. dozer operations on the storage piles, the open storage piles themselves, and non-fixed drop points from the dozer into the grizzly hopper) are considered unconfined emissions subject only to the general 20% opacity standard.  VE testing is not required for these unconfined fugitive emissions.

The conveyors and static conveyor drop/transfer points are generically subject to 5% opacity.  TECO is able to meet this limit by maintaining the required enclosures and by following best operating practices; therefore, additional add-on PM control devices are not needed.  Because the J3 Conveyor System is fully enclosed with no emissions to the atmosphere, VE testing is not required.}

##### Recordkeeping and Reporting Requirements

- Fugitive Coal Dust Emissions Control Plan.  In accordance with 40 CFR 60, Subpart Y - Standards of Performance for Coal Preparation and Processing Plants, the existing fugitive coal dust emissions control plan on file for this facility must be revised as needed to reflect any changes related to the construction or operation of this new emissions unit.  The revised plan must be submitted to the compliance authority prior to startup of this new unit.  [Rule 62-204.800, F.A.C.; and, 40 CFR 60.254(c)]

Operated by:	Tampa Electric Company

ORIS Code:	0645

Subsection A.  This Subsection addresses Acid Rain, Phase II SO2.

The emissions units listed below are regulated under Phase II SO2 of the federal Acid Rain Program.

| E.U. ID No. | Brief Description |
| --- | --- |
| -001 | Unit No. 1 Steam Generator |
| -002 | Unit No. 2 Steam Generator |
| -003 | Unit No. 3 Steam Generator |
| -004 | Unit No. 4 Steam Generator |

A.1.	The Phase II SO2 Acid Rain Part application submitted for this facility, as approved by the Department, is a part of this permit.  The owners and operators of these Phase II acid rain units must comply with the standard requirements and special provisions set forth in the application(s) listed below:

a.	DEP Form No. 62-210.900(1)(a) - Form, Effective:  3/16/08, received on June 6, 2008, and signed by the Designated Representative on June 5, 2008, which is included at the end of this subsection.

[Chapter 62-213, F.A.C.; and, Rule 62-214.320, F.A.C.]

A.2.	Sulfur dioxide (SO2) Emission Allowances.  SO2 emissions from sources subject to the Federal Acid Rain Program (Title IV) shall not exceed any allowances that the source lawfully holds under the Federal Acid Rain Program.  Allowances shall not be used to demonstrate compliance with a non-Title IV applicable requirement of the Act.

a.	No permit revision shall be required for increases in emissions that are authorized by allowances acquired pursuant to the Federal Acid Rain Program, provided that such increases do not require a permit revision pursuant to Rule 62-213.400(3), F.A.C.

b.	No limit shall be placed on the number of allowances held by the source under the Federal Acid Rain Program.

c.	Allowances shall be accounted for under the Federal Acid Rain Program.

[Rule 62-213.440(1)(c)1., 2. & 3., F.A.C.]

A.3.	Comments, Notes, and Justifications;  None.

Subsection B.  This subsection addresses Acid Rain, Phase II NOx.

{Permitting note:  The U.S. EPA issued Acid Rain Phase I permit(s)}

The emissions units listed below are regulated under Acid Rain Part, Phase II NOx.

| E.U. ID No. | Brief Description |
| --- | --- |
| -001 | Unit No. 1 Steam Generator |
| -002 | Unit No. 2 Steam Generator |
| -003 | Unit No. 3 Steam Generator |
| -004 | Unit No. 4 Steam Generator |

B.1.	The Acid Rain Phase II NOx Compliance Plan application(s) submitted for this facility, as approved by the Department, are a part of this permit.  The owners and operators of these Phase II acid rain unit(s) must comply with the standard requirements and special provisions set forth in the application(s) listed below:

a.	Phase II NOx Compliance Plan, EPA Form 7610-28 (12-03), received on October 7, 2009, and signed by the Designated Representative on October 6, 2009, which is included at the end of this subsection.

[Chapter 62-213 and Rule 62-214.320, F.A.C.]

B.2.  	Nitrogen oxide (NOX) requirements for each Acid Rain unit are as follows:

| E.U. ID No. | EPA ID No. | NOx limit 1 |
| --- | --- | --- |
| -001 | BB01 | The Florida Department of Environmental Protection approves a NOx compliance plan for this unit. The compliance plan is effective for calendar year 2010 through calendar year 2014. This unit’s applicable emission limitation for each year of the plan, is 0.84 lb/MMBtu from 40 CFR 76.6(a)(3) for wet bottom boilers. In addition to the described NOx compliance plan, this unit shall comply with all other applicable requirements of 40 CFR part 76, including the duty to reapply for a NOx compliance plan and the requirements covering excess emissions. |
| -002 | BB02 | The Florida Department of Environmental Protection approves a NOx compliance plan for this unit. The compliance plan is effective for calendar year 2010 through calendar year 2014. This unit’s applicable emission limitation for each year of the plan, is 0.84 lb/MMBtu from 40 CFR 76.6(a)(3) for wet bottom boilers. In addition to the described NOx compliance plan, this unit shall comply with all other applicable requirements of 40 CFR part 76, including the duty to reapply for a NOx compliance plan and the requirements covering excess emissions. |
| -003 | BB03 | The Florida Department of Environmental Protection approves a NOx compliance plan for this unit. The compliance plan is effective for calendar year 2010 through calendar year 2014. This unit’s applicable emission limitation for each year of the plan, is 0.84 lb/MMBtu from 40 CFR 76.6(a)(3) for wet bottom boilers. In addition to the described NOx compliance plan, this unit shall comply with all other applicable requirements of 40 CFR part 76, including the duty to reapply for a NOx compliance plan and the requirements covering excess emissions. |
| E.U. ID No. | EPA ID No. | NOx limit 1 |
| -004 | BB04 | The Florida Department of Environmental Protection approves a NOx compliance plan for this unit. The compliance plan is effective for calendar year 2010 through calendar year 2014. This unit’s applicable emission limitation for each year of the plan, is 0.45 lb/MMBtu from 40 CFR 76.5(a)(1) for tangentially fired boilers. In addition to the described NOx compliance plan, this unit shall comply with all other applicable requirements of 40 CFR part 76, including the duty to reapply for a NOx compliance plan and the requirements covering excess emissions. |

1	Based on the Phase II NOx Compliance Plan, EPA Form 7610-28 (12-03), dated October 6, 2009.

B.3.	Where an applicable requirement of the Act is more stringent than applicable regulations promulgated under Title IV of the Act, both provisions shall be incorporated into the permit and shall be enforceable by the Administrator.  [40 CFR 70.6(a)(1)(ii); and Rule 62-210.200, F.A.C., Definitions – Applicable Requirements.]

B.4.	Comments, Notes, and Justifications;  None.

Clean Air Interstate Rule (CAIR).

Operated by:  Tampa Electric Company

Plant Name:  Big Bend Station

ORIS Code:  0645

Subsection A.  This Subsection addresses CAIR.

The emissions units below are regulated under the Clean Air Interstate Rule.

| E.U. ID No. | EPA Unit ID# | Brief Description |
| --- | --- | --- |
| -001 | BB01 | Unit No. 1 Steam Generator |
| -002 | BB02 | Unit No. 2 Steam Generator |
| -003 | BB03 | Unit No. 3 Steam Generator |
| -004 | BB04 | Unit No. 4 Steam Generator |

- Clean Air Interstate Rule Application.  The Clean Air Interstate Rule Part Form submitted for this facility is a part of this permit.  The owners and operators of these CAIR units as identified in this form must comply with the standard requirements and special provisions set forth in the CAIR Part Form (DEP Form No. 62-210.900(1)(b) - Form, Effective:  3/16/08), which is attached at the end of this subsection.  [Chapter 62-213, F.A.C. and Rule 62-210.200, F.A.C.]

- Comments, notes, and justifications:

  - The “Unit ID#s” on the CAIR Part Form for the existing units were incorrect.  The EPA unit identification numbers under the acid rain program for the existing units have already been established and are shown in the above table.

  - Applications for CAIR retired unit exemptions were submitted subsequent to this CAIR part application.  As a result, this subsection now excludes the retired units.

Subsection B.  This Subsection addresses CAIR Retired Unit Exemptions.

| E.U. ID No. | EPA Unit ID# | Brief Description |
| --- | --- | --- |
| -005 | TBE | Combustion Turbine No. 2 |
| -006 | TBE | Combustion Turbine No. 3 |

“TBE” - to be established

The CT Nos. 2 & 3 (E.U. ID Nos. -005 & -006), were removed from the site on December 22, 2008.  The date of permanent retirement was September 30, 2008.

{Permitting note(s):  CT Nos. 2 & 3 (E.U. ID Nos. -005 & -006) are regulated under Rules 62-296.470, F.A.C., Clean Air Interstate Rule (CAIR) as retired CAIR units.  These emissions units were not regulated under 40 CFR 60, Subpart GG, Standards of Performance for New Stationary Gas Turbines.}

- Clean Air Interstate Rule Retired Unit Exemption Applications.  The Clean Air Interstate Rule Retired Unit Exemption Part Forms submitted for this facility are a part of this permit.  The owners and operators of these CAIR retired units as identified in these forms must comply with the standard requirements and special provisions set forth in the CAIR Retired Unit Exemption Part Forms (EPA Form No. 7610-20 (Rev. 11-2007), which are attached at the end of this subsection.  [Chapter 62-213, F.A.C. and Rule 62-210.200, F.A.C.]

- Comments, notes, and justifications:  The “Unit ID#s” on the forms are the state of Florida’s ARMS E.U. ID Nos.  The EPA “Unit ID#s” are to be established.

Appendix A, Glossary.

Appendix BOP, Best Operational Practices for Start up and Shutdown.

Appendix CAM, Compliance Assurance Monitoring Plan.

Appendix CEMS.

Appendix CEMS for EU 41 and 42.

Appendix CFJ, Consent Final Judgment (DEP vs. TEC).

Appendix CP-1 Compliance Plan.

Appendix 40 CFR 60, Subpart A, General Provisions.

Appendix 40 CFR 60, Subpart Da, Standards of Performance for Fossil-Fuel Fired Steam Generators.

Appendix 40 CFR 60, Subpart IIII, Standards of Performance for Stationary Compression

Ignition Internal Combustion Engines.

Appendix 40 CFR 60, Subpart KKKK, Requirements for Stationary Combustion Turbines

Appendix 40 CFR 60, Subpart OOO, Standards of Performance for Nonmetallic Mineral Processing Plants.

Appendix 40 CFR 63, Subpart A, General Provisions.

Appendix 40 CFR 63, Subpart II, National Emission Standards for Shipbuilding and Ship Repair (Surface

Coating).

Appendix 40 CFR 63, Subpart ZZZZ, National Emissions Standards for Hazardous Air Pollutants for

Stationary Reciprocating Internal Combustion Engines.

Appendix I, List of Insignificant Emissions Units and/or Activities.

Appendix O&M, Operation and Maintenance Plan under RACT for PM.

Appendix RR, Facility-wide Reporting Requirements.

Appendix TR, Facility-wide Testing Requirements.

Appendix TV, Title V General Conditions.

Appendix U, List of Unregulated Emissions Units and/or Activities.