Title V Air Operation Permit Renewal

Permit No. 0570039-067-AV

Applicant

The applicant for this project is Tampa Electric Company (TEC).  The applicant’s responsible official and mailing address are:  Ronald D. Bishop, Director, Tampa Electric Company, Big Bend Station, Post Office Box 111, Tampa, Florida 33601-0111.

Facility Description

The applicant operates the existing Big Bend Station, which is located in Hillsborough County at 13031 Wyandotte Road, Apollo Beach, Florida.

This existing facility consists of:  four fossil fuel fired steam generators, Boiler Unit Nos. 1 through 4; four steam turbines; two simple-cycle combustion turbines (SCCT), Unit Nos. 4A and 4B; solid fuels; fly ash; limestone; gypsum; slag; bottom ash storage and handling facilities; surface coating operations; and fuel oil storage tanks.

Also included in this permit are miscellaneous insignificant emission units and/or activities.

Project DESCRIPTION

The purpose of this permitting project is to revise the existing Title V permit for the above referenced facility which reflects the standards and requirements to be established in the concurrently issued Air Construction Permit No. 0570039-066-AC.  Further details are included in the Technical Evaluation and Preliminary Determination accompanying the draft air construction permit.

Processing Schedule and Related Documents

Application for Air Construction Permit/Title V Air Operation Permit Revision received on September 13, 2013.

Request for Additional Information issued on November 11, 2013.

Request for Additional Information response received on November 27, 2013.

2nd Request for Additional Information issued on December 12, 2013.

Request for an extension to the RAI response requested on March 20, 2014.

Request for Additional Information response received on April 17, 2014.

Primary Regulatory requirements

Standard Industrial Classification (SIC) Code:  4911 – Electrical Generation.

HAP:  The facility is identified as a major source of hazardous air pollutants (HAP).

Title IV:  The facility operates units subject to the acid rain provisions of the Clean Air Act.

Title V:  The facility is a Title V major source of air pollution in accordance with Chapter 62-213, Florida Administrative Code (F.A.C.).

PSD:  The facility is a Prevention of Significant Deterioration (PSD)-major source of air pollution in accordance with Rule 62-212.400, F.A.C.

NSPS:  The facility operates units subject to the New Source Performance Standards (NSPS) of 40 Code of Federal Regulations (CFR) 60.

NESHAP:  The facility operates units subject to the National Emissions Standards for Hazardous Air Pollutants (NESHAP) of 40 CFR 63.

CAIR:  The facility is subject to the Clean Air Interstate Rule (CAIR) set forth in Rule 62-296.470, F.A.C.

Siting:  Unit 4 was originally certified pursuant to the power plant siting provisions of Chapter 62-17, F.A.C. (Power Plant Siting Certification PA 79-12).

CAM:  Compliance Assurance Monitoring (CAM) applies to emissions units at this facility.  CAM applies to Boiler Unit Nos. 1 through 4 (EU 001 – EU 004) for the controlled emissions of particulate matter (PM).  Each unit is equipped with an electrostatic precipitator (ESP) to control PM emissions to meet the emissions limits.  The other emissions units at the facility are not subject to CAM for one or more of the following reasons:  they do not trigger the pre-air pollution control device major source emission thresholds; they demonstrate continuous compliance with a continuous emission monitoring system (CEMS); or, they are not equipped with air pollution control devices.

GHG:  The facility is identified as a major source of green house gas (GHG) pollutants.

PROJECT REVIEW

The permit revision includes the following changes.

- Changes throughout the Title V air operation permit:

- Changed petcoke to petroleum coke.

- Corrected referenced rules and permit numbers.

Table of Contents

- Emission Units and Conditions were updated to reflect changes made throughout the Title V air operation permit.

Section I.  Facility Information

- Subsection A.  Facility Description: Revised to indicate ultra-low sulfur diesel (ULSD) fuel is also fired in the SCCT.

- Subsection B.  Summary of Emission Units:  Revised to show emission units renamed or removed as described below.

- Subsection C.  Applicable Requirements:  Revised by updating the table to reflect changes made throughout the Title V air operation permit.

Section II. Facility-Wide Conditions.

- Revised Condition FW4. (General Visible Emission) to include Hillsborough County Environmental Protection Commission general visible emission requirement.

- Moved Condition D.5. (Unconfined Emissions of Particulate Matter) to Facility-Wide Condition FW5.b. since the truck Loadout and flyash handling and storage were moved to and considered insignificant emission units.

Section III. Emissions Units and Specific Conditions

Some of the revisions made in the section included removing activities and their complete subsection.  However, for easy reference, the subsections listed alphabetically were not changed during this revision.  These changes will be addressed during the Title V renewal permit.

Subsection A. Emission Units 001 – 003

- Revised Condition A.4.c.(1) (Methods of Operation) by moving the “Boiler Chemical Cleaning Waste” activities to “Insignificant Activities” as per Air Construction Permit No. 0570039-058-AC.

- Air Construction Permit No. 0570039-066-AC revised language in Condition A.4.c.(3) (Supplemental Material Injection) for clarity.

- Air Construction Permit No. 0570039-066-AC removed Condition A.5. (FGD Operation for Petcoke and Coal Residual) since the exhaust from these units cannot bypass the flue gas desulfurization (FGD) system.

- Air Construction Permit No. 0570039-066-AC removed Condition A.6. (Limit on Petcoke Bunkering) since these petroleum coke is limited to 20% weight and the exhaust from these units cannot bypass the FGD system.

- Revised Condition A.7. (Selective Catalytic Reduction (SCR) System Operation) by creating a new separate condition for circumvention.  The new condition will read as written in Rule 62-210.650, F.A.C.

- Air Construction Permit No. 0570039-066-AC revised the new Condition A.8. (Circumvention) to read as written in Rule 62-210.650, F.A.C.

- Revised Condition A.25.(2) (Calculation of Emission Rate) by correcting a typo in the numbering.

- Air Construction Permit No. 0570039-066-AC revised Condition A.29. (Monitoring of Petroleum Coke Usage) by removing the monitoring of coal bunkering since the coal bunkering limit was removed.

- Removed obsolete Condition A.38. (Nitrogen Oxide (NOX) Compliance Schedule - Unit No. 1 and 2) and Condition A.39. (NOX Compliance - Unit No. 3) in its entirety since the compliance schedules have been met and these conditions are in duplicate form, see Conditions A.21. and A.22.

- Revised Condition A.41. (Annual Compliance Test) for clarity allowing the NOX and sulfur dioxide (SO2) certified continuous emission monitoring system (CEMS) and annual Relative Accuracy Test Audit (RATA) test data to satisfy annual compliance requirements which will be used to satisfy the compliance test prior to renewal.

- Removed previous Condition A.45. (Compliance Test Prior to Renewal) in its entirety since the annual compliance test now includes the requirement for annual compliance testing to satisfy the compliance test prior to renewal.

- Revised Condition A.50. (Determination of Heat Input) to state that the gross power output will be measured on an arithmetic average during the compliance demonstration test and not on a 4-hour rolling average.  Additionally, the composite fuel samples collected in accordance with American Society for Testing and Materials (ASTM) to industry standard practices.  TEC industry standard practices will be used to collect the samples and ASTM standards are used to analyze the coal samples.  TEC compared the two sampling methods and provided a statistical analysis demonstrating the relative variance between the monthly heat input and boiler efficiency method.  TEC laboratory (NELAP certified laboratory) prepares the composite samples to determine the residual moisture, total moisture, heat content, sulfur content and trace metals.  The method used in the TEC sampling procedures are consistent with the ASTM method, but varied in the frequency and gross sampling procedures.  The statistical analysis showed TEC monthly heat input and the boiler efficiency calculated heat input are statistically equivalent at the 95% confidence interval (t>t'), which shows the variance of the frequency and sample size are not statistically significant.  Based on the information provided by TEC, the Department revised this condition to allow the fuel samples collected to be in accordance with TEC industry standard practices.

- Revised Condition A.52. (PM and VE Compliance Test) by removing requirements to retest Units 1 - 3 if the most recent particulate and visible emission compliance tests were conducted without fly ash re-injection occurring, and fly ash re-injection occurs for any reason other than a malfunction.  The historical stack tests provided by TEC shows the particulate matter emissions have decreased with essentially the same fly ash reinjection feed rate percentage.  This suggests the impact of fly ash on emissions is inconsequential at these reinjection rates and additional testing is not necessary.

- Revised Condition A.53. (Reporting Conditions) by updating the table to reflect the new condition numbers.

- Revised Condition A.57. (Quarterly NOX Report) to state that the report shall contain the heat input weighted 30-day NOX rolling average quarterly report for clarity.

- Revised Condition A.58. (Records of Operation) by removing the requirement for daily recordkeeping showing whether the flue gas was directed to the FGD system.  Units 1 – 3 (EU 001 - EU 003) are fully controlled and the exhaust gas cannot bypass the FGD system.

Subsection B. Emission Unit 004

- Revised Condition B.4.(a) (Methods of Operation) by correcting the units subject to this condition.

- Revised Condition B.4.c.(1) (Methods of Operation) by moving the “Boiler Chemical Cleaning Waste” activities to “Insignificant Activities” as per Air Construction Permit No. 0570039-058-AC.

- Air Construction Permit No. 0570039-066-AC revised language in Condition B.4.c.(3) (Supplemental Material Injection) for clarity.

- Air Construction Permit No. 0570039-066-AC revised Condition B.6. (Circumvention) to read as written in Rule 62-210.650, F.A.C.

- Revised Condition B.11. (SCR System) permitting note to include the date Unit 4 commenced operation.

- Revised the permitting note in Condition B.39. (CO CEMS – Appendix CEMS) for a typo.

- Revised Condition B.44. (Annual Compliance Test) for clarity allowing the NOX and SO2 certified CEMS and annual RATA test data to satisfy annual compliance requirements which will be used in lieu of the compliance test prior to renewal.

- Revised Condition B.54. (Determination of Heat Input) to state that the gross power output will be measured on an arithmetic average during the compliance demonstration test and not on a 4-hour rolling average.  Also, TEC requests that composite fuel samples be collected in accordance with industry standard practices in lieu of American Society for Testing and Materials (ASTM) standards.  Industry standard practices are typically used to collect the samples, and ASTM standards are typically used to analyze the coal samples, see details in No. 17 above.

- Revised Condition B.55. (Reporting Conditions) by updating the table to reflect the new condition numbers.

- Revised Condition B.56. (Quarterly NOX Report) to clarify the quarterly NOX report needs to contain the heat input weighted 30 day NOX rolling average.

Subsection C. Emission Unit 007

- Removed all reference to Combustion Turbine No. 1 since it was removed from service on 10/26/2010.

Subsection D. Emission Units 008, 009, 018, 019, and 026

- Revised the “Emission Unit Brief Description” table to reflect the following changes:  Moved Fly Ash Silo Nos. 1 and 2 Truck Loadout (EU 018 and EU 019) and Fly Ash Handling and Storage Fugitive Emissions (EU 026) to Insignificant Activities and noted in description since TEC no longer conducts truck loading operations except during emergency situations.  Additionally, the truck loadout drop transfer point where the discharge point and receiving point of the materials being handled are intermittently moved in relationship to each other; therefore are exempt from Rule 62-296.700, F.A.C. (Reasonably Available Control Technology (RACT) PM).

- Included Rule 62.296.711, F.A.C. RACT PM (Materials Handling, Sizing, Screening, Crushing and Grinding Operations) in the permitting note identifying that Fly Ash Silo’s and baghouses (EU 008 and EU 009) are regulated under this rule.

- Removed the fly ash handling system from Condition D.4. (Visible Emissions) requirement since the fly ash handling system is no longer part of this section.

- Moved Condition D.5. (Unconfined Emissions of Particulate Matter) to Section II Facility-Wide Conditions since the truck Loadout and fly ash handling and storage are insignificant emission units.

- Revised Condition D.8. (Annual Compliance Test) to allow the annual compliance tests to be used in lieu of the compliance test prior to renewal.

- Removed Condition D.9. (Compliance Test Prior to Renewal) since the annual compliance test for opacity will satisfy the compliance test prior to renewal.

- Removed Condition D.12. (Testing Conditions) since the truck loadout activities have been moved to insignificant activities.

Subsection E. Emission Units 014, 027 and 028

- Revised the “Emission Unit Brief Description” table to reflect the following changes:  Moved Fly Ash Silo No. 3 Truck Loadout (EU 027) and Fly Ash Handling System Fugitive Emissions (EU 028) to Insignificant Activities and noted in description since TEC no longer conducts truck loading operations except during emergency situations.  Additionally, the truck loadout drop transfer point where the discharge point and receiving point of the materials being handled are intermittently moved in relationship to each other; therefore are exempt from Rule 62-296.700, F.A.C. (RACT PM).

- Included Rule 62.296.711, F.A.C. RACT PM (Materials Handling, Sizing, Screening, Crushing and Grinding Operations) and Power Plant Siting Certification [PA 79-12] in the permitting note identifying that Fly Ash Silo baghouse (EU 014) is regulated under this rule and the Power Plant Siting Certification.

- Revised Condition E.1. (Hours of Operation) to read that this condition applies to a single emission unit.

- Air Construction Permit No. 0570039-066-AC revised Condition E.2. (Negative Pressures) since the fly ash handling system is no longer part of this section.

- Air Construction Permit No. 0570039-066-AC revised Condition E.4. (Particulate Matter Emissions) and Condition E.5. (Visible Emissions) to identify the actual emission point and by removing the fly ash handling system since the fly ash handling system is no longer part of this section.

- Revised Condition E.9. (Annual Compliance Test) to allow the annual compliance tests to be used in lieu of the compliance test prior to renewal.

- Removed Condition E.10. (Compliance Test Prior to Renewal) since the annual compliance test for opacity will satisfy the compliance test prior to renewal.

Subsection F. Emission Units 011 – 013, 020, 021, 023, and 025

- Deleted EU 011 (Truck Limestone Unloading Receiving Hopper) since it is fully enclosed and is no longer an emission point.  This was noted in the emission unit description.

- Renamed EUs 012, 013, 020, 021, and 023 to clarify the emission points.  TEC enclosed conveyors LB, LC, LD, LE LF, LG including the transfer points of these conveyors, Silo’s A –C, and Silo C Belt Feeder; therefore are not emission points.  The existing baghouses used to control particulate emissions for this equipment are the regulated emission units.

- Deleted EU 025 (Limestone Storage and Handling Fugitive Emissions) since a fully enclosed bucket elevator and a portable hopper/conveyor system are used as backup system to provide limestone to Silo C.  This was noted in the emission unit description.

- Added a new emission unit (EU 050) by separating the Limestone Conveyor LD/LE Baghouse from Limestone Conveyor LB/LC Baghouse for clarity and convenience.  This new emission unit was added throughout this subsection to identify its applicable requirements.

- Revised Condition F.3. (Best Operational Practices) by removing quarterly inspection requirements since TEC routinely inspects the conveyors, and maintenance is conducted as needed in accordance with best operational practices.

- Reworded Condition F.6. (Operating Procedures) to clarify that the training of operators will meet the training given by TEC.

- Revised Condition F.7. (Particulate Matter and Visible Emissions) to clarify that the baghouses are the emission points and are subject to these emission limits.

- Revised Condition F.12. (Test Methods) by removing the obsolete EPA Test Method 22 since it pertained to the Limestone Storage and Handling Fugitive Emissions (EU 025) that was deleted.

- Revised Condition F.13. (Annual Compliance Tests) by identifying the baghouses only are subject to annual visible emissions testing and that the annual compliance tests will be used in lieu of the compliance test prior to renewal.

- Removed Condition F.14. (Compliance Test Prior to Renewal) since the annual compliance test for opacity will satisfy the compliance test prior to renewal.

- Revised Condition F.16. (Visible Emissions Tests) by removing EU 011 since it is completely enclosed and is not an emission point.

Subsection G. Emission Units 015 – 017, and 039

- The emission unit description was revised to clarify that the Roto clones share a common head space in the blending bin building.

- Revised Condition G.7. (Annual Compliance Test) to allow a different Roto-clone unit (Units 1 – 4) to be tested each year since the building contains a shared head space above the bunkers and the testing on one Roto-clone unit would provide reasonable assurance that the building is meeting the required 5% opacity limit.  The annual compliance tests will be used in lieu of the compliance test prior to renewal.

- Removed Condition G.8. (Compliance Test Prior to Renewal) since the annual compliance test for opacity will satisfy the compliance test prior to renewal.

Subsection H. Emission Unit 010

- Revised the permitting note under the emission unit description to state this emission unit received a determination of Best Available Control Technology (BACT) pursuant to Rule 62-212.400, F.A.C.; therefore, Rule 62-296.700, F.A.C. RACT PM does not apply.

- Revised the table identifying what the solid fuel yard unloading and handling operations Is comprised of and to clarify what is subject to the fugitive visible emissions standard.

- Revised Condition H.5. (Water Sprays) to remove the 5% opacity standard established for confined emission units.  Confined emission points are completely enclosed and no emission point exists as shown in pictures and diagrams provided by TEC.  Additionally, PSD-FL-040 established this condition and did not require a 5% opacity limit.

- Revised Condition H.7. (VE/Opacity Limits) by removing the 5% opacity standard since Rule 62-296.711(2), F.A.C. RACT PM does not apply to this emission unit.  Revised the permitting note clarifying that a VE test is not required on enclosed conveyors, conveyor transfer points and static conveyor drop points.

- Removed Conditions H.11 – H.14 (Test Methods and Procedures) since “Unconfined Emissions” which is defined in Rule 62-210.200 F.A.C., and Rule 1.3.12 HCEPC, as “Emissions which escape and become airborne from unenclosed operations or which are emitted into the atmosphere without being conducted through a stack.”  Based on this definition, emissions from operations related to the open storage piles (i.e. dozer operations on the storage piles, the open storage piles themselves, and non-fixed drop points from the dozer into the grizzly hopper) are considered unconfined emissions subject only to the general 20% opacity standard.  VE testing is not required for these unconfined fugitive emissions.

- Removed Condition H.15. (Daily Fuel Logs) since this condition is in duplicate form.  Units 1 - 4 require a daily log to keep track of the amounts and types of fuels used as well as copies of fuel analyses containing information on sulfur content, ash content and heating values.

Subsection I. Emission Unit 032

- Revised Condition I.11 (Recordkeeping) by removing the requirement to maintain records on a daily basis.

Subsection J. Emission Units 033 and 034

- The Abrasive Blast Booth with Baghouse (EU 033) and the Abrasive Blast Media Storage with Baghouse (EU 034) were deleted in its entirety as requested by TEC since these emission units have been shutdown.  Abrasive blasting is done at another location at this facility and is fully enclosed.  The abrasive blasting activities at this location are minimal and are considered to be an insignificant activity.

Subsection K. Emission Unit 035

- The Surface Coating of Ships (EU 035) was deleted in its entirety as requested by TEC since these activities are no longer conducted.

Subsection L. Emission Unit 022

- Revised Condition L.2. (Operating Procedures) to clarify that the training of operators will meet the training given by TEC.

- Revised Condition L.7. (Annual Compliance Test) to allow the annual compliance tests to be used in lieu of the compliance test prior to renewal.

- Removed Condition L.8. (Compliance Test Prior to Renewal) since the annual compliance test will be used in lieu of the compliance test prior to renewal.

- Removed Condition L.12 (Records) since compliance with periodic monitoring is demonstrated by the annual compliance test and TEC properly trains personnel on all process equipment, including baghouse systems.

Subsection M. Emission Units 037 and 038

- Revised the permitting note following the description of the emission units stating these emission units are also subject to Rule 62-296.711, F.A.C., RACT PM - Materials Handling, Sizing, Screening, Crushing and Grinding Operations as identified in this subsection.

- Revised Condition M.8. (Annual Compliance Test) to allow the annual compliance tests to be used in lieu of the compliance test prior to renewal.

- Removed Condition M.9. (Compliance Test Prior to Renewal) since the annual compliance test for opacity will satisfy the compliance test prior to renewal.

Subsection O. Emission Units 041 and 042

- Revised Condition O.3.b. (Methods of Operation) by correcting a typo (SCCT).

- Air Construction Permit No. 0570039-066-AC revised Condition O.8. (NOX Emissions) consisting of the following revisions:  removed the SCCT NOX emission standard of 42.0 parts per million by volume, dry (ppmvd) at 15% oxygen (O2) and the corresponding state implementation plan (SIP) limit of 51.3 pounds/hour (lb/hour); removed the SIP limit of 32 lb/hour which is equivalent to the existing NOX emission limit of 25 ppmvd at 15% O2 when firing natural gas since compliance with the mass-based (lb/hour) NOX emissions limits (3-run average) are demonstrated by data collected during the required annual RATA; established the NSPS emission standard for NOX of 74 ppmvd when firing fuel oil; and established the NSPS emission standard of 96 ppmvd when operating at less than 75% peak load.  A permitting note was added stating that the 25 ppmvd at 15% O2 is equivalent to 32 lb/hour.

- Air Construction Permit No. 0570039-066-AC revised Condition O.9. (CO Emissions) by removing the carbon monoxide (CO) SIP limits of 9.1 lb/hour and 2.1 lb/hour since compliance with the mass-based (lb/hour) CO emissions limits (3-run average) are demonstrated by data collected during the required RATA.  A permitting note was added stating that these lb/hour limits are equivalent to the existing emission standards in ppmvd.

- Air Construction Permit No. 0570039-066-AC revised Condition O.18. (CEMS) to allow the SCCT to follow the quality assurance procedures in 40 CFR 75 instead of 40 CFR 60 for the CO CEMS.

- Air Construction Permit No. 0570039-066-AC revised Condition O.24. (Annual Compliance Test) to allow the SCCT to only perform a visible emissions test if the units fired ULSD fuel for more than 400 hours/year.

- Revised Condition O.25. (Compliance Test Prior to Renewal) to require the SCCT to perform a visible emissions test prior to renewal of the air operation permit if the SCCT did not fire ULSD fuel for more than 400 hours/year.

- Revised Condition O.30. (NSPS Compliance Demonstrations for Sulfur) by correcting a typo (SCCT).

- Revised Condition O.32. (Reporting Schedule) by correcting the related condition numbers and remove the notification of tuning.

- Removed Condition O.36. (Notification of Tuning) that requires TEC notify the Compliance Authority at least one working day prior to a planned tuning activity if excess emissions could reasonably be expected to occur.

- Revised Condition O.37. (Monitoring and Recording of Capacity) by correcting a typo (SCCT).

- Air Construction Permit No. 0570039-066-AC added a new Condition O.40. for an existing combustion turbine to be temporarily replaced with a “like-kind” combustion turbine while the existing combustion turbine is undergoing routine maintenance.

Subsection P. Emission Units 029 and 030

- Revised Condition P.10. (Annual Compliance Test) to allow a different Roto clone for each EU 029 (FH-032 - FH-035) and EU 030 (FH-048/FH-049) to be tested each year.  The building contains a shared head space above the conveyors and the testing of one Roto clone will show compliance with the emission unit.  The annual compliance tests will be used in lieu of the compliance test prior to renewal.

- Removed Condition P.11. (Compliance Test Prior to Renewal) since the annual compliance test for opacity will satisfy the compliance test prior to renewal.

- Removed Condition P.13. (Reserved).

- Removed Condition P.15. (Fuel Daily Log) since Units 1 – 4 (EU 001 – EU 004) maintain the fuel bunkering records.

Subsection Q. Emission Unit 046

- Revised the description and emission points of the solid fuel yard to accurately reflect the loading operations.

- Revised the permitting note by updating the rules and regulations the emission unit is subject to.

- Revised by updating the table identifying what EU 046 is comprised of.

- Revised Condition Q.1. (Permitted Capacity) to reflect the specific conditions established in Air Construction Permit No. 0570039-059-AC for the maximum solid fuels/slag transloading rate for all solid fuel and slag materials transloaded onto trucks, railcars and barges for shipment off-site.

- Remove Condition Q.2. (Emissions Unit Operating Rate Limitation after Testing) to reflect the changes made in Air Construction Permit No. 0570039-059-AC, which requires only a general visible emissions opacity limit of 20%.

- Replaced Condition Q.4. (Controls of Particulate Matter) with Reasonable Precautions to Prevent Unconfined Particulate Matter Emissions as established in Air Construction Permit No. 0570039-059-AC.

- Removed Condition Q.5. (Visible Emissions), Condition Q.6. (Excess Emissions Allowed), Condition Q.7. (Excess Emission Prohibited), Condition Q.8. (Test Methods), Condition Q.9. (Common Testing Requirements), Condition Q.10. (Annual Compliance Tests), Condition Q.11. (Compliance Test Prior to Renewal), and Condition Q.12. (Visible Emissions Test) as per Air Construction Permit No. 0570039-059-AC.

- Air Construction Permit No. 0570039-066-AC revised Condition Q.5. (Recordkeeping and Reporting) to clarify how the material is transported off-site.

Subsection R. Emission Unit 047

- The following revisions were made to the emission unit description:  revised the emission unit description to match the current activities; add a permitting note identifying the regulations EU 047 is subject to; removed the language “emission points”; and added a permitting note following the table to clarify actual emission points in this process.

- Air Construction Permit No. 0570039-066-AC revised Condition R.1. (Permitted Capacity) by removing the railcar unloading and conveying system transport rate averaging time.

- Air Construction Permit No. 0570039-066-AC revised Condition R.5. (Railcar Coal Unloading Building) to allow the water spray system or the chemical dust suppression system to control PM emission from the railcar unloading hopper.

- Air Construction Permit No. 0570039-066-AC revised Condition R.6. (Railcar Coal Unloading Conveying System) to allow the water spray system or the chemical dust suppression system to control PM emission from the railcar unloading conveyor system.

- Revised Condition R.10. (Test Methods) by correcting the name of test Method 9 for visible emissions.

Subsection S. Emission Unit 048

- Added the Supplemental Material Handling J3 Convey System (EU 048) as per Air Construction Permit No. 0570039-057-AC.

Appendices

- Appendix CEMS for E.U. ID Nos. -041 and -042.  Air Construction Permit No. 0570039-066-AC revised the quality assurance procedures for the CO CEMS to meet 40 CFR 75 instead of 40 CFR 60.  In addition, the quarterly excess emissions report will be required only if the units operate more than 760 hours.  The excess emissions report identifies the monitor availability when the CEMS are not achieving 95% availability.

- Appendix I, List of Insignificant Emissions Units and/or Activities.  Updated the Insignificant Activities to include:  the engines on site and their rules; Fly Ash Silo Nos. 1 and 2 Truck Loadout (EU 018 and EU 019); Fly Ash Handling and Storage Fugitive Emissions (EU 026); Fly Ash Silo No. 3 Truck Loadout (EU 027); Fly Ash Handling System Fugitive Emissions (EU 028); an administrative correction to the Five Induced Draft Cooling Towers for each of Units 1, 2, 3, 4, and the FGD Area table; evaporation up to 300,000 gallons/year of boiler cleaning waste generated onsite; and the abrasive blasting area.

Conclusion

This project revises Title V air operation permit No. 0570039-61-AV, which was effective on April 10, 2013.  The renewed Title V air operation permit No. 0570039-039-AV was effective January 1, 2010.  This Title V air operation permit revision is issued under the provisions of Chapter 403, Florida Statues (F.S.), and Chapters 62-4, 62-210, 62-213, F.A.C.