## EU 001 & 002
Table 1, Summary of Air Pollutant Standards and Terms
Hillsborough County Resource Recovery Facility |  |  |  |  | Final Permit No. 0570261-017-AV
Hillsborough County Resource Recovery Facility |  |  |  |  | Facility ID No. 0570261
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
001 | Municipal Waste Combustor Unit 1
002 | Municipal Waste Combustor Unit 2
003 | Municipal Waste Combustor Unit 3
The following apply to each individual emissions unit
Pollutant Name |  |  | Allowable Emissions |  |  | Equivalent Emissions*
or Parameter | Fuel(s) | Hours/Year | Standard(s) | lbs./hour | TPY | lbs./hour | TPY | Regulatory Citation(s) | See permit condition(s)
PM | MSW | 8760 | 25 mg/dscm, corrected to 7% O2 |  |  | 3.8 | 16.63 | 40 CFR 60.33b(a)(1)(i) & PSD-FL-121C | III.A.112.
VE (opacity) | MSW | 8760 | 10%, 6-minute average |  |  | N/A | N/A | 40 CFR 60.33b(a)(1)(iii) & PSD-FL-121C | III.A.123.
Cd | MSW | 8760 | 35 ug/dscm, corrected to 7% O2 |  |  | 5.3 x 10-3 | 0.023 | 40 CFR 60.33b(a)(2)(i) | III.A.134.
Hg** | MSW | 8760 | 50 ug/dscm, corrected to 7% O2 or 85% reduction by weight 1 |  |  | 0.014 | 0.062 | 40 CFR 60.33b(a)(3) & PSD-FL-121C | III.A.145.
| BS 2 |  | Mercury emissions from MWC Units 1, 2, 3 and 4 combined shall not exceed 7.1 pounds per 24-hour period when combusting sewage sludge biosolids. | 7.1 |  |  |  | 40 CFR 60.33b(a)(3) & Permit No. 0570261-016-AC/PSD-FL-121E and PSD-FL-369D | III.A.15.
Pb | MSW | 8760 | 400 ug/dscm, corrected to 7% O2 |  |  | 0.059 | 0.262 | 40 CFR 60.33b(a)(4) & PSD-FL-121C | III.A.156.
SO2 | MSW | 8760 | 29 ppmvd, corrected to 7% O2, 24-hour daily geometric mean or |  |  | 32.86 | 143.9 | 40 CFR 60.33b(b)(3)(i) & PSD-FL-121C | III.A.167.
|  |  | 80% reduction by weight or volume 1 |  |  |  |  | " | "
HCl | MSW | 8760 | 25 ppmvd, corrected to 7% O2 or |  |  | 17 | 74.43 | 40 CFR 60.33b(b)(3)(ii) & PSD-FL-121C | III.A.178.
|  |  | 95% reduction by weight or volume 1 |  |  |  |  | " | "
Dioxin/Furan | MSW | 8760 | 30 ng/dscm, corrected to 7% O2 |  |  | 4.5 x 10-6 | 1.96 x 10-5 | 40 CFR 60.33b(c)(1)(iii) & PSD-FL-121C | III.A.189.
NOx | MSW | 8760 | 180 ppmvd, corrected to 7% O2, 24-hour daily arithmetic average |  |  | 58.63 | 256 | 40 CFR 60.33b(d) & PSD-FL-121C | III.A.1920
CO | MSW | 8760 | 100 ppmvd, corrected to 7% O2, 4-hour block average |  |  | 17.4 | 76.26 | 40 CFR 60.34b(a) & PSD-FL-121C | III.A.201.
VE - fugitive ash emissions |  | 8760 | 5% of the observation period (i.e., 9 minutes per 3-hour period) |  |  | N/A | N/A | 40 CFR 60.36b | III.A.212.
O2/CO2 | MSW | 8760 | N/A |  |  | N/A | N/A | 40 CFR 60.38b | III.A.301.
** Mercury emissions from MWC Units 1, 2, 3 and 4 combined shall not exceed 7.1 pounds per 24-hour period when combusting sewage sludge biosolids.
[Permit No. 0570261-016-AC/PSD-FL-121E and PSD-FL-369D, Specific Condition 7.]
Notes:
"N/A" represents not applicable.
* The "Equivalent Emissions" listed are for informational purposes only. The "lbs./hour" equivalent emission values are based on a stack gas flow rate of 53,000 dscfm.
1 Whichever is least stringent.
2 Biosolids

## EU 107
Table 1, Summary of Air Pollutant Standards and Terms
Hillsborough County |  |  |  |  | Final Permit No. 0570261-017-AV
Hillsborough County Resource Recovery Facility |  |  |  |  | Facility ID No. 0570261
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
107 | Municipal Waste Combustor Unit 4
Pollutant Name |  |  | Allowable Emissions |  |  | Equivalent Emissions*
or Parameter | Fuel(s) | Hours/Year | Standard(s) | lbs./hour | TPY | lbs./hour | TPY | Regulatory Citation(s) | See permit condition(s)
PM/PM10 | MSW | 8760 | 12.0 mg/dscm, corrected to 7% O2 | 3.3 |  |  | 14.45 | 40 CFR 60.52b(a)(1)(ii) & PSD-FL-369 | III.B.910.&167.
VE (opacity) | MSW | 8760 | 10%, 6-minute average |  |  | N/A | N/A | 40 CFR 60.52b(a)(2) & PSD-FL-369 | III.B.910.&178.
Cd | MSW | 8760 | 10 ug/dscm, corrected to 7% O2 |  |  |  |  | 40 CFR 60.52b(a)(3)(ii) & PSD-FL-369 | III.B.910.
Hg ** | MSW | 8760 | 28 ug/dscm, corrected to 7% O2 or 85% reduction by weight 1 | 0.022 |  |  | 0.1 | 40 CFR 60.52b(a)(5)(ii) & PSD-FL-369 | III.B.910.
| BS 2 |  | Mercury emissions from MWC Units 1, 2, 3 and 4 combined shall not exceed 7.1 pounds per 24-hour period when combusting sewage sludge biosolids. | 7.1 |  |  |  | Rule 62-212.400(12) (Source Obligation, escape PSD BACT), F.A.C. & Permit No. 0570261-016-AC/PSD-FL-121E and PSD-FL-369D, Specific Condition 7 | III.B.15.
Pb | MSW | 8760 | 140 ug/dscm, corrected to 7% O2 |  |  |  |  | 40 CFR 60.52b(a)(4)(ii) & PSD-FL-369 | III.B.910.
SO2 | MSW | 8760 | 26 ppmvd, corrected to 7% O2 or | 19.2 |  |  | 84.1 | 40 CFR 60.52b(b)(1) & PSD-FL-369 | III.B.910.&123.
|  |  | 80% reduction by weight or volume, 24-hour daily geometric mean 1 |  |  |  |  | 40 CFR 60.52b(b)(1) & PSD-FL-151E | "
HCl | MSW | 8760 | 25 ppmvd, corrected to 7% O2 or | 25.4 |  |  | 111.25 | 40 CFR 60.52b(b)(2) & PSD-FL-369 | III.B.910.&134.
|  |  | 95% reduction by weight or volume 1 |  |  |  |  | " | "
Dioxin/Furan | MSW | 8760 | 13 ng/dscm, corrected to 7% O2 | 3.61 x 10-6 |  |  | 1.58 x 10-5 | 40 CFR 60.52b(c)(1) & PSD-FL-369 | III.B.910.&156.
NOx | MSW | 8760 | 110 ppmvd, corrected to 7% O2, 24-hour average | 58.5 |  |  |  | 40 CFR 60.52b(d) & PSD-FL-369 | III.B.910.&101.
NOx | MSW | 8760 | 90 ppmvd, corrected to 7% O2, 12-month rolling average | 47.9 |  |  | 209.8 | PSD-FL-369 | "
CO | MSW | 8760 | 100 ppmvd, corrected to 7% O2, 4-hour block average | 32.4 |  |  |  | 40 CFR 60.53b(a) & PSD-FL-369 | III.B.910.&112.
CO | MSW | 8760 | 80 ppmvd, corrected to 7% O2, 30-day rolling average | 25.9 |  |  | 113.4 | PSD-FL-369 | "
ammonia slip | MSW | 8760 | @195 MMBtu/hr: 10 ppmvd; @260 MMBtu/hr: 15 ppmvd; corrected to 7% O2 |  |  |  |  | PSD-FL-151E | III.B.910.
VE - fugitive ash emissions |  | 8760 | 5% of the observation period (i.e., 9 minutes per 3-hour period) |  |  | N/A | N/A | 40 CFR 60.55b | III.B.910.
O2/CO2 | MSW | 8760 | N/A |  |  | N/A | N/A | 40 CFR 60.58b(b) | III.B.289.d.&2930.
** Mercury emissions from MWC Units 1, 2, 3 and 4 combined shall not exceed 7.1 pounds per 24-hour period when combusting sewage sludge biosolids.
[Permit No. 0570261-016-AC/PSD-FL-121E and PSD-FL-369D, Specific Condition 7.]
Notes:
"N/A" represents not applicable.
* The "Equivalent Emissions" listed are for informational purposes only. The "lbs./hour" equivalent emission values are based on a stack gas flow rate of 73,061 dscfm.
1 Whichever is least stringent.
2 Biosolids

## EU 100 & 112
Table 1, Summary of Air Pollutant Standards and Terms
Hillsborough County |  |  |  |  | Final Permit No. 0570261-017-AV
Hillsborough County Resource Recovery Facility |  |  |  |  | Facility ID No. 0570261
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
100 | Ash Building and Handling System - Baghouse
112 | Ash Building and Handling System - Wet Scrubber
Pollutant Name |  |  | Allowable Emissions |  |  | Equivalent Emissions*
or Parameter | Fuel(s) | Hours/Year | Standard(s) | lbs./hour | TPY | lbs./hour | TPY | Regulatory Citation(s) | See permit condition(s)
100 PM |  |  |  | 1.63 |  |  | 7.14 | 0570261-002-AC/PSD-FL-121C | III.C.4.
100 VE |  |  | 5% |  |  |  |  | PSD-FL-121C & Rule 62-297.620(4), F.A.C. | III.C.5.
112 PM |  |  |  | 0.066 |  |  | 0.29 | 0570261-007-AC/PSD-FL-369 | III.C.6.
112 VE |  |  | 5% |  |  |  |  | PSD-FL-369 & Rule 62-297.620(4), F.A.C. | III.C.6.
VE (ash handling building) |  |  | 5% of the observation period (i.e., 9 minutes per 3-hour period) |  |  |  |  | 40 CFR 60.36b | III.C.8.
Notes:
* The "Equivalent Emissions" listed are for informational purposes only.

## EU 101, 102, 108 & 110
Table 1, Summary of Air Pollutant Standards and Terms
Hillsborough County |  |  |  |  | Final Permit No. 0570261-017-AV
Hillsborough County Resource Recovery Facility |  |  |  |  | Facility ID No. 0570261
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
101 | Pebble Lime Storage Silo - MWC Units 1, 2 & 3
102 | Activated Carbon Storage Silo - MWC Units 1, 2 & 3
108 | Pebble Lime Storage Silo - MWC Unit 4
110 | Activated Carbon Storage Silo - MWC Unit 4
Pollutant Name |  |  | Allowable Emissions |  |  | Equivalent Emissions*
or Parameter | Fuel(s) | Hours/Year | Standard(s) | lbs./hour | TPY | lbs./hour | TPY | Regulatory Citation(s) | See permit condition(s)
101 PM |  | 8760 | 0.015 gr/dscf |  |  | 0.96 | 4.22 | 0570261-002-AC/PSD-FL-121C | III.D.3.
101 VE |  |  | 5% |  |  |  |  | PSD-FL-121C & Rule 62-297.620(4), F.A.C. | III.D.4.
102 PM |  | 8760 | 0.015 gr/dscf |  |  | 0.96 | 4.22 | 0570261-002-AC/PSD-FL-121C | III.D.3.
102 VE |  |  | 5% |  |  |  |  | PSD-FL-121C & Rule 62-297.620(4), F.A.C. | III.D.4.
108 PM |  | 8760 | 0.015 gr/dscf |  |  | 2.11 x 10-6 | 5.67 x 10-4 | 0570261-007-AC/PSD-FL-369 | III.D.3.
108 VE |  |  | 5% |  |  |  |  | PSD-FL-369 & Rule 62-297.620(4), F.A.C. | III.D.4.
110 PM |  | 8760 | 0.015 gr/dscf |  |  | 6.21 x 10-7 | 1.62 x 10-4 | 0570261-007-AC/PSD-FL-369 | III.D.3.
110 VE |  |  | 5% |  |  |  |  | PSD-FL-369 & Rule 62-297.620(4), F.A.C. | III.D.4.
Notes:
* The "Equivalent Emissions" listed are for informational purposes only.