## EU 001 & 002
Table 2, Summary of Compliance Requirements
Hillsborough County Resource Recovery Facility |  |  |  |  | Final Permit No. 0570261-017-AV
Hillsborough County Resource Recovery Facility |  |  |  |  | Facility ID No. 0570261
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
001 | Municipal Waste Combustor Unit 1
002 | Municipal Waste Combustor Unit 2
003 | Municipal Waste Combustor Unit 3
|  |  | Testing | Frequency | Min. Compliance
Pollutant Name |  | Compliance | Time | Base | Test
or Parameter | Fuel(s) | Method | Frequency | Date * | Duration | CMS 1 | Regulatory Citation(s) | See permit condition(s)
PM | MSW | EPA Methods 5 | CY, 5 in 5-year period |  | 3 1-hour test runs | No | 40 CFR 60.58b(c)(9) | III.A.334.-389.
VE (opacity) | MSW | EPA Method 9 or COMS | CY, 5 in 5-year period (COMS) |  | 1-hour test | Yes | 40 CFR 60.58b(c)(8) & Rule 62-297.310(7)(a)4., F.A.C. | III.A.334.-389.
Cd | MSW | EPA Method 29 | CY, 5 in 5-year period |  | 3 1-hour test runs | No | 40 CFR 60.58b(d)(1)(vii) | III.A.334.-389.
Hg | MSW | EPA Method 29 | CY, 5 in 5-year period |  | 3 1-hour test runs | No | 40 CFR 60.58b(d)(2) | III.A.334.-389.
Pb | MSW | EPA Method 29 | CY, 5 in 5-year period |  | 3 1-hour test runs | No | 40 CFR 60.58b(d)(1)(vii) | III.A.334.-389.
SO2 | MSW | CEMS | daily (CEMS) |  | 24-hour daily geometric mean | Yes | 40 CFR 60.58b(e)(4) | III.A.334.-3840.
HCl | MSW | EPA Method 26 or 26A | annual 3 |  | 1-hour | No | 40 CFR 60.58b(f)(7) | III.A.334.-389.
Dioxin/Furan | MSW | EPA Method 23 | CY, 5 in 5-year period 4 |  | 4-hours | No | 40 CFR 60.58b(g)(i)-(iii) | III.A.334.-389.
NOx | MSW | CEMS | daily (CEMS) |  | 24-hour daily arithmetic average | Yes | 40 CFR 60.58b(h)(3) | III.A.334.-3840.
CO | MSW | CEMS | daily (CEMS) |  | 4-hour block average | Yes | 40 CFR 60.58b(i)(3) | III.A.334.-3840.
VE - fugitive ash emissions |  | EPA Method 22 | annual 3 |  | 3 1-hour observations | No | 40 CFR 60.58b(k) | III.A.334.-389.
O2/CO2 | MSW | Method 3, 3A, or 3B, or as an alternative ASME PTC-19-10-1981-Part 10 | N/A |  | N/A | Yes | 40 CFR 60.58b(b) | III.A.301.
steam flow | MSW |  | N/A |  | N/A | Yes | 40 CFR 60.58b(i)(6) | III.A.267.
inlet temperature to baghouse |  |  | N/A |  | N/A | Yes | 40 CFR 60.58b(i)(7) | III.A.278.
Notes:
"N/A" represents not applicable.
"CY" represents calendar year.
* The frequency base date is established for planning purposes only; see Rule 62-297.310, F.A.C.
1 CMS [=] continuous monitoring system.
3 The CFR contained an error on testing frequency per the 01/22/2009 dated e-mail from U.S. EPA.
4 Test at least one MWC unit annually, subject to 40 CFR 60.58b(g) requirements.

## EU 107
Table 2, Summary of Compliance Requirements
Hillsborough County |  |  |  |  | Final Permit No. 0570261-017-AV
Hillsborough County Resource Recovery Facility |  |  |  |  | Facility ID No. 0570261
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
107 | Municipal Waste Combustor Unit 4
|  |  | Testing | Frequency | Min. Compliance
Pollutant Name |  | Compliance | Time | Base | Test
or Parameter | Fuel(s) | Method | Frequency | Date * | Duration | CMS 1 | Regulatory Citation(s) | See permit condition(s)
PM/PM10 | MSW | EPA Method 5, 201 or 201A | CY, 5 in 5-year period |  | 3 1-hour test runs | No | 40 CFR 60.58b(c)(9) | III.B.356.-3940.
VE (opacity) | MSW | EPA Method 9 or COMS | CY, 5 in 5-year period (COMS) |  | 1-hour test | Yes | 40 CFR 60.58b(c)(8) & Rule 62-297.310(7)(a)4., F.A.C. | III.B.356.-3940.
Cd | MSW | EPA Method 29 | CY, 5 in 5-year period |  | 3 1-hour test runs | No | 40 CFR 60.58b(d)(1)(vii) | III.B.356.-3940.
Hg | MSW | EPA Method 29 | CY, 5 in 5-year period |  | 3 1-hour test runs | Yes | 40 CFR 60.58b(d)(2) | III.B.356.-3940.
Pb | MSW | EPA Method 29 | CY, 5 in 5-year period |  | 3 1-hour test runs | No | 40 CFR 60.58b(d)(1)(vii) | III.B.356.-3940.
SO2 | MSW | CEMS | daily (CEMS) |  | 24-hour daily geometric mean | Yes | 40 CFR 60.58b(e)(4) | III.B.356.-3940.
HCl | MSW | EPA Method 26 or 26A | annual 3 |  | 1-hour | No | 40 CFR 60.58b(f)(7) | III.B.356.-3940.
Dioxin/Furan | MSW | EPA Method 23 | CY, 5 in 5-year period 4 |  | 4-hours | No | 40 CFR 60.58b(g)(i)-(iii) | III.B.356.-3940.
NOx | MSW | CEMS | daily (CEMS) |  | 24-hour daily arithmetic average | Yes | 40 CFR 60.58b(h)(3) | III.B.356.-3940.
CO | MSW | CEMS | daily (CEMS) |  | 4-hour block average | Yes | 40 CFR 60.58b(i)(3) | III.B.356.-3940.
ammonia slip | MSW | EPA Method CTM-027 (Conditional Test Method) | annual |  | 3 1-hour test runs |  | PSD-FL-369 | III.B.356.-3940.
III.B.356.-3940.
VE - fugitive ash emissions |  | EPA Method 22 | annual 3 |  | 3 1-hour observations | No | 40 CFR 60.58b(k) | III.B.356.-3940.
O2/CO2 | MSW | Method 3, 3A, or 3B, or as an alternative ASME PTC-19-10-1981-Part 10 | N/A |  | N/A | Yes | 40 CFR 60.58b(b) | III.B.289.d.&2930.
steam flow | MSW |  | N/A |  | N/A | Yes | 40 CFR 60.58b(i)(6) | III.B.256.
inlet temperature to baghouse |  |  | N/A |  | N/A | Yes | 40 CFR 60.58b(i)(7) | III.B.267.
Notes:
"N/A" represents not applicable.
"CY" represents calendar year.
* The frequency base date is established for planning purposes only; see Rule 62-297.310, F.A.C.
1 CMS [=] continuous monitoring system.
3 The CFR contained an error on testing frequency per the 01/22/2009 dated e-mail from U.S. EPA.
4 Test at least one MWC unit annually, subject to 40 CFR 60.58b(g) requirements.

## EU 100 & 112
Table 2, Summary of Compliance Requirements
Hillsborough County |  |  |  |  | Final Permit No. 0570261-017-AV
Hillsborough County Resource Recovery Facility |  |  |  |  | Facility ID No. 0570261
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
100 | Ash Building and Handling System - Baghouse
112 | Ash Building and Handling System - Wet Scrubber
|  |  | Testing | Frequency | Min. Compliance
Pollutant Name |  | Compliance | Time | Base | Test
or Parameter | Fuel(s) | Method | Frequency | Date * | Duration | CMS** | See permit condition(s)
PM |  | EPA Method 5 | waived |  |  | none | III.C.13.-16.
VE |  | EPA Method 9 | annual |  | 30 minutes | none | "
VE (ash handling building) |  | EPA Method 22 | annual |  | 3 1-hour observations | none | "
Notes:
* The frequency base date is established for planning purposes only; see Rule 62-297.310, F.A.C.
**CMS [=] continuous monitoring system.

## EU 101, 102, 108 & 110
Table 2, Summary of Compliance Requirements
Hillsborough County |  |  |  |  | Final Permit No. 0570261-017-AV
Hillsborough County Resource Recovery Facility |  |  |  |  | Facility ID No. 0570261
This table summarizes information for convenience purposes only. This table does not supersede any of the terms or conditions of this permit.
E.U. ID No. | Brief Description
101 | Pebble Lime Storage Silo - MWC Units 1, 2 & 3
102 | Activated Carbon Storage Silo - MWC Units 1, 2 & 3
108 | Pebble Lime Storage Silo - MWC Unit 4
110 | Activated Carbon Storage Silo - MWC Unit 4
|  |  | Testing | Frequency | Min. Compliance
Pollutant Name |  | Compliance | Time | Base | Test
or Parameter | Fuel(s) | Method | Frequency | Date * | Duration | CMS** | See permit condition(s)
PM |  | EPA Method 5 | waived |  |  | none | III.D.9.-14.
VE |  | EPA Method 9 | annual |  | 30 minutes | none | III.D.9.-14.
Notes:
* The frequency base date is established for planning purposes only; see Rule 62-297.310, F.A.C.
**CMS [=] continuous monitoring system.