Title V Air Operation Permit Renewal

Permit No. 0850001-042-AV

Applicant

The applicant for this project is Florida Power and Light Company.  The applicant’s responsible official and mailing address are:  Jeff Smith, Martin Plant Regional General Manager, Florida Power and Light Company, Martin Power Plant, 21900 SW Warfield Blvd, Stuart, FL 34956.

Facility Description

The applicant operates the existing Martin Power Plant, which is located in Martin County at 21900 SW Warfield Blvd, Indiantown, Florida.

The facility primarily consists of two natural gas and oil-fired steam electric generating units (Units 1 and 2), two pairs of oil and natural gas fired combined cycle combustion turbine (CCCT)-electrical generators (Units 3 and 4) with unfired heat recovery steam generators (HRSGs) and Unit 8, which is an arrangement of 4 CCCT-electrical generators, each with a gas-fired HRSG, that serve a single steam turbine-electrical generator.  Ancillary equipment includes one auxiliary boiler, emergency generators, four hurricane shelter stationary spark ignition, engine driven generators, two oil storage tanks, a mechanical cooling tower and four electrical fuel line heaters (to heat up the natural gas prior to introduction into the combustion turbines, when needed).

Units 1 and 2 are identical fossil fuel-fired steam generators.  Each steam generator has a capacity of 863.3 megawatts (MW) and maximum heat input rates of 8,650 million Btu per hour (MMBtu/hr) while firing oil and 9,040 MMBtu/hr while firing natural gas.  Nitrogen oxide (NOX) emissions are controlled with low NOX, dual firing burners.  Particulate matter (PM) emissions are controlled with dry electrostatic precipitators (ESPs) with fly ash reinjection.  Sulfur dioxide (SO2) and NOX emissions are monitored using a continuous emissions monitoring system (CEMS) and visible emissions are monitored with a continuous opacity monitoring system (COMS).

Units 3 and 4 consist of four identical General Electric (GE) Model No. MS7001, Frame FA CCCTs.  Each unit consists of two CCCT-electrical generators, each with an unfired HRSG, coupled to a single steam turbine (2-on-1 set).  Each CCCT-electrical generator and steam turbine-electrical generator have nominal generating capacities of 170 MW and 160 MW, respectively, for a generating capacity of approximately 500 MW per unit (1000 MW total).  The maximum heat input rate of each CCCT is 1,966 MMBtu/hr while firing natural gas and 1,846 MMBtu/hr while firing fuel oil.  Each CCCT is equipped with inlet foggers at the compressor inlet to improve the power and heat rate of the CCCTs by providing cool, dense air at the inlet.  Dry low NOX burners are used to control NOX emissions.  Steam injection is used for power augmentation and NOX control while firing fuel oil.  Duct modules are installed on each unit for the potential future installation of selective catalytic reduction (SCR) equipment for NOX control.  SO2 emissions are controlled by firing pipeline natural gas and low sulfur fuel oil.  NOX emissions are monitored using a CEMS.

Unit 8 consists of four GE Model PG7241 Frame FA CCCT-electrical generators, each with a natural gas-fired HRSG, coupled to a single steam turbine-electrical generator (4-on-1 set).  Each CCCT-electrical generator has a nominal generating capacity of 207.6 MW.  The steam turbine-electrical generator has a nominal generating capacity of 470 MW, for a combined total of approximately 1,300.4 MW for Unit 8.  The maximum heat input rate of each CCCT is 1,660 MMBtu/hr while firing natural gas and 1,885 MMBtu/hr while firing distillate oil, based on a compressor inlet temperature of 59 degrees Fahrenheit, the lower heating value (LHV) of each fuel and 100% load.  Each HRSG has a maximum heat input rate of 495 MMBtu/hr, based on the LHV of natural gas.  Inlet fogging is used to provide evaporative cooling, reduce compressor inlet air temperature and provide additional direct power.  There is also a solar thermal facility on-site that produces steam, which is used to augment the steam produced by the Unit 8 HRSGs, thus reducing fossil fuel use in the duct burners when adequate sunlight is available.  NOX emissions are controlled by a GE Dry Low NOX 2.6 combustion system while firing natural gas and water injection while firing distillate oil.  SCR is used for NOX control while firing natural gas and distillate oil in combined cycle mode.  Carbon monoxide (CO) and volatile organic compound emissions are controlled using high combustion temperature.  SO2 and sulfuric acid mist are controlled by only firing low sulfur fuel oil and natural gas.  CO and NOX emissions are monitored using a CEMS.

The auxiliary boiler consists of a Vapor Circulatic Model VG-5907-SHK-350 natural gas fired boiler.  The boiler produces steam to actuate the steam seals on the steam turbine components for Units 3 and 4 during cold starts when steam is not available for this purpose.  The maximum heat input rate of this unit is 13.23 MMBtu/hr, which is the combined heat input of the boiler (11.73 MMBtu/hr) and super heater (1.5 MMBtu/hr), while firing natural gas.  PM and SO2 emissions are controlled by only firing natural gas.  Operation of this unit is limited to operation only during startup and shutdown of Units 3 and 4 and periodic maintenance testing.

This facility also includes miscellaneous unregulated/insignificant emissions units and/or activities.

regulated Emissions Unit IDentification Numbers and descriptions

| EU No. | ## Brief Description |
| --- | --- |
| Regulated Emissions Units |  |
| 001 | Fossil Fuel Fired Steam Generator No. 1 |
| 002 | Fossil Fuel Fired Steam Generator No. 2 |
| 003 | CT with HRSG (CT 3A) |
| 004 | CT with HRSG (CT 3B) |
| 005 | CT with HRSG (CT 4A) |
| 006 | CT with HRSG (CT 4B) |
| 011 | CT with HRSG (CT 8A) |
| 012 | CT with HRSG (CT 8B) |
| 014 | Two Distillate Oil Storage Tanks for Unit 8 Gas Turbines |
| 017 | CT with HRSG (CT 8C) |
| 018 | CT with HRSG (CT 8D) |
| 019 | Mechanical Draft Cooling Tower for Unit 8 |
| 022 | One Diesel Engine-driven Emergency Fire Pump |
| 023 | Four Hurricane Emergency Shelter Stationary Spark Ignition Engines |
| 024 | One Spark Ignition Engine-driven Emergency Generator |
| 026 | New Auxiliary Boiler (for EU Nos. 003–006) |

Applicable Regulations

Based on the Title V air operation permit renewal application received on May 21, 2018, this facility is a major source of hazardous air pollutants (HAP).  The existing facility is a prevention of significant deterioration (PSD) major source of air pollutants in accordance with Rule 62-212.400, F.A.C.  A summary of applicable regulations is shown in the following table:

| Regulation | EU No(s). |
| --- | --- |
| Federal Rule Citations |  |
| 40 CFR 60, Subpart A, NSPS General Provisions | 001, 002, 003, 004, 005, 006, 007, 011, 012, 017, 018, 026 |
| 40 CFR 60, Subpart D, Standards of Performance for Fossil-Fuel-Fired Steam Generators | 001, 002 |
| 40 CFR 60, Subpart Dc, Standards of Performance for Small Industrial-Commercial-Institutional Steam Generating Units | 026 |
| 40 CFR 60, Subpart GG, Standards of Performance for Stationary Gas Turbines | 003, 004, 005, 006 |
| 40 CFR 60, Subpart KKKK, Standards of Performance for Stationary Combustion Turbines | 011, 012, 017, 018 |
| 40 CFR 60, Subpart IIII, Standards of Performance for Stationary Compression Ignition Internal Combustion Engines | 022 |
| 40 CFR 60, Subpart JJJJ, Standards of Performance for Stationary Spark Ignition Internal Combustion Engines | 023, 024 |
| 40 CFR 63, Subpart A, NESHAP General Provisions | 001, 002, 022, 023, 024, 026 |
| 40 CFR 63, Subpart ZZZZ, NESHAP for Stationary Reciprocating Internal Combustion Engines | 022, 023, 024 |
| 40 CR 63, Subpart DDDDD, NESHAP for Major Sources: Industrial, Commercial, and Institutional Boilers and Process Heaters | 026 |
| 40 CFR 63, Subpart UUUUU, NESHAP: Coal- and Oil-fired Electric Utility Steam Generating Units | 001, 002 |
| 40 CFR 64, Compliance Assurance Monitoring (CAM) | 001, 002 |
| 40 CFR 75, Acid Rain Monitoring Provisions | 001, 002, 003, 004, 005, 006, 011, 012, 017, 018 |
| State Rule Citations |  |
| Chapter 62-4, F.A.C. Permits | 001, 002, 003, 004, 005, 006, 011, 012, 017, 018, 019, 026 |
| Rule 62-204.800, F.A.C., Federal Regulations Adopted by Reference |  |
| Chapter 62-210, F.A.C., Stationary Sources – General Requirements |  |
| Chapter 62-212, F.A.C., Stationary Sources – Preconstruction Review | 003, 004, 005, 006, 011, 012, 014, 017, 018, 019, 026 |
| Chapter 62-213, F.A.C., Operation Permits for Major Sources of Air Pollution | 001, 002, 003, 004, 005, 006, 009, 011, 012, 014, 015, 016, 017, 018, 019, 025, 026 |
| Chapter 62-214, F.A.C., Requirements For Sources Subject To The Federal Acid Rain Program | 001, 002, 003, 004, 005, 006, 011, 012, 017, 018 |
| Rule 62-296.405, F.A.C., Fossil Fuel Steam Generators with More Than 250 Million Btu Per Hour Heat Input | 001, 002 |
| Rule 62-296.406, F.A.C., Fossil Fuel Steam Generators with Less Than 250 Million Btu Per Hour Heat Input, New and Existing Emissions Units | 026 |
| Chapter 62-297, F.A.C. (Test Methods and Procedures, Continuous Monitoring Specifications, and Alternate Sampling Procedures) | 001, 002, 003, 004, 005, 006, 011, 012, 017, 018, 026 |

This facility also includes miscellaneous unregulated/insignificant emissions units and/or activities.

Project DESCRIPTION

The purpose of this permitting project is to renew the existing Title V permit for the above referenced facility.  The renewal incorporates changes made in concurrent Permit No. 0850001-041-AC/PSD-FL-146J and 327G, minor formatting changes, typographical error corrections and updates in rule applicability.

Processing Schedule and Related Documents

Initial Title V Air Operation Permit issued June 29, 1998

Application for a Title V Air Operation Permit Renewal received May 21, 2018

Primary Regulatory requirements

Standard Industrial Classification (SIC) Code:  4911 – Electrical Generation.

North American Industry Classification System (NAICS):  22112 – Fossil Fuel Electric Power Generation.

HAP:  The facility is identified as a major source of hazardous air pollutants (HAP).

Title IV:  The facility operates units subject to the acid rain provisions of the Clean Air Act.

Title V:  The facility is a Title V major source of air pollution in accordance with Chapter 62-213, Florida Administrative Code (F.A.C.).

PSD:  The facility is a Prevention of Significant Deterioration (PSD)-major source of air pollution in accordance with Rule 62-212.400, F.A.C.

NSPS:  The facility operates units subject to the New Source Performance Standards (NSPS) of 40 Code of Federal Regulations (CFR) 60.

NESHAP:  The facility operates units subject to the National Emissions Standards for Hazardous Air Pollutants (NESHAP) of 40 CFR 63.

Siting:  Unit 3 (Emissions Unit Nos. 003 and 004), Unit 4 (Emissions Unit Nos. 005 and 006) and Unit 8 (Emissions Unit 011, 012, 017 and 018) were originally certified pursuant to the power plant siting provisions of Chapter 62-17, F.A.C.

CAM:  Compliance Assurance Monitoring (CAM) applies to Emissions Unit Nos. 001 and 002 for the controlled emissions of PM, because these units use an electrostatic precipitator to achieve permitted PM limits and have uncontrolled potential emissions of greater than 100 tons per year.

GHG:  The facility is identified as a major source of greenhouse gas (GHG) pollutants.

PROJECT REVIEW

This renewal primarily incorporates changes made in concurrent Permit No. 0850001-041-AC/PSD-FL-146J and 327G.  This air construction permit authorized reporting on a semiannual basis, revised inlet fogger monitoring for Martin Units 3 and 4, revised natural gas tracking for the auxiliary boiler, increased the allowable heat input rate for Martin Unit 8 and allowed use of a CO CEMS to be optional.  Other changes include typographical error corrections and format updates for the permit and appendices.  All subsections with engine rules (NSPS Subparts IIII and JJJJ and NESHAP Subpart ZZZZ) were updated to reflect the vacatur of certain provisions by the EPA.  Section III., Subsection I. has been updated to reflect the future construction of an emergency engine.  Changes to the permit made as part of this revision are shown in strike through format for deletions and in double underline format for additions.  Obsolete and nonapplicable provisions were removed from the permit.  For ease of identification, all changes have also been highlighted in yellow within the permit document.

General Changes

- The new Department logo and letterhead have been added to the title and placard pages of this permit.

- Citations were updated throughout the permit to reflect current Title V air operation permit format standards.

- Terms have been abbreviated throughout the permit wherever applicable.

- Specific conditions that reference rules that are cited in the body of the permit have been replaced with the appropriate cross references, as applicable.

- Rules and specific conditions that refer to “owner or operator” have been replaced with “permittee” wherever applicable to reflect current Title V air operation permit format standards.

- For all NSPS and NESHAP language in which the Department is the Administrator, the word “Administrator” has been replaced with “Department.”

- Cross-references in the permit have been updated to reflect the addition and removal of conditions.

- Minor typographical errors have been removed throughout the permit.

Table of Contents Changes

- Page numbers have been replaced by appropriate cross references.

- Section III., Subsection I has been updated to reflect the addition of EU No. 027.

Section I., Subsection A. Changes

- The upgrades authorized by Permit No. 0850001-038-AC increased the nominal generating capacity of each combustion turbine (CT)-electrical generator of Martin Unit 8 to 207.6 megawatts (MW).  To reflect this increase, the third paragraph of the facility description has been revised as follows:

Emissions Units 011, 012, 017 and 018:  Collectively regulated as Unit 8, this unit is a “4-on-1” combined cycle system which consists of four oil and natural gas fired combustion turbine/HRSG systems with a single steam turbine electrical generator.  Each of the four gas combustion turbines (8A, 8B, 8C and 8D) is nominally rated at 170 207.6 MW, with a matched 495 million British thermal units per hour (MMBtu/hr) gas-fired HRSG, and a single 470 MW steam turbine driven electrical generator that serves all four CT/HRSG systems, and associated support equipment.  Nitrogen oxides (NOX) emissions are controlled by using Dry Low NOX (DLN) combustors for natural gas and steam injection for fuel oil firing.  A selective catalytic reduction (SCR) system, in combination with the other NOX controls, further reduces NOX emissions during combined cycle operation.  The total generating capacity of this combined cycle combustion turbine system is approximately 1,150 1,300.4 MW.  There is also a solar thermal facility on-site that produces steam, which is used to augment the steam produced by the Unit 8 HRSGs, thus reducing fossil fuel use in the duct burners when adequate sunlight is available.

- Minor revisions were made to the last paragraph of the facility description, which appears as follows:

This facility also includes emergency generators, four hurricane emergency shelter stationary spark ignition (SI) engine driven generators, an emergency fire pump, two storage oil tanks, a mechanical cooling tower, and four electrical fuel line heaters (to heat up the natural gas fuel prior to introduction into the CT, when needed).  Also included in this permit are additional unregulated emissions units identified as facility-wide particulate matter (PM) and volatile organic compounds (VOC) emissions.

Section I. Subsection C. Changes

- The table of applicable regulations has been updated to reflect minor corrections and current Title V Air Operation Permit format standards.  The table has been revised as follows:

| Regulation | ## EU No(s). |
| --- | --- |
| Federal Rule Citations |  |
| 40 CFR 60, Subpart A, NSPS General Provisions | 001, 002, 003, 004, 005, 006, 007, 011, 012, 017, 018, 026 |
| 40 CFR 60, Subpart D, Standards of Performance for Fossil-Fuel-Fired Steam Generators | 001, 002 |
| 40 CFR 60, Subpart Dc, Standards of Performance for Small Industrial-Commercial-Institutional Steam Generating Units | 026 |
| 40 CFR 60, Subpart GG, Standards of Performance for Stationary Gas Turbines | 003, 004, 005, 006 |
| 40 CFR 60, Subpart KKKK, Standards of Performance for Stationary Combustion Turbines | 011, 012, 017, 018 |
| 40 CFR 60, Subpart IIII, Standards of Performance for Stationary Compression Ignition Internal Combustion Engines | 022 |
| 40 CFR 60, Subpart JJJJ, Standards of Performance for Stationary Spark Ignition Internal Combustion Engines | 023, 024 |
| 40 CFR 63, Subpart A, NESHAP General Provisions | 001, 002, 009, 022, 023, 024, 026 |
| 40 CFR 63, Subpart ZZZZ, NESHAP for Stationary Reciprocating Internal Combustion Engines | 009, 022, 023, 024 |
| 40 CR 63, Subpart DDDDD, NESHAP for Major Sources: Industrial, Commercial, and Institutional Boilers and Process Heaters | 026 |
| 40 CFR 63, Subpart UUUUU, NESHAP: Coal- and Oil-fired Electric Utility Steam Generating Units | 001, 002 |
| 40 CFR 64, Compliance Assurance Monitoring (CAM) | 001, 002 |
| 40 CFR 75, Acid Rain Monitoring Provisions | 001, 002, 003, 004, 005, 006, 011, 012, 017, 018 |
| State Rule Citations |  |
| Chapter 62-4, Florida Administrative Code (F.A.C.) (Permitting Requirements), Permits | 001, 002, 003, 004, 005, 006, 009, 011, 012, 017, 018, 019, 026 |
| Chapter Rule 62-204.800, F.A.C., (Ambient Air Quality Requirements, PSD Increments, and Federal Regulations Adopted by Reference) |  |
| Chapter 62-210, F.A.C., Stationary Sources – General Requirements (Permits Required, Public Notice, Reports, Stack Height Policy, Circumvention, Excess Emissions, and Forms) |  |
| Chapter 62-212, F.A.C., Stationary Sources – (Preconstruction Review, PSD Review and Best Available Control Technology (BACT)) | 001, 002, 003, 004, 005, 006, 009, 011, 012, 014, 017, 018, 019, 026 |
| Chapter 62-213, F.A.C. (Title V Air Operation Permits for Major Sources of Air Pollution) | 001, 002, 003, 004, 005, 006, 009, 011, 012, 017, 018, 019, 026 |
| Chapter 62-214, F.A.C. (Requirements For Sources Subject To The Federal Acid Rain Program) | 001, 002, 003, 004, 005, 006, 011, 012, 017, 018 |
| Chapter 62-296, F.A.C. (Emission Limiting Standards) | 001, 002, 003, 004, 005, 006, 009, 011, 012, 017, 018, 019, 026 |
| Rule 62-296.405, F.A.C., Fossil Fuel Steam Generators with More Than 250 Million Btu Per Hour Heat Input | 001, 002 |
| Rule 62-296.406, F.A.C., Fossil Fuel Steam Generators with Less Than 250 Million Btu Per Hour Heat Input, New and Existing Emissions Units | 026 |
| Chapter 62-297, F.A.C. (Test Methods and Procedures, Continuous Monitoring Specifications, and Alternate Sampling Procedures) | 001, 002, 003, 004, 005, 006, 009, 011, 012, 017, 018, 019, 026 |

Section III., Section A.

- To reflect minor clarifications, clarifications in NESHAP Subpart UUUUU applicability and current Title V air operation permit format standards, the EU description has been revised as follows:

Each fossil fuel fired steam generator emissions unit is identical in configuration.  Each steam generator has a capacity of 863.3 MW and are equipped with low NOX dual fuel firing burners to reduce emissions of NOX; and dry electrostatic precipitator (ESPs), with fly ash reinjection, to control PM emissions.  In addition, the units have a continuous emission monitoring system (CEMS) for measuring NOX and sulfur dioxide (SO2) and a continuous opacity monitoring system (COMS) for measuring opacity visible emissions (VE).  Steam Generator No. 1 commenced commercial operation in December 1980.  Steam Generator No. 2 commenced commercial operation in June 1981.  The stack parameters for both steam generators are:  499 feet in height; 36 feet in diameter; a flow rate of 2,634,519 actual cubic feet per minute (acfm) at a temperature of 338 degrees Fahrenheit (ºF); and exit velocity is 43.1 feet per second (fps).

{Permitting Note:  These emissions units are regulated under:  40 CFR 60, Subpart A, General Provisions, and Subpart D, Standards of Performance for Fossil Fuel-Fired Steam Generators, adopted by reference in Rule 62-204.800(8)(d) and (8)(b)1., F.A.C., respectively; 40 CFR 63, Subpart A, General Provisions, and, Subpart UUUUU, NESHAP:  Coal- and Oil-Fired Electric Utility Steam Generating Units, adopted by reference in Rule 62-204.800(11)(d)1. and (11)(b)1., F.A.C., respectively; Rule 62-296.405, F.A.C., Fossil Fuel Steam Generators with More Than 250 Million Btu Per Hour Heat Input; and, Chapter 62-214, F.A.C., the Phase II Acid Rain Program as specified in Section IV of this Permit.  These emissions units currently do not meet the definition of “oil-fired electric utility steam generating units”, in accordance with 40 CFR 63.10042, because these units have not burned oil for more than 10.0 percent(%) of the average annual heat input during the previous 3 calendar years or more than 15.0% of the annual heat input during any of the previous 3 calendar years.  These units currently meet the definition of “natural-gas fired electric utility steam generating units” in accordance with 40 CFR 63.10042.  In accordance with 40 CFR 63.9983(b), these units are currently not subject to 40 CFR 63, Subpart UUUUU, but shall be required to meet the provisions of this subpart if these units meet the definition of “oil-fired electric utility steam generating units”, pursuant to 40 CFR 63.9984(f).}

{Permitting Note:  The emissions units are regulated under Acid Rain, Phase II and NSPS – 40 CFR 60, Subpart D, Standards of Performance for Fossil-Fuel-Fired Steam Generators; adopted and incorporated by reference in Rule 62-204.800., F.A.C.  Units 1 and 2 are also subject to regulation pursuant to 40 CFR 63, Subpart UUUUU - National Emission Standards for Hazardous Air Pollutants (NESHAP) for Coal- and Oil-Fired Electric Utility Steam Generating Units, and must comply with the applicable requirements no later than April 16, 2015.  Construction permit No. 0850001-029-AC was issued on December 10, 2012 to authorize the installation of electrostatic precipitators (ESP) on these units in order to comply with Subpart UUUUU.  The construction of the ESP’s began in June 2013.}

- Specific Condition A.1 has been revised to reflect current Title V air operation permit format standards as follows:

- Permitted Capacity.  The maximum allowable heat input rate to each boiler is as follows:

| Unit No. | MMBtu/hr Heat Input | Fuel Type |
| --- | --- | --- |
| 001 & 002 | 8,650 | Fuel Oil |
| 001 & 002 | 9,040 | Natural Gas |

When a blend of fuel oil and natural gas is burned, the heat input is prorated based on the percent heat input of each fuel.

[Rules 62-4.160(2), & 62-210.200(PTE), 62-214.330 & 62-296.405, F.A.C.; and, Permit Nos. AC43-4037 & AC43-4038, as amended 2/16/93 February 16, 1993]

- Specific Condition A.2 has been revised to reflect the current version of Rule 62-297.310, F.A.C. as follows:

- Emissions Unit Operating Rate Limitation After Testing.  Testing of emissions shall be conducted with the emissions unit operating at permitted testing capacity ( i.e., 90% of the maximum operation rate in Specific Condition A.1).  If it is impracticable to test at the testing capacity, the emissions unit may be tested at less than the testing capacity.  If an emissions unit is tested at less than the testing capacity, another emissions test shall be conducted and completed no later than 60 days after the emissions unit exceeds 110% of the capacity at which its most recent emissions test was conducted. If it is impractical to test at permitted capacity, an emissions unit may be tested at less than the maximum permitted capacity; in this case, subsequent emissions unit operation is limited to 110 percent of the test rate until a new test is conducted.  Once the unit is so limited, operation at higher capacities is allowed for no more than 15 consecutive days for the purpose of additional compliance testing to regain the authority to operate at the permitted capacity.  Permitted capacity is defined as 90 to 100 percent of the maximum operation rate allowed by the permit.  (See also the related testing provisions in Appendix TR, Facility-wide Testing Requirements.)  [Rule 62-297.310(24), F.A.C.]

- Specific Condition A.5 has been deleted, revised and moved to the end of Section III., Subsection A. to reflect current Title V air operation permit format standards.  Specific Condition A.6 has been deleted to reflect that EU Nos. 001 and 002 are currently not subject to 40 CFR 63, Subpart UUUUU.

- The Air Pollution Control Devices & Measures section of Section III., Subsection A. has been renamed to Control Technology to reflect current Title V air operation permit format standards.

- Specific Condition A.11 has been deleted and combined with Specific Condition A.12 as follows:

- 40 CFR 60 Opacity Standard.  The opacity standards set forth in 40 CFR 60 shall apply at all times except during periods of startup, shutdown, malfunction, and as otherwise provided in the applicable standard.  [40 CFR 60.11(c)]

- Other Opacity Standard Visible Emissions.  The maximum emission limit for opacity exhibited by the gases discharged into the atmosphere from each of these emissions units any gases which exhibit greater than 20% opacity except for one six-minute period per hour of not more than 27% opacity.  This standard shall apply at all times except during periods of startup, shutdown, malfunction and as otherwise provided in NSPS Subpart D (see Appendix NSPS Subpart D).  [40 CFR 60.11(c) & 60.42(a)(2); and, Permit Nos. AC43-4031 & AC43-4038, as amended 2/16/93]

- Specific Conditions A.13 has been revised to incorporate minor format corrections and NSPS Subpart D provisions as follows:

- SO2 Emissions.  As determined by CEMS or fuel sampling and analysis, the maximum emission limit for sulfur dioxide contained in the gases discharged to the atmosphere from each of these emissions units shall not exceed:

- 340 nanograms per joule (ng/J) heat input (0.80 lb/MMBtu) derived from liquid fossil fuel.

- In addition, emissions shall not exceed 6,920 lb/hr when firing 100% oil.

Compliance shall be based on the total heat input from all fossil fuels burned, including gaseous fuels.  When different fuels are burned simultaneously in any combination, the applicable standard (in ng/J) shall be determined by proration using the following formula:

PSSO2=y340+z(520)(y+z)

Where:

PSSO2 = Prorated standard for SO2 when burning different fuels simultaneously, in ng/J heat input derived from all fossil fuels or from all fossil fuels fired;

y = Percentage of total heat input derived from liquid fossil fuel; and

z = Percentage of total heat input derived from solid fossil fuel.

[40 CFR 60.43(a)(1), (b) & (c), ; and, Permit Nos. AC43-4031 & AC43-4038, as amended 2/16/93]

- Minor revisions and corrections were made to Specific Condition A.16 as follows:

- NSPS Best Operational Procedures Excess Emissions Requirements.  At all times, including periods of startup, shutdown, and malfunction, owners and operators shall, to the extent practicable, maintain and operate any affected facility including associated air pollution control equipment in a manner consistent with good air pollution control practice for minimizing emissions.  Determination of whether acceptable operating and maintenance procedures are being used will be based on information available to the Administrator Department which may include, but is not limited to, monitoring results, opacity observations, review of operating and maintenance procedures, and inspection of the source.  [40 CFR 60.11(d)]

- To reflect the current version of Rule 62-210.700, F.A.C., Specific Condition A.17 has been revised as follows:

- Startup, Shutdown or Malfunction Excess Emissions Allowed.  In order to minimize excess emissions during startup/shutdown/ malfunction the following general procedures shall be followed:  Excess emissions resulting from startup, shutdown or malfunction of any emissions unit shall be permitted provideding:

- best operational practices to minimize emissions are adhered to, and

- the duration of excess emissions shall be minimized but in no case exceed two hours in any 24-hour period unless specifically authorized by the Department for longer duration.

[Rules 62-210.700(1) & (2), F.A.C.; and, Permit Nos. AO43-170568, Specific Condition 9.; and & AO43-170567, Specific Condition 9.]

- To reflect current Title V air operation permit format standards, Specific Condition A.18 has been added as follows:

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown or malfunction shall be prohibited.  [Rule 62-210.700(1), F.A.C.]

- Excess emissions provisions from NSPS Subpart D have been added as follows:

- NSPS Excess Emissions.  Excess emissions with are defined with respect to the standards in NSPS Subpart D are defined as follows:

- Visible Emissions.  Excess VE are defined as any 6-minute period during which the average opacity of emissions exceeds 20% opacity, except that one 6-minute average per hour of up to 27% opacity need not need be reported (see Specific Condition A.12).

- Sulfur Dioxide.  Excess SO2 emissions are defined as any 3-hour period during which the average emissions (arithmetic average of 3 contiguous 1-hour periods) of SO2 as measured by a CEMS exceed the applicable standard in Specific Condition A.13.

- Nitrogen Oxides.  Excess NOX emissions are defined as any 3-hour period during which the average emissions (arithmetic average of 3 contiguous 1-hour periods) exceed the applicable standard in Specific Condition A.14.

[40 CFR 60.45(g)(1), (2) & (3)]

- The Monitoring Requirements section has been renamed to Monitoring of Operations to reflect current Title V air operation permit format standards.

- Specific Condition A.35 (CAM Plan) has been deleted, revised and moved to the Monitoring of Operations section to reflect minor clarifications, citation corrections and current Title V air operation permit format standards.  This condition appears as follows:

Monitoring Requirements of Operations

- CAM Plan.  When these emissions units meet the definition of “natural gas-fired electric utility steam generating unit”, as defined in 40 CFR 63.10042, these emissions units are subject to the Compliance Assurance Monitoring (CAM) requirements contained in the attached Appendix CAM.  Failure to adhere to the monitoring requirements specified does not necessarily indicate an exceedance of a specific emissions limitation; however, it may constitute good reason to require compliance testing pursuant to Rule 62-297.310(78)(bc), F.A.C.  [40 CFR 64; Rules 62-204.800; 40 CFR 64; and, 62-213.440(1)(b)1.a., F.A.C.]

- Rule 62-296.405(1)(f)1., F.A.C. only applies to existing fossil fuel fired steam generators, as defined in Rule 62-210.200, F.A.C.  Martin Units 1 and 2 are not existing units.  Therefore, Specific Condition A.21 has been revised as follows:

- COMS for Periodic Monitoring.  When required, the owner or operator shall maintain and operate continuous opacity monitoring systems (COMS) pursuant to 40 CFR Part 75.  The owner or operator shall maintain and operate COMS and shall make and maintain records of opacity measured by the COMS, for purposes of periodic monitoring.  [Rule 62-213.440, F.A.C.; and applicant agreement with EPA on March 3, 1998.]

{Permitting Note:  In addition, Units 1 or 2 are no longer required to operate continuous opacity monitors (COMS) so long as each unit maintains “gas-firing” status according to 40 CFR Part 75.  40 CFR Part 75 exempts “gas-fired” units from opacity monitor requirements by way of the definition in 40 CFR 72.2.  The Martin Units 1 & 2 meet the gas-fired definition.  Also, Rule 62-296.405(1)(f)1., F.A.C. requires that fossil fueled steam generators with capacity factors greater than 30% must install opacity monitors.  Martin Units 1 & 2 are well below the 30% capacity factor requirement.  Lastly, tThe installation of the ESPs, initial compliance test results from each unit, and implementation of a particulate matter continuous parametric monitoring system (PM CPMS) according to the requirements specified in MATS or a Continuous Assurance Monitoring (CAM) Plan for the “natural gas-fired electric utility steam generating unit,” assures that the NSPS 40 CFR 60 Subpart D limit of 0.10 lb/MMBtu will continuously be met and the COMS exemption criteria of 40 CFR 60.45(b)(8) would be satisfied.  Therefore, COMS are no longer required.  In the future if FP&L Martin Unit 1 or 2 fails to meet the definition of “gas-fired” in 40 CFR 72, then FP&L has one year to install and certify an opacity monitor from the end of year in which the units at Martin do not meet the definition of a “gas-fired” unit in 40 CFR 72.2 and the COMS portions of the specific conditions of this permit shall once again apply.}

- Minor corrections were made to Specific Conditions A.24, A.25 and A.26 (formerly A.21, A.22 and A.23 of Permit No. 0850001-040-AV) as follows:

- Performance Evaluation.  If the owner or operator of an affected facility permittee elects to use COMS data for compliance with the opacity standard as provided under 40 CFR 60.11(e)(5) Specific Condition A.25, the permittee shall conduct a performance evaluation of the COMS as specified in Performance Specification 1, Appendix B, of 40 CFR 60 before the performance test required under 40 CFR 60.8 is conducted.  Otherwise, owner or operator of an affected facility permittee shall conduct a performance evaluation of the COMS or CEMS during any performance test required under 40 CFR 60.8 or within 30 days thereafter in accordance with the applicable performance specification in Appendix B of 40 CFR 60.  The owner or operator of an affected facility shall conduct COMS or CEMS performance evaluations at such other times as may be required by the Administrator Department under section 114 of the Act.  [40 CFR 60.13(c)]

- COMS Data for Compliance.  The owner or operator of an affected facility subject to an opacity standard may submit, for compliance purposes COMS data results produced during any performance test required under 40 CFR 60.8 in lieu of Method 9 observation data.  If an owner or operator the permittee elects to submit COMS data for compliance with the opacity standard, he shall notify the Administrator Department of that decision, in writing, at least 30 days before any performance test required under 40 CFR 60.8 is conducted.  Once the owner or operator of an affected facility has notified the Administrator Department to that effect, the COMS data results will be used to determine opacity compliance during subsequent tests required under 40 CFR 60.8 until the owner or operator notifies the Administrator Department, in writing, to the contrary.  For the purpose of determining compliance with the opacity standard during a performance test required under 40 CFR 60.8 using COMS data, the minimum total time of COMS data collection shall be averages of all 6-minute continuous periods within the duration of the mass emission performance test.  Results of the COMS opacity determinations shall be submitted along with the results of the performance test required under 60.8.  The owner or operator of an affected facility using a COMS for compliance purposes is responsible for demonstrating that the COMS meets the requirements specified in 40 CFR 60.13(c), that the COMS has been properly maintained and operated, and that the resulting data have not been altered in any way.  If COMS data results are submitted for compliance with the opacity standard for a period of time during which Method 9 data indicates noncompliance, the Method 9 data will be used to determine opacity compliance with the opacity standard.  [40 CFR 60.11(e)(5)]

- CEMS Procedures.

- Owners and operators of all CEMS installed in accordance with the provisions of this pPart 60 shall check the zero (or low-level value between 0 and 20% of span value) and span (50 to 100% of span value) calibration drifts at least once daily in accordance with a written procedure.  The zero and span shall, as a minimum, be adjusted whenever the 24-hour zero drift or 24-hour span drift exceeds two times the limits of the applicable performance specifications in Appendix B.  The system must allow the amount of excess zero and span drift measured at the 24-hour interval checks to be recorded and quantified, whenever specified.  For continuous monitoring systems measuring opacity of emissions, the optical surfaces exposed to the effluent gases shall be cleaned prior to performing the zero and span drift adjustments except that for systems using automatic zero adjustments.  The optical surfaces shall be cleaned when the cumulative automatic zero compensation exceeds 4% opacity.

- Unless otherwise approved by the Administrator Department, the following procedures shall be followed for continuous monitoring systems measuring opacity of emissions.  Minimum procedures shall include a method for producing a simulated zero opacity condition and an upscale (span) opacity condition using a certified neutral density filter or other related technique to produce a known obscuration of the light beam.  Such procedures shall provide a system check of the analyzer internal optical surfaces and all electronic circuitry including the lamp and photo detector assembly.

[40 CFR 60.13(d)(1) and (2)]

- Specific Condition A.31 (formerly A.28 of Permit No. 0850001-040-AV) has been revised to reflect minor corrections and the removal of nonapplicable requirements.  The revisions appear as follows:

- Performance Evaluations and Calibration Checks.  For performance evaluations under 40 CFR 60.13(c) Specific Condition A.24 and calibration checks under 40 CFR 60.13(d) Specific Condition A.26, the following procedures shall be used:

- Methods 6, 7, and 3B, as applicable, shall be used for the performance evaluations of sulfur dioxide and nitrogen oxides continuous monitoring systems.  Acceptable alternative methods for Methods 6, 7, and 3B are given in 40 CFR 60.46(d).

- SO2 or NOX, as applicable, shall be used for preparing calibration gas mixtures under Performance Specification 2 of Appendix B to 40 CFR 60.

- For affected facilities burning fossil fuel(s), the span value for a continuous monitoring system measuring the opacity of emissions shall be 80, 90, or 100% and for a continuous monitoring system measuring sulfur oxides or nitrogen oxides the span value shall be determined using one of the following procedures:

- Except as provided under paragraph c.(2), SO2 and NOX span value shall be determined as follows:

| Fossil Fuel | Span value for sulfur dioxide SO2 (ppm) | Span value for nitrogen oxides NOX (ppm) |
| --- | --- | --- |
| Gas | Not applicable | 500 |
| Liquid | 1,000 | 500 |
| Combinations | 1,000y | 500 (x + y) |

Where:

x  =  the fraction of total heat input derived from gaseous fossil fuel, and

y  =  the fraction of total heat input derived from liquid fossil fuel.

- As an acceptable alternative, the owner or operator of an affected facility may elect to use the SO2 and NOX span values determined according to sections 2.1.1 and 2.1.2 in appendix A to part 75 of this chapter. Span values shall be rounded off according to the applicable procedures in section 2 of appendix A to part 40 CFR 75.

- All span values computed under 40 CFR 60.45(c)(3) paragraph c(1) for burning combinations of fossil fuels shall be rounded to the nearest 500 ppm.  Span values that are computed under paragraph c(2) shall be rounded off according to the applicable procedures in section 2 of appendix A to 40 CFR 75.

- For a fossil fuel-fired steam generator that simultaneously burns fossil fuel and nonfossil fuel, the span value of all continuous monitoring systems shall be subject to the Administrator's approval.

[40 CFR 60.45(c)]

- Specific Condition A.34 (formerly A.31 of Permit No. 0850001-040-AV) is a CEMS data reporting requirement that has been deleted and move to the Recordkeeping and Reporting section of this subsection.

- As stated in item 26, to reflect current Title V air operation permit format standards, the Monitoring of Operations section and CAM plan requirements have been revised and removed.  Specific Condition A.35 (formerly A.32 of Permit No. 0850001-040-AV) now exists as Specific Condition A.20 in the draft permit.

- To reflect current Title V air operation permit format standards and the removal of obsolete , Specific Condition A.36 (formerly A.33 of Permit No. 0850001-040-AV) has been revised as follows:

- Test Methods.  When Rrequired tests shall be performed in accordance with the following reference methods.

| Method | Description of Method and Comments |
| --- | --- |
| 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| 3, 3A, 3B | Determination of Oxygen and Carbon Dioxide Concentrations in Emissions from Stationary Sources |
| 5, 5B, 17 | Method for Determining Particulate Matter Emissions (All PM is assumed to be PM10.) |
| 6, 6A, 6B, 6C | Determination of Sulfur Dioxide Emissions from Stationary Sources |
| 7, 7A, 7C, 7D, 7E | Determination of Nitrogen Oxide Emissions from Stationary Sources |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |
| 19 | Determination of Sulfur Dioxide Removal Efficiency and Particulate Matter, Sulfur Dioxide, and Nitrogen Oxides Emission Rates (Optional F-factor method may be used to determine flow rate and gas analysis to calculate mass emissions in lieu of Methods 1-4.) |
| 20 | Determination of Nitrogen Oxides, Sulfur Dioxide and Diluent Emissions from Stationary Gas Turbines |

The above methods are described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [40 CFR 60, Appendix A; and Rules 62-204.800297.400 and 62-297.620, F.A.C.]

- To reflect current Title V air operation permit format standards and the current version of Rule 62-297.310, F.A.C., Specific Condition A.38 (formerly A.35 of Permit No. 0850001-040-AV) has been revised as follows:

- Compliance Tests Prior To Renewal.  Unless specifically exempted per Florida Rule 62-297 Except as provided in subparagraph 62-297.310(8)(b)3., F.A.C. (see condition TR7.b.(3) in Appendix TR – Facility-wide Testing Requirements), prior to permit renewal, compliance tests shall be performed for the following pollutants:  VE (except as provided in Specific Condition A.18A.21), PM, NOX and SO2 (except as provided in Specific Condition A.37A.40).  [Rule 62-297.310(78)(ab)3., F.A.C.]

- The obsolete Rule 62-297.401, F.A.C. has been removed from the citation under Specific Condition A.40 (formerly A.37 of Permit No. 0850001-040-AV).

- Minor corrections and clarifications were made to Specific Condition A.45 (formerly A.42 of Permit No. 0850001-040-AV), which appears as follows:

- Compliance.

- The owner or operator permittee shall determine compliance with the particulate matter, SO2, and NOX standards in 40 CFR 60.42, 60.43, and 60.44 as follows:

- The emission rate (E) of particulate matter, SO2, or NOX shall be computed for each run using the following equation:

E=CFd20.920.9-%O2

Where:

E = Emission rate of pollutant, ng/J (1b/million Btu).

C = Concentration of pollutant, ng/dscm (1 lb/dscf).

%O2 = Oxygen O2 concentration, percent dry basis.

Fd = factor as determined from Method 19 of appendix A of 40 CFR 60.

- Method 5 of appendix A of 40 CFR 60 shall be used to determine the particular matter (PM) concentration (C) at affected facilities without wet flue-gas-desulfurization (FGD) systems and Method 5B of appendix A of 40 CFR 60 shall be used to determine the particular matter (PM) concentration (C) after FGD systems.

- The sampling time and sample volume for each run shall be at least 60 minutes and 0.85 dscm (30 dscf).  The probe and filter holder heating systems in the sampling train may be set to provide a gas temperature no greater than 160  14⁰C (320  25⁰F).

- The emission rate correction factor, integrated or grab sampling and analysis procedure of Method 3B shall be used to determine the O2 concentration (%O2).  The O2 sample shall be obtained simultaneously with, and at the same traverse points as, the particulate sample.  If the grab sampling procedure is used, the O2 concentration for the run shall be the arithmetic mean of all the individual sample O2 sample concentrations at each all traverse points.

- If the particulate run has more than 12 traverse points, the O2 traverse points may be reduced to 12 provided that Method 1 is used to locate the 12 O2 traverse points.

- Method 9 of appendix A of 40 CFR 60 and the procedures in 40 CFR 60.11 shall be used to determine opacity.

- Method 6 of appendix A of 40 CFR 60 shall be used to determine the SO2 concentration.

- The sampling site shall be the same as that selected for the particulate sample.  The sampling location in the duct shall be at the centroid of the cross section or at a point no closer to the walls than 1 m (3.28 ft).  The sampling time and sample volume for each sample run shall be at least 20 minutes and 0.020 dscm (0.71 dscf).  Two samples shall be taken during a 1-hour period, with each sample taken within a 30-minute interval.

- The emission rate correction factor, integrated sampling and analysis procedure of Method 3B shall be used to determine the O2 concentration (%O2).  The O2 sample shall be taken simultaneously with, and at the same point as, the SO2 sample.  The SO2 emission rate shall be computed for each pair of SO2 and O2 samples.  The SO2 emission rate (E) for each run shall be the arithmetic mean of the results of the two pairs of samples.

- Method 7 shall be used to determine the NOX concentration.

- The sampling site and location shall be the same as for the SO2 sample.  Each run shall consist of four grab samples, with each sample taken at about 15-minute intervals.

- For each NOX sample, the emission rate correction factor, grab sampling and analysis procedure of Method 3B shall be used to determine the O2 concentration (%O2).  The sample shall be taken simultaneously with, and at the same point as, the NOX sample.

- The NOX emission rate shall be computed for each pair of NOX and O2 samples.  The NOX emission rate (E) for each run shall be the arithmetic mean of the results of the four pairs of samples.

- When combinations of fossil fuels are fired, the owner or operator (in order to compute the prorated standard as shown in 40 CFR 60.43(b) and 60.44(b)) shall determine the percentage (x or y) of the total heat input derived from each type of fuel as follows:

- The heat input rate of each fuel shall be determined by multiplying the gross calorific value of each fuel fired by the rate of each fuel burned.

- ASTM Methods D240-76 (liquid fuels), or D 1826-77 (gaseous fuels) (incorporated by reference-see 40 CFR 60.17) shall be used to determine the gross calorific values of the fuels.

- Suitable methods shall be used to determine the rate of each fuel burned during each test period, and a material balance over the steam generating system shall be used to confirm the rate.

- The owner or operator may use the following as alternatives to the reference methods and procedures in 40 CFR 60.46 or in other sections as specified:

- The emission rate (E) of particulate matter, SO2 and NOX may be determined by using the Fc factor, provided that the following procedure is used:

- The emission rate (E) shall be computed using the following equation:

E=CFc100%CO2

Where:

E = Emission rate of pollutant, ng/J (lb/million Btu).

C = Concentration of pollutant, ng/dscm (lb/dscf).

# %CO2 = carbon dioxide CO2 concentration, percent dry basis.

# Fc = factor as determined in appropriate sections of Method 19 of appendix A of 40 CFR 60.

- If and only if the average Fc factor in Method 19 is used to calculate E and either E is from 0.97 to 1.00 of the emission standard or the relative accuracy of a continuous emission monitoring system (CEMS) is from 17 to 20 percent, then three runs of Method 3B of appendix A of 40 CFR 60 shall be used to determine the O2 and CO2 concentration according to the procedures in 40 CFR 60.46(b) (2)(ii), (4)(ii), or (5)(ii).  Then if Fo (average of three runs), as calculated from the equation in Method 3B of appendix A of 40 CFR 60, is more than  3 percent than the average Fo value, as determined from the average values of Fd and Fc in Method 19, i.e., Foa = 0.209 (Fda / Fca), then the following procedure shall be followed:

- When Fo is less than 0.97 Foa, then E shall be increased by that proportion under 0.97 Foa, e.g., if Fo is 0.95 Foa, E shall be increased by 2 percent. This recalculated value shall be used to determine compliance with the emission standard.

- When Fo is less than 0.97 Foa and when the average difference () between the continuous monitor minus the reference methods is negative, then E shall be increased by that proportion under 0.97 Foa, e.g., if Fo is 0.95 Foa, E shall be increased by 2 percent.  This recalculated value shall be used to determine compliance with the relative accuracy specification.

- When Fo is greater than 1.03 Foa and when  is positive, then E shall be decreased by that proportion over 1.03 Foa, e.g., if Fo is 1.05 Foa, E shall be decreased by 2 percent.  This recalculated value shall be used to determine compliance with the relative accuracy specification.

- For Method 5 or 5B, Method 17 may be used at facilities with or without wet FGD systems if the stack gas temperature at the sampling location does not exceed an average temperature of 160⁰C (320⁰F).  The procedures of sections 2.1 and 2.3 of Method 5B may be used with Method 17 only if it is used after wet FGD systems.  Method 17 shall not be used after wet FGD systems if the effluent gas is saturated or laden with water droplets.

- Particulate matter (PM) and SO2 may be determined simultaneously with the Method 5 of appendix A of 40 CFR 60 train provided that the following changes are made:

- The filter and impinger apparatus in sections 2.1.5 and 2.1.6 of Method 8 is used in place of the condenser (section 2.1.7) of Method 5.

- All applicable procedures in method 8 for the determination of SO2 including moisture) are used.

- For Method 6 of appendix A of 40 CFR 60, Method 6C of appendix A of 40 CFR 60 may be used.  Method 6A of appendix A of 40 CFR 60 may also be used whenever Methods 6 and 3B of appendix A of 40 CFR 60 data are specified to determine the SO2 emission rate, under the conditions in 40 CFR 60.46(d)(1).

- For Method 7 of appendix A of 40 CFR 60, Method 7A, 7C, 7D, or 7E of appendix A of 40 CFR 60 may be used.  If Method 7C, 7D, or 7E of appendix A of 40 CFR 60 is used, the sampling time for each run shall be at least 1 hour and the integrated sampling approach shall be used to determine the O2 concentration (%O2) for the emission rate correction factor.

- For Method 3 of appendix A of 40 CFR 60, Method 3A or 3B of appendix A of 40 CFR 60 may be used.

- For Method 3B of appendix A of 40 CFR 60, Method 3A of appendix A of 40 CFR 60 may be used.

[40 CFR 60.46(b), (c) and & (d)]

- Rule 62-297.400, F.A.C. no longer exists.  Reference test methods are incorporated by reference in Rule 62-204.800, F.A.C.  To reflect this, Specific Condition A.46 (formerly A.43 of Permit No. 0850001-040-AV) has been revised as follows:

- Test Methodology.  All compliance tests shall be performed using reference test methods as given in 40 CFR 60, Appendix A, as adopted by reference in Rule 62-297.400204.800, F.A.C.  Any deviations from the test methodology in order to facilitate “representative” testing shall be approved by the Department pursuant to Rule 62-297.620, F.A.C., prior to conducting the tests.  [40 CFR 60, Appendix A; Rules 62-297.400204.800 & 62-297.620, F.A.C.; and, Permit Nos. AO43-170568, Specific Condition 3. & AO43-170567, Specific Condition 3.]

- To reflect the approved Department request to change quarterly reporting to semiannual reporting, the revision of a CEMS reporting requirement (see item 30) and current Title V air operation permit format standards, Specific Condition A.49 (formerly A.46 of Permit No. 0850001-040-AV) has been revised as follows:

- Reporting Schedule.  The following reports and notifications shall be submitted to the Compliance Authority:

| Report | Reporting Deadline | Related Condition(s) |
| --- | --- | --- |
| Notice of Operational Changes | 60 days prior to change. | A.48A.51 |
| NSPS Excess Emissions Reports | Semi-annually | A.50A.53 |
| CEMS Reports | Semi-annually | A.56 |
| NSPS 40 CFR 60 Subpart D Reports | Quarterly Semi-annually. | A.57A.61 |

[Rule 62-213.440(1)(b), F.A.C.]

- Specific Condition A.56 is a CEMS reporting requirement that has been deleted (see item 30), revised in accordance with Permit No. 0850001-041-AC (PSD-FL-146J & 327G) and added under the Recordkeeping and Reporting section of Section III., Subsection A. as follows:

- CEMS Reports.  Operation and maintenance of CEMS shall be carried out according to the requirements of 40 CFR 60; reports thereof shall be submitted to the Compliance Authority within thirty (30) days following each 6-month period in a calendar year and will include information required under 40 CFR 60.7(c).  The Department reserves the right to modify the format of the reports.  For any periods of excess emissions, as defined in 40 CFR 60.45(g), the reports shall specify the cause and corrective actions taken as well as the specific operational conditions existing (i.e., steady-state output, load charging rate; soot blowing, limiting, or air preheated steam cleaning sequences), during the period of excess emissions.  [Permit No. 0850001-041-AC (PSD-FL-146J & 327G)]

- Excess emissions definitions in NSPS Subpart D were moved into the Excess Emissions section of Section III., Subsection A. (see item 24) and removed from Specific Condition A.61 (formerly A.57 of Permit No. 0850001-040-AV).  This condition has been revised as follows:

- NSPS Subpart D Requirements.  Excess emission and monitoring system performance (MSP) reports shall be submitted to the Administrator Department for every calendar quarter 6-month period in a calendar year.  All quarterly reports shall be postmarked by the 30th day following the end of each calendar quarter 6-month period in a calendar year.  Each excess emission and MSP report shall include the information required in 40 CFR 60.7(c).  Periods of excess emissions and monitoring systems (MS) downtime that shall be reported are defined as follows:

a.	Opacity.  Excess emissions are defined as any six-minute period during which the average opacity of emissions exceeds 20 percent opacity, except that one six-minute average per hour of up to 27 percent opacity need not be reported.

b.	Sulfur Dioxide.  Excess emissions for affected facilities are defined as any three-hour period during which the average emissions (arithmetic average of three contiguous one-hour periods) of sulfur dioxide as measured by a continuous monitoring system exceed the applicable standard under 40 CFR 60.43.

c.	Nitrogen Oxides.  Excess emissions for affected facilities using a continuous monitoring system for measuring nitrogen oxides are defined as any three-hour period during which the average emissions (arithmetic average of three contiguous one-hour periods) exceed the applicable standards under 40 CFR 60.44.

[40 CFR 60.45(g)(1), (2), & (3)]

- Specific Condition A.5 has been deleted, revised and reinserted as Specific Condition A.62, which appears as follows:

Other Requirements

- NSPS Requirements.  These emissions units are subject to the performance and monitoring requirements of the New Source Performance Standards for Subparts A and D in 40 CFR 60.  For completeness, the provisions of Subparts A and D are included in the Appendices of this permit.  [Rule 62-204.800, F.A.C. and 40 CFR 60, Subpart D]

- A discussion of NESHAP Subpart UUUUU applicability now appears under the EU description.  To eliminate redundant and outdated language, the first paragraph of Specific Condition A.63 (formerly A.58 of Permit No. 0850001-040-AV) has been revised as follows:

- Subpart UUUUU Requirements.  In addition to the emissions limits shown above, if either unit meets the definition of an oil-fired electric utility steam generating unit in Subpart UUUUU, the permittee shall for that unit also comply with the following emissions limits as applicable, and other Subpart UUUUU requirements based on a compliance date no later than April 16, 2015, within a 180-day period following that date to demonstrate compliance.  The permittee must also meet all the applicable requirements of NESHAP 40 CFR 63, Subpart A – General Provisions which is included in Appendix NESHAP, Subpart A:  General Provisions.

Note:  A unit meeting the definition for “natural gas-fired electric utility steam generating unit” is not subject to Subpart UUUUU [63.9983(b)]. “Natural gas-fired electric utility steam generating unit” means an electric utility steam generating unit meeting the definition of “fossil fuel-fired” that is not a coal-fired, oil-fired, or IGCC electric utility steam generating unit and that burns natural gas for more than 10.0 percent of the average annual heat input during any 3 consecutive calendar years or for more than 15.0 percent of the annual heat input during any one calendar year.

- Pursuant to 40 CFR 63.7491(a), EU Nos. 001 and 002 are not subject to 40 CFR 63, Subpart DDDDD and cannot be subject to this subpart as long as they are defined as “oil-fired electric utility steam generating units” or “natural-gas-fired electric utility steam generating units” in accordance with NESHAP Subpart UUUUU.  Therefore, Specific Condition A.64 (formerly A.58 of Permit No. 0850001-040-AV) has been deleted.

Changes to Section III., Subsection B

- Clarifications were made to the EU description, which has been revised as follows:

All four combined cycle CT units are identical in configuration.  All four CTs are identical General Electric (GE) Model MS7001FA CT-electrical generators.  CTs 3A and 4A are paired with CTs 3B and 4B, respectively, in a pair of “two-on-one” arrangements.  A common steam turbine electrical generator (STEG) is shared by each pair of CTs.  Exhaust from each pair vents through an unfired HRSG to produce steam, which is vented through the STEG.  NOX emissions are controlled by using dry low NOX (DLN) combustors for natural gas with steam injection for fuel oil firing.  Steam injection is also used for power augmentation.  Inlet foggers installed at the compressor inlet to each of the four CT units reduce the turbine inlet air temperature.  The temperature reduction improves the heat rate and increases power due to the cooler/denser inlet air.  Duct modules suitable for future installation of selective catalytic reduction (SCR) equipment have been installed on each combined cycle generating unit.  CT 3A and CT 3B commenced commercial operation in February 1994.  CT 4A and CT 4B commenced commercial operation in April 1994.  For all CT, the stack parameters are:  stack heights 213 feet; stack diameter 20 feet; flow rate 2,420,307 acfm at 280ºF; and exit velocity 128.4 fps.

CAM is not applicable to these CT’s since DLN combustors when firing natural gas are not considered a pollution control device under 40 CFR 64.  When firing distillate fuel oil, compliance with the emissions limits are determined using CEMS data, and therefore the requirements of CAM are not required.

{Permitting Note:  These emissions units are regulated under:  40 CFR 60, Subpart A, General Provisions, and Subpart GG, Standards of Performance for Stationary Gas Turbines, adopted by reference in Rule 62-204.800(8)(d) and (8)(b)42., F.A.C., respectively; Rule 62-212.400, Best Available Control Technology (BACT) limits for NOX, VOC, carbon monoxide (CO), PM and PM less than 10 microns in diameter (PM10), lead (Pb) and SO2; and Chapter 62-214, F.A.C., the Phase II Acid Rain Program as specified in Section IV of this Permit}

{Permitting Note:  The emissions units are regulated under Acid Rain, Phase II and NSPS - 40 CFR 60, Subpart GG, Standards of Performance for Stationary Gas Turbines; adopted and incorporated by reference in Rule 62-204.800, F.A.C; PSD-FL-146, Prevention of Significant Deterioration (PSD), in Rule 62-212.400, F.A.C.; Best Available Control Technology (BACT), in Rule 62-212.410, F.A.C.; and PA89-27.}

- To reflect changes made in Permit No. 0850001-041-AC (PSD-FL-146J and 327G), Specific Condition B.3 has been revised as follows:

- Methods of Operation.

  - Fuels.  Only natural gas or No. 2 fuel oil shall be fired in the CT units.

  - Inlet Foggers.  Operation of the foggers on each unit may shall not exceed a combined total of 3,663 hours per calendar year the following limits:  181,661⁰F-hours in aggregate firing natural gas fuel if no distillate fuel is fired.  If distillate oil is fired in any of the CT units during a calendar year, the allowable ⁰F-hours for natural gas shall be decreased by 2.77⁰F-hours for every hour operated on distillate oil fuel.  No CT may exceed 4,000⁰F-hours per year firing distillate oil fuel.

  - Power Augmentation.  The CTs may also be operated in power augmentation mode, which involves the introduction of steam into the combustion chamber turbine to generate additional direct, shaft-driven electrical power to respond to peak demands

[Permit Nos. PSD-FL-146, Specific Condition No. 3, 0850001-005-AC/PSD-FL-146(G) & 0850001-016-AC/PSD-FL-327B & 146C & 0850001-041-AC/PSD-FL-146J & 327G]

- To reflect current Title V air operation permit format standards, the Applicable Standards and Regulations and Specific Conditions B.5 and B.6 have been deleted.

- To reflect current Title V air operation permit format standards, Specific Condition B.8 has been deleted and converted into Specific Conditions B.9, B.10, B.11, B.12, B.13, B.14 and B.15.  NOX and SO2 limits from NSPS Subpart GG have been incorporated into Specific Conditions B.10 and B.15.  Chapter 403.0872(13)(b) of the Florida Statutes has been incorporated in order to establish an averaging period for NOX emissions.  The revisions appear as follows:

- The maximum allowable emissions from each CT, in accordance with the BACT determination, shall not exceed the following, at 40 degrees F, except during periods of startup and shutdown:

| Pollutant | Fuel | Basis | Emission Limitations |  | Compliance Method |
| --- | --- | --- | --- | --- | --- |
|  |  | Concentration | lb/hr/CT | TPY/CTa. |  |
| NOX | Gas | 25 ppmvd @ 15% O | 177 | 3,108 | CEMS |
|  | Oil | 65 ppmvd @ 15% O | 461 |  |  |
| VOCb. | Gas | 1.6 ppmvd | 3 | 57 | CO Compliance & Stack Test |
|  | Oil | 6 ppmvd | 11.0 |  |  |
| CO | Gas | 30 ppmvd | 94.3 | 871 | Stack Test |
|  | Oil | 33 ppmvd | 105.8 |  |  |
| PM/PM10 | Gas |  | 18 | 100 | N/A |
|  | Oil |  | 60.6 |  | Stack Test |
| Pb | Gas |  | negligible | 0.015 | N/A |
|  | Oil |  | 0.015 |  |  |
| SO2 | Gas |  | 91.5 | 568 | Fuel Specs. |
|  | Oilc. |  | 920 |  |  |
| - Tons per year (TPY) emission limits listed for natural gas and oil combined apply as an emissions cap based on limiting oil firing to an annual aggregate of 2,000 hours for the 4 CT units, with compliance to be demonstrated in annual operation reports. - Exclusive of background concentrations. - Sulfur dioxide emissions based on a maximum of 0.5 percent sulfur content, by weight, in oil for hourly emissions and an average sulfur content of 0.3 percent, by weight, for annual emissions. |  |  |  |  |  |

[Rule 62-212.400(BACT), F.A.C.; and, Permit No. PSD-FL-146, Specific Condition No. 4.]

- Annual Mass Emissions Rates.  Tons per year (TPY) emissions limits listed for natural gas and oil combined in Specific Conditions B.10 through B.15 apply as an emissions cap based on limiting oil firing to an annual aggregate of 2,000 hours for the 4 CT units, with compliance to be demonstrated in annual operation reports (AORs).  [Permit No. PSD-FL-146, Specific Condition 4.]

- NOX Emissions.  The permittee shall comply with the following NOX emissions standards:

- BACT Limits.  As determined by CEMS, the NOX emissions shall not exceed the following, at 40⁰F, except during periods of startup, shutdown, documented malfunction, DLN tuning and Full Speed No Load (FSNL) testing, as specified in Specific Conditions B.18 and B.19:

- Natural Gas.

- 25 parts per million by volume, dry at 15% oxygen (ppmvd at 15% O2), based on a 30-day rolling average; and

- 177 pounds per hour per CT (lb/hr/CT), based on a 30-day rolling average.

- Fuel Oil.

- 65 ppmvd at 15% O2, based on a 30-day rolling average; and

- 461 lb/hr/CT, based on a 30-day rolling average

- Natural Gas and Fuel Oil.  3,108 TPY per CT (TPY/CT) for the combined total of emissions generated through natural gas and fuel oil firing.

- NSPS Limits.  The permittee shall not cause to be discharged into the atmosphere from any stationary gas turbine, any gases which contain NOX in excess of:

STD=0.0075(14.4)Y+F

Where:

STD = allowable ISO corrected (if required as given in 40 CFR 60.335(b)(1)) NOX emission concentration (percent by volume at 15% O2 on a dry basis),

Y = manufacturer’s rated heat rate at manufacturer’s rated peak load (kilojoules per watt hour), or actual measured heat rate based on lower heating value of fuel as measured at actual peak load for the facility.  The value of Y shall not exceed 14.4 kilojoules per watt hour, and

F = Optional NOX emission allowance for fuel-bound nitrogen as defined in 40 CFR 60.332(a)(4) (see Appendix NSPS, Subpart GG).

[Rule 62-212.400(BACT), F.A.C.; 40 CFR 60.332(a)(1)-(4) & (b); and, Permit Nos. PSD-FL-146, Specific Condition 4. & 0850001-032-AC/PSD-FL-146H & 327F]

{Permitting Note:  Chapter 403.0872(13)(b) of the Florida Statutes states that, for emission units that are subject to continuous monitoring requirements under 40 CFR 75, compliance with NOX emission limits shall be demonstrated based on a 30-day rolling average, except as specifically provided by 40 CFR part 60 or part 76.}

- VOC Emissions.  The emissions standards in this condition are exclusive of background concentrations.  As determined by compliance with CO emissions standards or stack test, VOC emissions shall not exceed the following, at 40⁰F, except during periods of startup and shutdown:

- Natural Gas.

- 1.6 ppmvd; and

- 3 lb/hr/CT.

- Fuel Oil.

- 6 ppmvd; and

- 11.0 lb/hr/CT.

- Natural Gas and Fuel Oil.  57 TPY/CT for the combined total of emissions generated through natural gas and fuel oil firing.

[Rule 62-212.400(BACT), F.A.C.; and, Permit Nos. PSD-FL-146, Specific Condition 4. & 0850001-032-AC/PSD-FL-146H & 327F]

- CO Emissions.  As determined by stack test, CO emissions shall not exceed the following, at 40⁰F, except during periods of startup and shutdown:

- Natural Gas.

- 30 ppmvd; and

- 94.3 lb/hr/CT.

- Fuel Oil.

- 33 ppmvd; and

- 105.8 lb/hr/CT

- Natural Gas and Fuel Oil.  871 TPY/CT for the combined total of emissions generated through natural gas and fuel oil firing.

[Rule 62-212.400(BACT), F.A.C.; and, Permit Nos. PSD-FL-146, Specific Condition 4. & 0850001-032-AC/PSD-FL-146H & 327F]

- PM/PM10 Emissions.  As determined by stack test (for fuel oil firing only), PM/PM10 emissions shall not exceed the following, at 40⁰F, except during periods of startup and shutdown:

- Natural Gas.  18 lb/hr/CT;

- Fuel Oil.  60.6 lb/hr/CT; and

- Natural Gas and Fuel Oil.  100 TPY/CT for the combined total of emissions generated through natural gas and fuel oil firing.

[Rule 62-212.400(BACT), F.A.C.; and, Permit Nos. PSD-FL-146, Specific Condition 4. & 0850001-032-AC/PSD-FL-146H & 327F]

- Lead (Pb) Emissions As determined by initial stack test (for fuel oil firing only), Pb emissions shall not exceed the following, at 40⁰F, except during periods of startup and shutdown:

- Fuel Oil.  0.015 lb/hr/CT; and

- Natural Gas and Fuel Oil.  0.015 TPY/CT for the combined total of emissions generated through natural gas and fuel oil firing.

[Rule 62-212.400(BACT), F.A.C.; and, Permit Nos. PSD-FL-146, Specific Condition 4. & 0850001-032-AC/PSD-FL-146H & 327F]

- SO2 Emissions.

- BACT SO2 Limits.  As determined by fuel specifications, SO2 emissions shall not exceed the following, at 40⁰F, except during periods of startup and shutdown:

- Natural Gas.  91.5 lb/hr/CT;

- Fuel Oil.  920 lb/hr/CT; and

- Natural Gas and Fuel Oil.  568 TPY/CT for the combined total of emissions generated through natural gas and fuel oil firing.

SO2 emissions are based on a maximum 0.5% sulfur content, by weight, in oil for hourly emissions and an average sulfur content of 0.3%, by weight, for annual emissions.

- BACT Fuel Sulfur Content Limit.  The average annual sulfur content of the light distillate oil shall not exceed 0.3%, by weight, during any consecutive 12-month period.  The maximum sulfur content of the light distillate oil shall not exceed 0.5% by weight.

- NSPS SO2 Limits.  The permittee shall comply with either of the following conditions:

- No permittee shall cause to be discharged into the atmosphere from any stationary gas turbine any gases which contain SO2 in excess of 0.015% by volume at 15% O2 and on a dry basis.

- No owner or operator subject to the provisions of this subpart shall burn in any stationary gas turbine any fuel which contains total sulfur in excess of 0.8 percent by weight (8000 ppmw).

[Rule 62-212.400(BACT), F.A.C.; 40 CFR 60.333; and, Permit Nos. PSD-FL-146, Specific Conditions 4 & 11 & 0850001-032-AC/PSD-FL-146H & 327F]

- Unless otherwise established in an air construction permit, provisions in NSPS Subpart A do not apply to SIP limits.  Therefore, Specific Condition B.16 (formerly B.9 of Permit No. 0850001-040-AV) has been revised as follows:

- Opacity.

- Visible Emissions.   Visible emissions As determined by stack test, VE shall neither exceed 10% opacity while burning natural gas, nor 20% opacity while burning distillate oil.  [Permit No. PSD-FL-146, Specific Condition No. 8.]

- Compliance.  Compliance with standards in 40 CFR 60, other than opacity standards, shall be determined in accordance with performance tests established by 40 CFR 60.8, unless otherwise specified in the applicable standard.  [40 CFR 60.11(a)]

- Startup, Shutdown and Malfunction.  The opacity standards set forth in 40 CFR 60 shall apply at all times except during periods of startup, shutdown, malfunction, and as otherwise provided in the applicable standard.  [40 CFR 60.11(c)]

- To reflect current Title V air operation permit format standards and the current version of Rule 62-210.700, F.A.C., Specific Condition B.17 has been added to this subsection.  Language has been added to this condition to reflect that alternative excess emissions standards apply to NOX emissions measured using a CEMS.  The revision appears as follows:

- Excess Emissions Allowed.  Except as provided in Specific Condition B.19, excess emissions resulting from startup, shutdown or malfunction of any emissions unit shall be permitted provided that best operational practices to minimize emissions are adhered to and the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C.]

- Excess emissions provisions from NSPS Subpart GG were incorporated into the body of this permit as Specific Conditions B.21, B.22 and B.23.

- Specific Condition B.25 (formerly B.14 of Permit No. 0850001-040-AV) has been deleted.  The combustion turbines in this subsection utilize a NOX CEMS that meets the requirements of 40 CFR 75.  Pursuant to 40 CFR 60.334(b)(3)(iii), a 40 CFR 75 CEMS may be used to satisfy the requirements of 40 CFR 60.334, thus, making Specific Condition B.25 redundant.

- To reflect the current version of NSPS Subpart GG, Specific Condition B.26 (formerly B.15 in Permit No. 0850001-040-AV) has been revised as follows:

- Custom Fuel Monitoring Schedule for Natural Gas.  The Martin Power Plant facility requested approval for and was granted approval to utilize a customized fuel monitoring schedule for natural gas firing, pursuant to 40 CFR 60.334.  The schedule is as follows:

- Nitrogen Content.  Monitoring of fuel nitrogen content shall not be required if natural gas is the only fuel being fired in the gas turbines.

- Sulfur Monitoring.

- Analysis for fuel sulfur content of the natural gas shall be conducted using one of the approved ASTM reference methods for the measurement of sulfur in gaseous fuels, or an approved alternative method.  The reference methods are ASTM D1072-80, ASTM D3031-81, ASTM D3246-81, ASTM D4468-85 and ASTM D6667-01 and ASTM D4084-82, as referenced in 40 CFR 60.335(b)(210), and ASTM D4084-82 (if the total sulfur content of the gaseous fuel during the most recent performance test was less than 0.4 weight percent), or the latest edition(s).

- This custom fuel monitoring schedule shall become effective on the date this permit becomes valid. Effective the date of this custom schedule, sulfur monitoring shall be conducted twice monthly for six months.  If this monitoring shows little variability in the fuel sulfur content, and indicates consistent compliance with 40 CFR 60.333, then sulfur monitoring shall be conducted once per quarter for six quarters.  If monitoring data is provided by the applicant which demonstrates consistent compliance with the requirements herein the applicant may begin monitoring as per the requirements of 2(c).

- If after the monitoring required in item 2(b) above, or herein, the sulfur content of the fuel shows little variability and, calculated as sulfur dioxide, represents consistent compliance with the sulfur dioxide emission limits specified under 40 CFR 60.333, sample analysis shall be conducted twice per annum.  This monitoring shall be conducted during the first and third quarters of each calendar year.

- Should any sulfur analysis as required in items 2(b) or 2(c) above indicate noncompliance with 40 CFR 60.333, the owner or operator shall notify the Department of such excess emissions and the custom schedule shall be re-examined by the Environmental Protection Agency.  Sulfur monitoring shall be conducted weekly during the interim period when this custom schedule is being re-examined.

- Change in Fuel Supply.  If there is a change in fuel supply, the owner or operator must notify the Department of such change for re-examination of this custom schedule.  A substantial change in fuel quality shall be considered as a change in fuel supply.  Sulfur monitoring shall be conducted weekly during the interim period when this custom schedule is being re-examined.

- Fuel Records.  Records of sample analysis and fuel supply pertinent to this custom schedule shall be retained for a period of five years, and be available for inspection by personnel of federal, state, and local air pollution control agencies.

[40 CFR 60.334(h)(1), (i)(3) & 60.335(b)(10)(ii); Permit No. PSD-FL-146; and, NSPS Custom Fuel Monitoring Schedule dated 10/14/1997]

- Specific Condition B.27 has been added to reflect the incorporation of provisions from NSPS Subpart GG fuel sulfur monitoring, specifically a fuel sulfur monitoring exemption for natural gas from 40 CFR 60.334(h)(3).

- To reflect the incorporation of Permit No. 0850001-041-AC (PSD-FL-146J and 327G) Specific Condition B.28 (formerly B.16 of Permit No. 0850001-040-AV) has been deleted.  The language in this condition comes from Guidance Document No. DARM-EM-03, which established temperature monitoring system operational procedures.  This guidance document was established by Permit No. 0850001-005-AC/PSD-FL-146(G).  Since the revision made by Permit No. 0850001-041-AC (PSD-FL-146J and 327G), temperature monitoring is no longer required, making this condition obsolete.

- To reflect the incorporation of Permit No. 0850001-041-AC (PSD-FL-14J and 327G), Specific Condition B.29 (formerly B.17 of Permit No. 0850001-040-AV) has been revised as follows:

- Monitoring of Inlet Foggers.  The permittee shall monitor and record both the hours of operation for the inlet foggers. and the degrees of cooling afforded by the inlet foggers.  Computation of the degree-hour will be performed as follows:

- ⁰F-hours = (Number of hours of inlet fogger operating time) x (⁰F of cooling)

- Degrees of Cooling shall be calculated by subtracting the fogged compressor inlet air temperature from the unfogged compressor inlet temperature (upstream of the fogger).  The above calculation shall be performed for each hour of fogger operation.  Calculation records shall be maintained on the plant site and made available for inspection upon request.

The temperature drop across the inlet foggers shall be monitored whenever water is injected at the foggers and hourly average temperature drops shall be calculated and recorded along with hours of operation automatically using a computer system.  The product of each hour of fogger operation and the average temperature depression for that hour (degree F-hours) shall be summed for each calendar year and shall be submitted to the Department’s Southeast District Office with the Annual Operating Report.  The temperature monitoring system shall be calibrated annually.  [Rule 62-213.440, F.A.C. and Permit No. 0850001-041005-AC/PSD-FL-146J(G) & 327G]

- Specific Conditions B.32 and B.33 (formerly B.20 and B.21 of Permit No. 0850001-040-AV) have been deleted.  The emissions units in this subsection do not utilize a COMS and have no requirements to install and maintain a COMS.

- To reflect that the emissions units in this subsection do not utilize a COMS, Specific Conditions B.35 and B.38 (formerly B.23 and B.26 of Permit No. 0850001-040-AV) have been revised as follows:

- Frequency of Operation.  During each full unit operating hour, each CEMS must complete a minimum of one cycle of operation (sampling, analyzing and data recording) for each 15-minute quadrant of the hour, to validate the hour.  For partial unit operating hours, at least one valid data point must be obtained for each quadrant of the hour in which the unit operates.  For unit operating hours in which required quality assurance and maintenance activities are performed on the CEMS, a minimum of two valid data points (on in each of two quadrants) are required to validate the hour.  Except for system breakdowns, repairs, calibration checks, and zero and span adjustments required under 40 CFR 60.13(d), all continuous monitoring systems (CMS) shall be in continuous operation and shall meet minimum frequency of operation requirements as follows:

- All continuous monitoring systems referenced by 40 CFR 60.13(c) for measuring opacity of emissions shall complete a minimum of one cycle of sampling and analyzing for each successive 10-second period and one cycle of data recording for each successive 6-minute period.

- All continuous monitoring systems referenced by 40 CFR 60.13(c) for measuring emissions, except opacity, shall complete a minimum of one cycle of operation (sampling, analyzing, and data recording) for each successive 15-minute period.

[40 CFR 60.334(b)(2)13(e)(1) and (2)]

- Data Reduction.  Owners or operators of all continuous monitoring systems for measurement of opacity For the purpose of complying with NSPS Subpart GG standards, the permittee shall reduce all CEMS data to 6-minute averages and for continuous monitoring systems other than opacity to 1-hour averages for time periods as defined in 40 CFR 60.2.  Six-minute opacity averages shall be calculated from 36 or more data points equally spaced over each 6-minute period.  For continuous monitoring systems other than opacity, 1One-hour averages shall be computed from four or more data points equally spaced over each 1-hour period.  Data recorded during periods of continuous monitoring system breakdowns, repairs, calibration checks, and zero and span adjustments shall not be included in the data averages computed under this paragraph.  An arithmetic or integrated average of all data may be used.  The data may be recorded in reduced or non-reduced form (e.g., ppm pollutant and percent O2 or ng/J of pollutant).  All excess emissions shall be converted into units of the standard using the applicable conversion procedures specified in subparts.  After conversion into units of the standard, the data may be rounded to the same number of significant digits as used in the applicable subparts to specify the emission limit (e.g., rounded to the nearest 1 percent opacity).  [40 CFR 60.13(h)]

- Specific Condition B.39 (formerly B.27 of Permit No. 0850001-040-AV) has been reorganized as follows:

- Test Methods.  When Rrequired, tests shall be performed in accordance with the following reference methods:

| Method | Description of Method and Comments |
| --- | --- |
| 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| 3 | Determination of Oxygen and Carbon Dioxide Concentrations in Emissions from Stationary Sources |
| 5 or 17 | Method for Determining Particulate Matter Emissions (All PM is assumed to be PM10.) |
| 7E | Determination of Nitrogen Oxide Emissions from Stationary Sources |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |
| 10 | Determination of Carbon Monoxide Emissions from Stationary Sources {Note: The method shall be based on a continuous sampling train.} |
| 20 | Determination of Nitrogen Oxides, Sulfur Dioxide and Diluent Emissions from Stationary Gas Turbines |

The above methods are described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  The stack test for each turbine shall be performed within 10% of the maximum heat rate input for the tested operating temperature.  See Specific Condition B.2 for utilization of ambient temperature versus heat input curves during compliance testing.  [Rule 62-204.800, F.A.C.; and, Permit No. 0850001-032-AC/PSD-FL-327B & 146C]

Unless specifically exempted per Florida Rule 62-297, F.A.C., annual compliance tests shall be conducted for each CT to demonstrate compliance with the permitted emissions standards for normal gas firing, gas firing with power augmentation, and backup distillate oil firing.  CO and NOX performance tests shall be conducted concurrently.  If conducted at permitted capacity, NOX emissions data collected during the annual NOX continuous monitor Relative Accuracy Test Assessments (RATA) required pursuant to 40 CFR 75 may be substituted for the required annual performance test.  Tests required on an annual basis shall be conducted at least once during each calendar year (January 1st to December 31st).

For each CT that fires distillate oil for less than 400 hours during the previous calendar year, the annual performance tests when firing distillate oil for the current calendar year of operation are not required.  CT’s firing more than 400 hours on oil will also be required to demonstrate compliance with PM standards.

For each CT that operates with power augmentation for less than 400 hours during the previous calendar year, the annual performance tests when operating with power augmentation for the current calendar year of operation are not required.  During power augmentation each unit shall comply with the emissions limits stated in Specific Condition B.9.

[Rules 62-204.800 & 62-297.310(7)(a)4., F.A.C.; 40 CFR 60, Appendix A; and, Permit Nos. PSD-FL-146, Specific Condition No. 10 & 0850001-016-AC(PSD-FL-327B and PSD-FL-146C)]

- Language removed from Specific Condition B.39 (see item 57) has been added to Specific Condition B.40 (formerly B.28 of Permit No. 0850001-040-AV), which has been revised as follows:

- Annual Compliance Tests Required.  Unless exempted by Chapter 62-297, F.A.C. or Specific Condition B.41, Dduring each calendar year (January 1st to December 31st), each CT shall be tested to demonstrate compliance with the emissions standards for PM (only while firing oil), VE, CO, and NOX and PM for normal gas firing, gas firing with power augmentation and backup distillate oil firing (for oil only) with the fuel(s) used for more than 400 hours in the preceding 12-month period.  No other test methods may be used for compliance testing unless prior DEP approval is received in writing.  VOC testing is only required if the annual CO test indicates an exceedance of the CO standard.  CO and NOX compliance tests shall be conducted concurrently.  If conducted at permitted capacity, NOX emissions data collected during the annual NOX CEMS Relative Accuracy Test Audit (RATA), required pursuant to 40 CFR 75, may be substituted for the required annual compliance test.  [Rules 62-212.400(BACT) & 62-297.310(78), F.A.C., and, Permit Nos. PSD-FL-146, Specific Condition 10 & 0850001-032-AC/(PSD-FL-146H / PSD-FL-327F) 0850001-016-AC/PSD-FL-327B & 146C, Specific Condition 10]

- Language from Specific Condition B.39 (see item 57) has been converted to a separate specific condition as follows:

- Compliance Tests Not Required.

- Power Augmentation.  Annual compliance tests when operating in power augmentation mode are not required for any CT that operates in power augmentation mode for less than 400 hours in the previous calendar year.

- Distillate Oil Firing.  Annual compliance tests when firing distillate oil are not required for any CT that fires distillate oil for less than 400 hours in the previous calendar year.  CTs firing more than 400 hours on oil will also be required to demonstrate compliance with PM emissions standards.

[Rule 62-297.310(8); and, Permit No. 0850001-032-AC/PSD-FL-146H & 327F, Specific Condition 10]

- Because all VOC compliance tests are conditional, language from Permit Nos. PSD-FL-146 and 0850001-032-AC/PSD-FL-146H and 327F has been converted into a separate condition as follows:

- VOC Compliance Requirements.  Annual testing and testing prior to permit renewal are only required if the annual CO test indicates an exceedance of the CO emissions standards (see Specific Condition B.12).  [Permit Nos. PSD-FL-146 & 0850001-032-AC/PSD-FL-146H & 327F, Specific Condition 10]

- To incorporate minor clarifications and the current version of Rule 62-297.310, F.A.C., Specific Condition B.43 (formerly B.29 of Permit No. 0850001-040-AV) has been revised as follows:

- Compliance Tests Prior To Renewal.  Unless specifically exempted per Florida Rule Chapter 62-297, F.A.C. (see condition TR7.b.(3) in Appendix TR – Facility-wide Testing Requirements), prior to permit renewal, compliance tests shall be performed for the following pollutants:  VE, CO, VOC (if the annual CO test indicates an exceedance of the CO standard), NOX (if substitution with the 40 CFR 75 RATA is not performed) and PM (if oil is fired).  The permittee may submit the most recent compliance test to satisfy this requirement, provided such test occurred within the term of the current operating permit.  [Rule 62-297.310(78)(ab)3., F.A.C.; and, 0850001-032-AC/ (PSD-FL-146H/ & PSD-FL-327F)]

- Specific Conditions B.45 and B.46 (formerly B.31 and B.32) have been deleted.  Specific Condition B.45 has been deleted, because 40 CFR 60.335 outlines stack test procedures for NOX, which are not applicable because the compliance method for NOX is a CEMS.  Specific Condition B.46 because SO2 and NOX compliance methods are already present in the body of the permit, making this condition redundant.

- Specific Condition B.47 (formerly B.33 of Permit No. 0850001-040-AV) has been revised, because Permit No. PSD-FL-146 already outlines fuel sulfur content testing requirements.  Unless otherwise stated in an air construction permit or rule, testing provisions in NSPS Subpart GG are only used to demonstrate compliance with the applicable NSPS Subpart GG standard.  Therefore, this condition has been revised as follows:

- Sulfur Content.  The owner or operator shall determine compliance with the sulfur content standard of 0.58 percent, by weight, by following all requirements of 40 CFR 60.335. (See Appendix NSPS Subpart GG).  [40 CFR 60.335]

- Minor clarifications to Specific Condition B.48 (formerly B.34 of Permit No. 0850001-040-AV) were made as follows:

- Fuel Analysis.  To meet the requirements of 40 CFR 60.334, the owner or operator shall use the methods specified in 40 CFR 60.335 and the Custom Fuel Monitoring Schedule for Natural Gas (See Specific Condition B.26) to determine the nitrogen and sulfur content of the fuel being burned.  The analysis may be performed by the owner or operator, a service contractor retained by the owner or operator, the fuel vendor, or any other qualified agency.  See Specific Condition B.15 that describes the approved Custom Fuel Monitoring Schedule for Natural Gas for this facility.  [40 CFR 60.335]

- Fuel sulfur content limits from Specific Condition B.49 (formerly B.35 of Permit No. 0850001-040-AV) for distillate oil have been moved to Emission Limitations and Standards (see Specific Condition B.15 and item 46).  This condition has been revised as follows:

- Distillate Oil Sulfur Content Testing.  The average sulfur content of the light distillate oil shall not exceed 0.3%, by weight, during any consecutive 12-month period.  The maximum sulfur content of the light distillate fuel oil shall not exceed 0.5%, by weight.  The 12-month average sulfur content (see Specific Condition B.15, paragraph b) shall be calculated as a weighted average based upon the sulfur content of the oil and the amount burned on a daily basis.  Compliance shall be demonstrated in accordance with the requirements of 40 CFR 60.334 by testing for sulfur content, for nitrogen content, and for heating value of oil storage tanks once per day when firing oil using ASTM D 2880-96.  [Rule 62-213.440, F.A.C.; applicant agreement with EPA on March 3, 1998; and PSD-FL-146, Specific Condition No. 11]

- EPA Method 9 is required for VE testing, pursuant to Permit No. PSD-FL-146 and Permit No. 0850001-016-AC/PSD-FL-327B and 146C, Specific Condition 10.  Language from 40 CFR 60.11(b) that incorporates EPA Method 9, as described in Appendix A of 40 CFR 60, is redundant.  Therefore, Specific Condition B.50 (formerly B.36 of Permit No. 0850001-040-AV) has been deleted.

- To reflect revisions in made to Recordkeeping and Reporting Requirements and current Title V air operation permit format standards, Specific Condition B.51 (formerly B.37 of Permit No. 0850001-040-AV) has been revised as follows:

- Reporting Schedule.  The following reports and notifications shall be submitted to the Compliance Authority:

| Report | Reporting Deadline | Related Condition(s) |
| --- | --- | --- |
| NSPS 40 CFR 60 Subpart GG Reports | Quarterly Semiannually. | B.41 B.55 |
| Notice of Operational Changes | 60 days prior to change. | B.43 |
| Performance Reports | Semi-annually | B.45 |

[Rule 62-213.440(1)(b), F.A.C.]

- Permit No. 0850001-041-AC/PSD-FL-146J and 327G authorized the permittee to submit quarterly excess emission reports on a semiannual basis.  Because this condition requires reporting in accordance with NSPS Subparts A and GG, Specific Conditions B.42 and B.45 of Permit No. 0850001-040-AV have been combined into Specific Condition B.55, which appears as follows:

- Quarterly Semiannual Reports.  Quarterly Semiannual excess emission reports, in accordance with 40 CFR 60.7 and 60.334, shall be submitted to the Compliance Authority Department’s Southeast District Office.  Annual reports shall be submitted to the District Compliance Authority office in accordance with Rule 62-2.700(7), F.A.C. Condition TR9. in Appendix TR – Facility-wide Testing Requirements.  Semiannual reports shall be postmarked by the 30th day following the end of each 6-month period.  Each semiannual report shall include the following:

- The magnitude of excess emissions computed in accordance with 40 CFR 60.13(h), any conversion factor(s) used, and the date and time of commencement and completion of each time period of excess emissions.  The process operating time during the reporting period.

- Specific identification of each period of excess emissions that occurs during startups, shutdowns, and malfunctions of the affected facility.  The nature and cause of any malfunction (if known), the corrective action taken or preventative measures adopted.

- The date and time identifying each period during which the continuous monitoring system was inoperative except for zero and span checks and the nature of the system repairs or adjustments.

- When no excess emissions have occurred or the continuous monitoring system(s) have not been inoperative, repaired, or adjusted, such information shall be stated in the report.

- Ambient conditions (temperature, pressure and humidity) at the time of the excess emission period.  If the worst case ISO correction factor, as specified in 40 CFR 60.334(b)(3)(ii), is used; or, if the ISO correction equation under the provisions of 40 CFR 60.335(b)(1) is not used, the ambient conditions do not have to be reported.

- The nitrogen content of the fuel during the period of excess emissions (only if the permittee has claimed an emission allowance for fuel bound nitrogen).

[Permit No. PSD-FL-146, Specific Condition No. 19 & 0850001-041-AC/PSD-FL-146J & 327G]

- Because NSPS reporting is accounted for in Specific Condition B.55, Specific Condition B.56 (formerly B.42 of Permit No. 0850001-040-AV) is obsolete and, therefore, has been deleted.

- Specific Condition B.57 (formerly B.43 of Permit No. 0850001-040-AV) incorporates language from 40 CFR 60.7(a)(4), which requires the permittee to notify the Department of any physical or operational change to an existing facility that may increase the emission rate of any air pollutant to which a standard applies, unless exempted in accordance with another NSPS subpart or 40 CFR 60.14(e).  This requirement, while pertinent, is best left in an appendix.  Physical or operational changes that increase emissions will be subject to Department review under the permitting process.  Therefore, this condition is redundant and has been removed from the body of this subsection.

- Specific Condition B.61 (formerly B.47 of Permit No. 0850001-040-AV) outlines procedures to reduce reporting frequency to a semiannual basis.  All reporting requirements in Section III., Subsection B are on a semiannual basis.  This condition is redundant and has been deleted.

- A minor correction was made to Specific Condition B.63 (formerly B.48 of Permit No. 0850001-040-AV) as follows:

- NSPS Requirements.  This unit shall comply with all applicable provisions of NSPS in 40 CFR 60 including Subpart A (General Provisions) and Subpart GG (Standards of Performance for Stationary Gas Turbines).  See Appendix NSPS Subpart A and Appendix NSPS Subpart GG for provisions of NSPS Subparts A and DcGG, respectively.  [Rule 62-204.800(8)(b)42. & (8)(d), F.A.C.; and, 40 CFR 60, Subparts A & GG]

Changes to Section III., Subsection C.

- Specific Condition C.13 has been removed from Test Methods and Procedures and added under Emission Limitations and Standards, because this condition outlines work practice standards.  It appears as Specific Condition C.5.

- Specific Condition C.8 (formerly C.7 of Permit No. 0850001-040-AV) and Monitoring Requirements have been deleted.  This condition is the sole monitoring requirement and, after the revision in Permit No. 0850001-041-AC/PSD-FL-146J and 327G, has been added under Recordkeeping and Reporting as Specific Condition C.19.  The changes appear as follows:

Monitoring Requirements

- Fuel Flow Monitoring.  The permittee shall install and maintain equipment to monitor and record the fuel flow rates of the auxiliary boiler.  [Permit No. 0850001-039-AC]

- Fuel Usage Recordkeeping.  The permittee shall record and maintain records of the amount of natural gas combusted during each calendar month by this unit using the hours of operation each month, the maximum heat input rate of 13.23 MMBtu/hr and the most recent natural gas heating value data from the vendor.  [40 CFR 60.48c(g)(2) & Permit No. 0850001-041-AC/PSD-FL-146J & 327G]

- Changes made in item 74 make provisions in Specific Condition C.20 (formerly C.19 in Permit No. 0850001-040-AV) obsolete.  This condition has been revised as follows:

- NSPS Subpart Dc Recordkeeping.  The permittee shall comply with the following recordkeeping provisions:

- The amount of fuel combusted during each calendar month shall be recorded and maintained; or

- If all steam generating units in the facility (including steam generating units not subject to 40 CFR 60, Subpart Dc) combust natural gas and distillate oil meeting the most current requirements of 40 CFR 60.42c to use fuel certification to demonstrate compliance with the SO2 standard may elect to record and maintain records of the total amount of each steam generating unit fuel delivered to the facility property during each calendar month.

- All records required under this specific condition shall be maintained by the owner or operator of the affected facility for a period of 5 years following the date of such records.

[Rules 62-204.800(8)(b)4., F.A.C. & 62-213.205(1)(e); and, 40 CFR 60.48c(g)(2), (3) & (i)]

Changes to Section III., Subsection D.

- To reflect the generating capacity of the upgraded combustion turbine-electrical generators in Martin Unit 8 and current Title V air operation permit format standards, the EU description has been revised as follows:

Each CT (8A, 8B, 8C and 8D) consists of a nominal 170 207.4 MW General Electric Model PG7241(FA) gas turbine-electrical generator set, an automated gas turbine control system, an inlet air filtration system, an evaporative inlet air cooling system, and associated support equipment.  Each CT is coupled with a HRSG equipped with a 495 MMBtu/hr natural gas fired duct burner.  Steam from each HRSG is delivered to the single steam turbine driven electrical generator that serves all four CT/HRSG systems, which has a nominal capacity of 470 MW.  The total nominal generating capacity of the (one “4-on-1” set) combined cycle unit is 1,150 1,300.4 MW.  The stack parameters for each CT/HRSG are: 120 feet in height; 19 feet in diameter; exhaust flow rates of 1,004,200 acfm for natural gas firing and 1,193,900 acfm for oil firing; and gas exit temperatures of 202°F (gas) and 295°F (oil).  At a compressor inlet air temperature of 59°F, the heat input rate to each CT based on lower heating value (LHV) is approximately 1,660 MMBtu/hr (gas) and 1,885 MMBtu/hour (oil).

# The CTs use natural gas as the primary fuel and distillate oil as a restricted alternate fuel.  The efficient combustion of natural gas at high temperatures minimizes emissions of CO, PM/PM10, SAM, SO2, and VOC.  NOX emissions are reduced by Dry Low-NOX (DLN) combustion technology.  A selective catalytic reduction (SCR) system combined with DLN combustion technology further reduces NOX emissions during combined cycle mode.  Each CT is equipped with CEMS to measure and record CO and NOX emissions as well as flue gas O2 or CO2 content.  CAM does not apply since these emissions units have NOX CEMS which are used to demonstrate continuous compliance.

Emissions Units 8A and 8B commenced commercial simple cycle operation in November 2001.  In a permitting action issued on 2003, these two existing units in addition to two new units conformed the (one “4-on-1” set) combined cycle combustion system (Units 8A, 8B, 8C and 8D) that commenced commercial operation on June 30, 2005.

{Permitting Note:  These emissions units are regulated under:  40 CFR 60, Subpart A, General Provisions, and Subpart KKKK, Standards of Performance for Stationary Combustion Turbines, adopted by reference in Rules 62-204.800(8)(d) and (8)(b)84., F.A.C., respectively; 40 CFR 63, Subpart A, General Provisions, and Subpart YYYY, NESHAP for Stationary Combustion Turbines, adopted by reference in Rule 62-204.800(11)(d)1. and (11)(b)81., F.A.C., respectively; Rule 62-212.400, F.A.C., BACT for CO, NOX, PM/PM10, SO2, SAM and VOC under Permit No. 0850001-010-AC/PSD-FL-327, which was issued on 4/16/2003 and modified on 7/7/2005, and superseded Permit No. PSD-FL-286; and, Chapter 62-214, F.A.C., the Phase II Acid Rain Program as specified in Section IV of this Permit.

On March 5, 2004, EPA promulgated 40 CFR 63, Subpart YYYY – National Emission Standards for Hazardous Air Pollutants for Stationary Combustion Turbines built after January 14, 2003.  Unit 8 was under contractual obligations before this date and is therefore an existing unit.  Currently, ‘existing combustion turbines’ are not required to meet the emission limitations, notifications, reporting or any other requirements of 40 CFR 63, Subpart YYYY or 40 CFR 63, Subpart A, pursuant to 40 CFR 63.6090(b)(4).  EPA may at a future date promulgate standards for existing units.}

{Permitting Note: These emissions units are regulated under Acid Rain-Phase II, 40 CFR 60, Subpart KKKK, Standards of Performance for Stationary Combustion Turbines; and 40 CFR 63, Subpart YYYY, National Emission Standards for Hazardous Air Pollutants for Stationary Combustion Turbines, all adopted by reference in Rules 62-204.800(8) and 62-204.800(11), F.A.C.; Rule 212.400, F.A.C., Prevention of Significant Deterioration (PSD), Best Available Control Technology (BACT); Air Construction Permit PSD-FL-286; and Air Construction Permit PSD-FL-327 (0850001-010-AC) issued 04/16/03 and modified on 7/7/2005.  PSD-FL-327 replaced and superseded PSD-FL-286.

- Equipment has been changed to Equipment and Control Technology to reflect combustion turbine and control technology operating standards in this subsection.

- Specific Condition D.5 contains obsolete language pertaining to installation practices and initial testing requirements that has been deleted.  Minor corrections and clarifications were also made.  This condition appears as follows:

- Gas Turbine NOX Controls.

- DLN Combustion.  The permittee shall operate and maintain the General Electric DLN 2.6 combustion system (or better) to control NOX emissions from each gas turbine when firing natural gas.  Each system shall be maintained and tuned in accordance with the manufacturer’s recommendations.

- Water Injection.  The permittee shall install, operate, and maintain a water injection system to reduce NOX emissions from each gas turbine when firing distillate oil.  Prior to the initial emissions performance tests required for each gas turbine, the water injection system shall be tuned to achieve the permitted levels for CO and NOX emissions.  Thereafter, each system shall be maintained and tuned in accordance with the manufacturer’s recommendations.

- SCR System.  The permittee shall install, tune, operate, and maintain an SCR system to control NOX emissions from each gas turbine during combined cycle operation when firing either natural gas or distillate oil.  The SCR system consists of an ammonia injection grid, catalyst, ammonia storage, monitoring and control system, electrical, piping and other ancillary equipment.  The SCR system shall be designed, constructed and operated to achieve the permitted levels for NOX emissions and ammonia slip.  {Note:  In accordance with 40 CFR 608.130, the storage of ammonia shall comply with all applicable requirements of the Chemical Accident Prevention Provisions in 40 CFR 68 (see Facility-Wide Condition FW8).}

[Permit No. 0850001-010-AC/(PSD-FL-327)]

- To reflect current Title V air operation permit format standards, Specific Condition D.7 has been split into separate conditions (Specific Conditions D.9-D.17).  Revisions to CO monitoring provisions made in Permit No. 0850001-041-AC/PSD-FL-146J and 327F were incorporated into Specific Condition D.9.  Alternative VE standards during periods of startup and shutdown were incorporated into Specific Condition D15.  These conditions appear as follows:

- Emissions Standards.  Emissions from each gas turbine shall not exceed the following standards.

| Pollutant | Fuel | Method of Operation | Stack Test, 3-Run Average |  | CEMS Block Average |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | ppmvd @ 15% O2 | lb/hour | ppmvd @ 15% O2 |  |
| CO a | Oil | Combined Cycle | 14.4 | 64.7 | 15.0, 24-hr |  |
|  | Gas | Combined Cycle, Normal | 7.4 | 27.5 | 10.0, 24-hr |  |
|  |  | Combined Cycle, All Modes | NA | NA |  |  |
| NOX b | Oil | Combined Cycle w/SCR | 10.0 | 76.0 | 10.0, 24-hr |  |
|  | Gas | Combined Cycle w/SCR, Normal | 2.5 | 16.3 | 2.5, 24-hr |  |
|  |  | Combined Cycle w/SCR and DB | 2.5 | 23.6 |  |  |
|  |  | Combined Cycle w/SCR, All Modes | NA | NA |  |  |
| NOX (NSPS)g. | Gas | All modes (> 75% of peak load) | 15h. | N/A | N/A |  |
|  | Oil |  | 42i. | N/A | N/A |  |
|  | Oil/Gas | All modes (< 75% of peak load) | 96j. | N/A | N/A |  |
| PM/PM10 c | Oil/Gas | Combined Cycle | Fuel Specifications |  |  |  |
|  |  | Combined Cycle | Visible emissions shall not exceed 10% opacity for each 6-minute block average. |  |  |  |
| SAM/SO2 d | Oil/Gas | Combined Cycle | Fuel Specifications |  |  |  |
| SO2 (NSPS)g. | Oil/Gas | Combined Cycle | 0.060 lb SO2/MMBtu heat inputk. |  |  |  |
| VOC e | Oil | Combined Cycle | 2.5 | 6.0 |  | NA |
|  | Gas | Normal Combined Cycle | 1.3 | 2.8 |  | NA |
|  |  | Combined Cycle, w/DB and/or PA | 4.0 | 10.5 |  | NA |
| Ammonia f | Oil/Gas | Combined Cycle w/SCR | 5 | NA |  | NA |

- Compliance with the CO standards shall be demonstrated based on data collected by the required CEMS.  Compliance may also be determined by EPA Method 10.  Compliance with the 24-hour CO CEMS standards shall be determined separately for each method of operation based on the hours of operation for each method.  {Note:  A 24-hour compliance average may be based on as little as 1-hour of CEMS data or as much as 24-hours of CEMS data.}

- Compliance with the NOX standards shall be demonstrated based on data collected by the required CEMS.  Compliance may also be determined by EPA Method 7E or 20.  NOX mass emission rates are defined as oxides of nitrogen expressed as NO2.  {Note:  A 24-hour compliance average may be based on as little as 1-hour of CEMS data or as much as 24-hours of CEMS data.}

- The fuel specifications established in Specific Condition D.3 of this section, combined with the efficient combustion design and operation of each gas turbine represents the Best Available Control Technology (BACT) determination for PM/PM10 emissions.  Compliance with the fuel specifications, CO standards, and visible emissions standards shall serve as indicators of good combustion.  Compliance with the fuel specifications shall be demonstrated by keeping records of the fuel sulfur content.  Compliance with the visible emissions standard shall be demonstrated by conducting tests in accordance with EPA Method 9.  {Note:  PM10 emissions for gas firing are estimated at 11 lb/hour for combined cycle operation and 17 lb/hour for combined cycle operation with duct burning.  PM10 emissions for oil firing are estimated at 37 lb/hour for combined cycle operation.}

- The fuel sulfur specifications in Specific Condition D.3 of this section effectively limit the potential emissions of SAM and SO2 from the gas turbines and represent the Best Available Control Technology (BACT) determination for these pollutants.  Compliance with the fuel sulfur specifications shall be determined by the requirements in Specific Condition D.31.  {Note:  SO2 emissions for gas firing are estimated at 9.8 lb/hour for combined cycle operation and 12.8 lb/hour for combined cycle operation with duct burning.  SO2 emissions for oil firing are estimated at 99 lb/hour for combined cycle operation.  SAM emissions are estimated to be less than 10% of the SO2 emissions.}

- Compliance with the VOC standards shall be demonstrated by conducting tests in accordance with EPA Method 25A.  Optionally, EPA Method 18 may also be performed to deduct emissions of methane and ethane.  The emission standards are based on VOC measured as methane.

- Subject to the requirements of Specific Condition D.27. of this section, each SCR system shall be designed and operated for an ammonia slip target of less than 5 ppmvd corrected to 15% oxygen based on the average of three test runs.  Compliance with the ammonia slip standard shall be demonstrated by conducting tests in accordance with EPA Method CTC-027.

- NSPS emissions standards apply to emissions from each unit and its associated duct burner/HRSG.

- Acceptable alternative emissions standard of 54 nanograms per Joule (ng/J) of useful output (0.43 lb/MWh).

- Acceptable alternative emissions standard of 160 ng/J of useful output (1.3 lb/MWh).

- Acceptable alternative emissions standard of 590 ng/J of useful output (4.7 lb/MWh).

- Acceptable alternative emissions standard of 110 ng/J (0.90 lb/MWh) of gross output.

{Permitting Notes:  “DB” means duct burning.  “PA” means power augmentation.  “SCR” means selective catalytic reduction.  “NA” means not applicable.  The mass emission rate standards are based on a turbine inlet condition of 59 °F and may be adjusted to actual test conditions in accordance with the performance curves and/or equations on file with the Department.  These emissions units have not to date been operated in the high power modes (HPM) of peaking or power augmentation; therefore, a compliance plan is included to cover initial testing requirements for these HPM for emissions of CO and NOX.  See Appendix CP}

[Rules 62-204.800(8)(b)83., F.A.C. & 62-212.400(BACT), F.A.C.; 40 CFR 60.4325 & 60.4330; and Permit No. 0850001-010-AC (PSD-FL-327)]

- Adjustment of Emissions Standards.  The mass emission rate standards in Specific Conditions D.9, D.10 and D.16 are based on a turbine inlet condition of 59⁰F and may be adjusted to actual test conditions in accordance with the performance curves and/or equations on file with the Department.  [Rule 62-212.400(BACT), F.A.C.; and, Permit No. 0850001-010-AC/PSD-FL-327]

- CO Emissions.  Emissions from each gas turbine are subject to the following CO emissions standards:

- Natural Gas.

- As determined by stack test (3-run average), CO emissions shall not exceed the following during normal operation:

- 7.4 ppmvd at 15% O2; and

- 27.5 lb/hr.

- As determined by CEMS (optional), CO emissions shall not exceed 10.0 ppmvd at 15% O2, based on a 24-hour block average.

- Fuel Oil.

- As determined by stack test (3-run average), CO emissions shall not exceed the following:

- 14.4 ppmvd at 15% O2; and

- 64.7 lb/hr.

- As determined by CEMS (optional), CO emissions shall not exceed 15.0 ppmvd at 15% O2, based on a 24-hour block average.

Compliance with the CO standards shall either be demonstrated by stack tests using EPA Method 10 or based on data collected by the optional CEMS.  If a CEMS is used compliance with the 24-hour CO CEMS standards shall be determined separately for each method of operation based on the hours of operation for each method.  {Permitting Note:  A 24-hour compliance average may be based on as little as 1-hour of CEMS data or as much as 24-hours of CEMS data.}  [Rule 62-212.400(BACT), F.A.C.; and, Permit No. 0850001-010-AC/PSD-FL-327 & 0850001-041-AC/PSD-FL-146J & 327F]

- NOX Emissions.  Emissions from each gas turbine are subject to the following NOX emissions standards:

- Natural Gas.

- As determined by stack test (3-run average), NOX emissions shall not exceed the following during normal combined cycle operation with SCR:

- 2.5 ppmvd at 15% O2; and

- 16.3 lb/hr.

- As determined by stack test (3-run average), NOX emissions shall not exceed the following during combined cycle operation with SCR and duct burning (DB):

- 2.5 ppmvd at 15% O2; and

- 23.6 lb/hr.

- As determined by CEMS, NOX emissions shall not exceed 2.5 ppmvd at 15% O2 during combined cycle with SCR for all operating modes, based on a 24-hour block average.

- Fuel Oil.

- As determined by stack test (3-run average), NOX emissions shall not exceed the following during combined cycle operation with SCR:

- 10.0 ppmvd at 15% O2; and

- 76.0 lb/hr.

- As determined by CEMS, NOX emissions shall not exceed 2.5 ppmvd at 15% O2 during combined cycle operation with SCR for all operating modes, based on a 24-hour block average.

Compliance with the NOX standards shall be demonstrated based on data collected by the required CEMS.  Compliance may also be determined by EPA Method 7E or 20.  NOX mass emission rates are defined as oxides of nitrogen expressed as NO2.  {Permitting Note:  A 24-hour compliance average may be based on as little as 1-hour of CEMS data or as much as 24-hours of CEMS data.}  [Rule 62-212.400(BACT), F.A.C.; and, Permit No. 0850001-010-AC/PSD-FL-327]

{Permitting Note:  These emissions units have not to date been operated in the high-power modes (HPM) of peaking or power augmentation (PA).  Therefore, a compliance plan (see Appendix CP) is included to cover initial testing requirements for these HPM for emissions of CO and NOX.}

- NOX Emissions Limits – NSPS Subpart KKKK.  The concentration of NOX in the exhaust gas of each CT shall not exceed the following limits, based on a 30-unit operating day rolling average (as described in Specific Condition D.25, paragraph a):

- Natural Gas.  15 ppm at 15% O2 or 54 nanograms per Joule (ng/J) of useful output (0.43 pounds per megawatt-hour (lb/MWh)) while operating at 75% of peak load or greater.

- Fuel Oil.  42 ppm at 15% O2 or 160 ng/J of useful output (1.3 lb/MWh) while operating at 75% of peak load or greater.

- Low Load Operation.  96 ppm at 15% O2 or 590 ng/J of useful output (4.7 lb/MWh) while operating at less than 75% of peak load.

- Multiple Fuels.  If the total heat input to each CT is greater than or equal to 50% natural gas, the corresponding limit for a natural-gas fired turbine must be met when burning that fuel.  Similarly, when the total heat input to each CT is greater than 50% distillate oil, the corresponding limit for distillate oil must be met for the duration of the time that distillate oil is burned.

- Independent HRSGs.  Each HRSG must meet a limit of 54 ppm at 15% O2 or 110 ng/J of useful output (0.86 lb/MWh) while the duct burners are operating independent of the CT.

[40 CFR 60.4320(a), 60.4325 & 60.4350(h)]

- PM/PM10 Emissions Standards.  The fuel specifications established in Specific Condition D.3 of this section, combined with the efficient combustion design and operation of each gas turbine represents the Best Available Control Technology (BACT) determination for PM/PM10 emissions.  Compliance with the fuel specifications, CO standards and visible emissions standards shall serve as indicators of good combustion.  Compliance with the fuel specifications shall be demonstrated by keeping records of the fuel sulfur content.  Compliance with the visible emissions standard shall be demonstrated by conducting tests in accordance with EPA Method 9.  {Permitting Note:  PM10 emissions for gas firing are estimated at 11 lb/hour for combined cycle operation and 17 lb/hour for combined cycle operation with duct burning.  PM10 emissions for oil firing are estimated at 37 lb/hour for combined cycle operation.}  [Rule 62-212.400(BACT), F.A.C.; and, Permit No. 0850001-010-AC/PSD-FL-327]

- SAM/SO2 Emissions Standards.  The fuel sulfur specifications in Specific Condition D.3 of this section effectively limit the potential emissions of SAM and SO2 from the gas turbines and represent the BACT determination for these pollutants.  Compliance with the fuel sulfur specifications shall be determined by the requirements in Specific Condition  D.41.  {Permitting Note:  SO2 emissions for gas firing are estimated at 9.8 lb/hour for combined cycle operation and 12.8 lb/hour for combined cycle operation with duct burning.  SO2 emissions for oil firing are estimated at 99 lb/hour for combined cycle operation.  SAM emissions are estimated to be less than 10% of the SO2 emissions.}  [Rule 62-212.400(BACT), F.A.C.; and, Permit No. 0850001-010-AC/PSD-FL-327]

- SO2 Emissions Limits – NSPS Subpart KKKK.  The permittee must not burn in each CT any fuel which contains total potential sulfur emissions in excess of 26 ng SO2/J (0.060 lb SO2/MMBtu) heat input.  If the CT simultaneously fires multiple fuels, each fuel must meet this requirement.  [Rule 62-204.800(8)(b)82., F.A.C.; and, 40 CFR 60.4330(a)(2)]

- Visible Emissions.  VE from each CT shall not exceed the following limits:

- Combined Cycle Operation While Firing All Fuels.  10% opacity for each 6-minute block average; and

- Startup, Shutdown and Malfunction.  10% opacity except for up to ten, 6-minute averaging periods during a calendar day, which shall not exceed 20% opacity.

[Rule 62-212.400(BACT), F.A.C.; and, Permit No. 0850001-010-AC/PSD-FL-327]

- VOC Emissions.  As determined by stack test (3-run average), VOC emissions from each CT shall not exceed the following standards:

- Natural Gas.

- Normal Combined Cycle Operation.

- 1.3 ppmvd at 15% O2; and

- 2.8 lb/hr.

- Combined Cycle Operation with DB and/or PA.

- 4.0 ppmvd at 15% O2; and

- 10.5 lb/hr

- Fuel Oil and Combined Cycle Operation.

- 2.5 ppmvd at 15% O2; and

- 6.0 lb/hr.

Compliance with the VOC standards shall be demonstrated by conducting tests in accordance with EPA Method 25A.  Optionally, EPA Method 18 may also be performed to deduct emissions of methane and ethane.  The emission standards are based on VOC measured as methane.  [Rule 62-212.400(BACT), F.A.C.; and, Permit No. 0850001-010-AC/PSD-FL-327]

- Ammonia Slip.  Subject to the requirements of Specific Condition D.37 of this section, each SCR system shall be designed and operated for an ammonia slip target of less than 5 ppmvd corrected to 15% oxygen based on the average of three test runs.  Compliance with the ammonia slip standard shall be demonstrated by conducting tests in accordance with EPA Method CTC-027.  [Rule 62-212.400(BACT), F.A.C.; and, Permit No. 0850001-010-AC/PSD-FL-327]

- Specific Condition D.19 (Rule 62-210.700, F.A.C.) has been added to establish excess emissions provisions for emissions standards that do not utilize a CEMS for compliance.

- To reflect current Title V air operation permit format standards, the alternative VE standards in Specific Condition D.22 (formerly D.11 of Permit No. 0850001-040-AV) has been moved to Specific Condition D.15.

- Revisions made in Permit No. 0850001-041-AC/PSD-FL-146J and 327G have been incorporated into Specific Condition D.23 (formerly D.12 of Permit No. 0850001-040-AV) as follows:

- Excess Emissions Allowed.  As specified in this condition, excess emissions resulting from startup, shutdown, fuel switches, and documented malfunctions are allowed provided that operators employ the best operational practices to minimize the amount and duration of emissions during such incidents.  For each gas turbine/HRSG System, excess emissions of NOX and CO (if the option to use a CO CEMS is chosen)  resulting from startup, shutdown, fuel switches or malfunction shall be excluded from CEMS data in any 24-hour period for the following conditions (these conditions are considered separate events and each event may occur independently within any 24-hour period):

- Documented Malfunction:  For each gas turbine/HSRG system, excess emissions of NOX and CO (if the option to use a CO CEMS is chosen)resulting from documented malfunctions shall not exceed two hours in any 24-hour period.  A "documented malfunction" means a malfunction that is documented within one working day of detection by contacting the Compliance Authority by telephone, facsimile transmittal, or electronic mail.

- The combustion turbines in this subsection are not capable of simple cycle operation.  Thus, a minor correction to Specific Condition D.25 (formerly D.14 of Permit No. 0850001-040-AV) has been made as follows:

- NSPS Subpart KKKK Excess NOX Emissions Definition.  Excess emissions for simple and combined cycle operation are defined as follows:

- Current Title V air operation permit format standards have separate section for parametric monitors and CEMS/COMS.  Therefore, Specific Condition D.32 (formerly D.20 of Permit No. 0850001-040-AV), which pertains to water injection monitoring, has been added under Monitoring of Operations as Specific Condition D.29.

- To incorporate revisions made in Permit No. 0850001-041-AC/PSD-FL-146J and 327F, Specific Conditions D.34, D.35 and D.38 (formerly D.22, D.23 and D.26 of Permit No. 0850001-040-AV) have been revised as follows:

- Annual Compliance Tests.  During each calendar year (January 1st to December 31st), each gas turbine shall be tested to demonstrate compliance with the emission standards for visible emissions VE and CO (if a CO CEMS is not used).  Annual testing to determine the ammonia slip shall be conducted while firing the primary fuel.  CEMS data collected during the required Relative Accuracy Test Assessments (RATA) may be used to demonstrate compliance with the CO (if the optional CO CEMS is used) and NOX standards.  NOX emissions recorded by the CEMS shall be reported for each ammonia slip test run.  If an optional CO CEMS is used, CO emissions recorded by the CEMS shall be reported for the visible emissions VE observation period.  VOC testing is only required if the CO CEMS (optional) and/or stack test indicates an exceedance of the CO standard.  [Rules 62-212.400(BACT) & 62-297.310(7)(a)4, F.A.C.; and, Permit No. 0850001-010-AC/ (PSD-FL-327), 0850001-032-AC/PSD-FL-146H & 327F & 0850001-041-AC/PSD-FL-146J & 327G]

- Compliance Tests Prior To Renewal.  Unless specifically exempted per Florida Rule Chapter 62-297, F.A.C., prior to permit renewal, compliance tests shall be performed for the following pollutants:  VE, CO, VOC (only if the CO CEMS indicates an exceedance of the CO standard), NOX and ammonia slip.  VOC testing is only required if the CO CEMS (optional) and/or stack test indicates an exceedance of the CO standard.  [Rule 62-297.310(7)(a)3., F.A.C.; and, Permit Nos. 0850001-010-AC/ (PSD-FL-327), & 0850001-032-AC/ (PSD-FL-146H / & PSD-FL-327F) & 0850001-041-AC/PSD-FL-146J & 327G]

- Continuous Compliance.  The permittee shall demonstrate continuous compliance with the CO and NOX emissions standards based on data collected by the certified CEMS.  The permittee shall demonstrate compliance with the CO emissions standards using data collected by a certified CEMS if an optional CO CEMS is used.  Within 45 days of conducting any Relative Accuracy Test Assessments (RATA) on a CEMS, the permittee shall submit a report to the Compliance Authority summarizing results of the RATA.  Compliance with the CO emission standards also serves as an indicator of efficient fuel combustion, which reduces emissions of particulate matter and volatile organic compounds.  [Permit Nos. 0850001-010-AC/(PSD-FL-327) & 0850001-041-AC/PSD-FL-146J & 327G]

- To reflect the addition, removal and revision of specific conditions in this subsection, Specific Condition D.40 (formerly D.28 of Permit No. 0850001-040-AV) has been revised as follows:

- Reporting Schedule.  The following reports and notifications shall be submitted to the Compliance Authority:

| Report | Reporting Deadline | Related Condition(s) |
| --- | --- | --- |
| Notice of Capacity Monitoring | Daily. | D.30 D.41 |
| Notice of Monthly Operations | Monthly. | D.31 D.42 |
| NSPS Excess Emissions Report | Semiannual. | D.34 D.45 |
| Quarterly Permit Excess Emission Report | Quarterly Semiannual. | D.35 D.46D.46 |

[Rule 62-213.440(1)(b), F.A.C.]

- To reflect revisions made in Permit No. 0850001-041-AC/PSD-FL-146J and 327G, Specific Condition D.46 (formerly D.34 has been revised as follows):

- Quarterly Semiannual Permit Excess Emission Report:  Within 30 days following the end of each quarter 6-month period in a calendar year, the permittee shall submit a report to the Compliance Authority summarizing periods of excess CO (if the option to use a CO CEMS is chosen) and NOx emissions.  Such information shall also be summarized for combined cycle startups, combined cycle shutdowns, malfunctions, and major tuning sessions.  In addition, the report shall summarize the CEMS systems monitor availability for the previous quarter.  [Rules 62-4.130, 62-204.800, 62-210.700(6), F.A.C.; and 40 CFR 60.7; and, Permit No. 0850001-010-AC/(PSD-FL-327) & 0850001-041-AC/PSD-FL-146J & 327G]

Changes to Section III., Subsection E

- Startup date, rule applicability and EU description were added as follows:

This emissions unit is a 22-Cell Mechanical Draft Cooling Tower that commenced operation on December 10, 2004.

{Permitting Note:  This unit is subject to Rule 62-212.400, F.A.C., BACT for PM/PM10}

Changes to Section III., Subsection F

- A permitting note was marked by numbered item F.5.  This item has been deleted.  The permitting note remains, otherwise, unchanged.

Changes to Section III., Subsection G

- The EU description has been revised as follows:

This emissions unit is a diesel engine-driven emergency fire pump that services Martin Unit 8.  Exhaust gas exits a stack that is 6 ft high and 0.33 ft in diameter.  The following table provides important details for this emissions unit:

| E.U. ID No. | Engine Brake HP | Date of Construction | Model Year | Primary Fuel | Type of Engine | Displacement liters/cylinder (l/c) | Manufacturer |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | Model # |
|  |  |  |  |  |  |  | Engine Serial # |
| 022 | 197 | 2015 | 2015 | Diesel | Emergency | 1.13 | John Deere® |
|  |  |  |  |  |  |  | JU6H-UFADN0 |
|  |  |  |  |  |  |  | - |

{Permitting note:  This compression ignition (CI) internal combustion engine (ICE) is regulated under:  40 CFR 60, Subpart A, General Provisions, and 40 CFR 60, Subpart IIII, NSPS for Stationary CI ICE, adopted by reference in Rule 62-204.800(8)(d) and (8)(b)82., F.A.C., respectively; and 40 CFR 63, Subpart A, General Provisions, and 40 CFR 63, Subpart ZZZZ, NESHAP for Stationary Reciprocating Internal Combustion Engines (RICE), adopted by reference in Rule 62-204.800(11)(d) and (11)(b)82., F.A.C., respectively.  This subsection of the permit addresses a stationary CI RICE of model year 2007 or later, with a displacement of less than 10 liters per cylinder.  In accordance with the provisions of 40 CFR 63.6590(c)(1), meeting the requirements of 40 CFR 60, Subpart IIII, satisfies compliance with the requirements of 40 CFR 63, Subpart ZZZZ.  This part of the subsection addresses “new” stationary CI RICE less than 175 HP, with a displacement less than 10 liters per cylinder, that are located at a major source of HAP and that have been modified, reconstructed or commenced construction on or after 6/12/2006 and have a 2007 or later model year. This RICE is used as a fire pump.}

- Specific Condition G.1 is redundant.  NSPS and NESHAP applicability is addressed in the permitting note under the EU description.

- Minor corrections were made to Specific Condition G.2, to reflect provisions from NSPS Subpart IIII and minor clarifications.  The revisions were made as follows:

- Allowable Fuel.  The stationary RICE must use diesel fuel that meets the following requirements for non-road diesel fuel:

- Sulfur Content.  The sulfur content shall not exceed 15 ppm (0.0015% by weight) for non-road diesel fuel.  {Permitting Note:  equivalent to:  0.0006 lb SO2/hour}

- Cetane and Aromatic.  The fuel must have a minimum cetane index of 40 or must have a maximum aromatic content of 35 volume percent.

- Use of Existing Fuel.  Any existing diesel fuel purchased (or otherwise obtained) prior to October 1, 2010, may be used until depleted.

[40 CFR 60.4207(b) and 40 CFR 80.510(b)]

- To reflect current Title V air operation permit format standards, minor corrections and clarifications were made to Specific Condition G.3, which appears as follows:

- Restricted Hours of Operation.

  - Emergency Situations.  There is no time limit on the use of emergency stationary RICE in emergency situations.  [40 CFR 60.4211(f)(1)]

  - Maintenance and Testing.  Each This RICE is authorized to operate for the purpose of maintenance checks and readiness testing, provided that the tests are recommended by federal, state, or local government, the manufacturer, the vendor, or the insurance company associated with the engine. Maintenance checks and readiness testing of such units is limited to 100 hours per year.  The owner or operator may petition the Administrator for approval of additional hours to be used for maintenance checks and readiness testing, but a petition is not required if the owner or operator maintains records indicating that Federal, State, or local standards require maintenance and testing of emergency RICE beyond 100 hours per year.  [40 CFR 60.4211(f)(2)(i)]

  - Other Non-emergency Situations.  Each RICE cannot be used for peak shaving or to generate income for a facility to supply power to an electric grid or otherwise supply power as part of a financial arrangement with another entity.  Each RICE may be operated for up to 50 hours per calendar year in non-emergency situations.

[40 CFR 60.4211(f)(3)]

- Minor clarifications were made to Specific Conditions G.4, G.5 and G.6 to reflect accurate citations and current Title V air operation permit format standards:

- NMHC + NOx Emissions.  Non-methane hydrocarbons and nitrogen oxide emissions shall not exceed 4.0 g/KW-hr (equivalent to 3.0 g/HP-hr).  {Permitting Note:  equivalent to:  1.3 lb/hour}.  [40 CFR 60.4205(bc) , Subpart IIII, Table 4 & 40 CFR 89.112(a)]

- CO Emissions.  Carbon monoxide emissions shall not exceed 3.5 g/KW-hr (equivalent to 4.8 g/HP-hr)..  {Permitting Note:  equivalent to:  1.1 lb/hour}.  [40 CFR 60.4205(bc), Subpart IIII, Table 4 & 40 CFR 89.112(a)]

- PM Emissions.  Particulate matter emissions shall not exceed 0.20 g/KW-hr (equivalent to 0.15g/HP-hr) {Permitting Note:  equivalent to:  0.06 lb/hour}.  [40 CFR 60.4205(bc), Subpart IIII, Table 4 & 40 CFR 89.112(a)]

- Specific Condition G.7 has been deleted, revised and reinserted under Testing and Compliance Requirements to reflect current Title V air operation permit format standards.  Language from 40 CFR 60.4206 was added to this condition, which appears as follows:

Testing and Compliance Requirements

- Operation and Maintenance.  The owner or operator must operate and maintain the stationary CI ICE according to the manufacturer's written emission-related instructions.  In addition, owners and operators may only change those settings that are permitted by the manufacturer.  The owner or operator must meet the requirements of 40 CFR 89, 94 and/or 1068, as they apply.  This RICE must be maintained and operated to meet the emissions limits in Specific Conditions G.4, G.5 and G.6 over the entire life of the engine.  [40 CFR 60.4206 & 60.4211(a)]

- Specific Conditions G.10, G.11 and G.12 were added to reflect the addition of provisions from 40 CFR 60.4211(c), 60.4211(g) and 60.4212.

- Specific Condition G.13 (formerly G.9 of Permit No. 0850001-040-AV) has been deleted, because 40 CFR 60.4211(b) does not apply to engines manufactured after 2011.

- To reflect current Title V air operation permit format standards, Specific Condition G.24 (formerly G.16 of Permit No. 0850001-040-AV) has been deleted and added as Specific Condition G.14.

- Specific Conditions G.15, G.16 and G.17 have been deleted because the conditions added in item 96 more accurately reflect the applicable provisions of NSPS Subpart IIII.

- To reflect current Title V air operation permit format standards, the Recordkeeping Requirements section has been changed to Recordkeeping and Reporting Requirements.

- Specific Conditions G.18 and G.20 have been added to reflect current Title V air operation permit format standards.

- Minor clarifications were made to Specific Condition G.19 (formerly G.13 of Permit No. 0850001-040-AV), which appears as follows:

- Hours of Operation Required Records.  Owner or operator must keep records of the operation of the engine in emergency and non-emergency service that are recorded through the non-resettable hour meter.  The owner or operator must record the time of operation of the engine and the reason the engine was in operation during that time.  [40 CFR 60.4214(b)]

- Specific Condition G.25 (formerly G.17 of Permit No. 0850001-040-AV) has been deleted, revised and added as Specific Condition G.21 to reflect current Title V air operation permit format standards.

- Specific Conditions G.22 and G.26 (formerly G.14 and G.18, respectively, of Permit No. 0850001-040-AV) have been deleted because the NESHAP Subpart ZZZZ requirements do not apply to engines that are subject to NSPS Subpart IIII.

- To reflect current Title V air operation permit format standards, NSPS 40 CFR 60, Subpart A Requirements and Specific Condition G.23 (formerly G.15 of Permit No. 0850001-040-AV) have been deleted and replaced by General Provisions and Specific Condition G.27.

Changes to Section III., Subsection H.

- To reflect current Title V air operation permit format standards, the permitting note under the EU description has been revised as follows:

{Permitting Note:  These SI RICE are regulated under:  40 CFR 63, Subpart A, General Provisions, and 40 CFR 63, Subpart ZZZZ, NESHAP for Stationary RICE adopted by reference in Rule 62.-204.800(11)(d)1. and (11)(b)82., F.A.C., respectively.  These RICE are exempted from regulations under 40 CFR 60, Subpart JJJJ – New Source Performance for Stationary Internal Combustion Engines (ICE) Standards of Performance for Stationary Spark Ignition (SI) ICE based on the manufacturer date.  These are “existing” stationary SI RICE less than or equal to 500 bhp, with a displacement of less than 10 liters per cylinder that are located at a major source of HAP and that have not been modified or reconstructed after 6/12/2006.}

- On May 1, 2015, the EPA vacated 40 CFR 63.6640(f)(2)(ii)-(iii).  To reflect the vacation of these paragraphs, Specific Condition H.1 has been revised as follows:

- Hours of Operation.

  - Emergency Situations.  There is no time limit on the use of emergency stationary RICE in emergency situations.  [40 CFR 63.6640(f)(1)]

  - Other Situations.  You may operate your emergency stationary RICE for any combination of the purposes specified in paragraphs H.1.b.(1) through (3) for a maximum of 100 hours per calendar year.  Any operation for non-emergency situations as allowed by paragraphs H.1.c. of this section counts as part of the 100 hours per calendar year allowed by this paragraph H.1.b.

- Maintenance and Testing.  Each RICE is authorized to operate for a maximum of 100 hours per calendar year for the purpose of maintenance checks and readiness testing, provided that the tests are recommended by federal, state or local government, the manufacturer, the vendor, or the insurance company associated with the engine.  Maintenance checks and readiness testing of such units is limited to 100 hours per year.  The owner or operator may petition the Administrator for approval of additional hours to be used for maintenance checks and readiness testing, but a petition is not required if the owner or operator maintains records indicating that Federal, State, or local standards require maintenance and testing of emergency RICE beyond 100 hours per year.  [40 CFR 63.6640(f)(2)(i)]

- Emergency Demand Response.  Each RICE may be operated for emergency demand response for periods in which the Reliability Coordinator under the North American Electric Reliability Corporation (NERC) Reliability Standard EOP-002-3, Capacity and Energy Emergencies (incorporated by reference, see 40 CFR 63.14), or other authorized entity as determined by the Reliability Coordinator, has declared an Energy Emergency Alert Level 2 as defined in the NERC Reliability Standard EOP-002-3.  [40 CFR 63.6640(f)(2)(ii)]

- Voltage or Frequency Deviations.  Emergency stationary RICE may be operated for periods where there is a deviation of voltage or frequency of 5 percent or greater below standard voltage or frequency.  [40 CFR 63.6640(f)(2)(iii)]

  - Non-emergency Situations.  These RICE may be operated for up to 50 hours per calendar year in non-emergency situations.  The 50 hours of operation in non-emergency situations are counted as part of the 100 hours per calendar year for maintenance and testing and emergency demand response provided in paragraph b., above.  The 50 hours per year for non-emergency situations cannot be used for peak shaving or non-emergency demand response, or to generate income for a facility to supply power to an electric grid or otherwise supply power as part of a financial arrangement with another entity.

[40 CFR 63.6640(f)(3)]

- To reflect current Title V air operation permits, Specific Conditions H.8 and H.10 were added to this subsection.

- 40 CFR 63.6645(a) was added to the citation under Specific Condition H.11 (formerly H.9 of Permit No. 0850001-040-AV).  The hyperlinks in this specific condition have been revised as follows:

- 40 CFR 63 Subpart A – General Provisions.  The owner or operator shall comply with the following applicable requirements of 40 CFR 63 Subpart A – General Provisions, which have been adopted by reference in Rule 62-204.800(11)(d)1., F.A.C., except that the Secretary is not the Administrator for purposes of 40 CFR 63.5(e), 40 CFR 63.5(f), 40 CFR 63.6(g), 40 CFR 63.6(h)(9), 40 CFR 63.6(j), 40 CFR 63.13, and 40 CFR 63.14.  Link to 40 CFR 63, Subpart A – General Provisions and Link to Subpart ZZZZ.

Changes to Section III., Subsection I.

- The EU description has been updated to reflect current Title V air operation permit format standards and the future addition of the facility data center and emergency engine.  The revisions appear as follows:

| EU No. | Brief Description |
| --- | --- |
| 024 | Spark Ignition SI Engine-driven Emergency Generator |
| 027 | Data Center Emergency SI RICE |

Emissions Unit EU No. 024 is an emergency generator/engine set, spark ignition (SI) four-stroke reciprocating internal combustion engine (RICE) that fires natural gas with a maximum engine power of 48 HP at 100% load (approximately 30 kW).  The engine has never been reconstructed or modified.

EU No. 027 is an SI emergency engine-electrical generator that fires propane with a maximum engine horsepower of 71 HP at its rated kW (45 kW).  This engine-generator set supplies emergency power to a phone room/data center that will be added to the facility.

The following table provides important details for the engines collectively regulated as EU Nos. 024 and 027:

| Engine Identification | Engine Brake HP | Date of Construction | Model Year | Displacement liters/cylinder (l/c) | Engine Manufacturer | Model No. |
| --- | --- | --- | --- | --- | --- | --- |
| Emergency SI Generator EU No. 024 | 48 (30 kW) | 2013 | 2013 | 0.5 | Generac | QT030 |
| EU No. 027 | 82 (61 kW) | 2018 | 2017 | 0.675 | Generac | SG045 |

{Permitting Note:  These SI ICE are regulated under:  40 CFR 60, Subpart A, General Provisions, and 40 CFR 60, Subpart JJJJ, Standards of Performance for Stationary SI ICE, adopted by reference in Rule 62-204.800(8)(d) and (8)(b)83., F.A.C., respectively.  This These spark ignition four-stroke internal combustion engine (SI ICE) is are regulated under:  40 CFR Part 60, Subpart A, General Provisions, and , 40 CFR 60, Subpart JJJJ, - Standards of Performance for Stationary Spark Ignition Internal Combustion Engines adopted by reference in Rule 62.204.800(8)(d) and (8)(b)83., F.A.C., respectively.  Pursuant to Subpart JJJJ, this is “new” emergency stationary engines, with an engine power greater than 19 kW (25 HP) and less than 75 kW (100 HP), with a displacement of less than 10 liters per cylinder, and that are located at a major source of HAPs.  Construction commenced (ordered) on these engines after January 1, 2009.  Pursuant to Subpart ZZZZ, these are two “new” four-stroke emergency stationary SI RICE engines with a site rating of less than 250 brake HP located at a major source of HAP that commenced construction after December 19, 2002.  In accordance with 40 CFR 63.6590(c) (3), these engines meet the requirements of Subpart ZZZZ by meeting the requirements of 40 CFR 60 Subpart JJJJ.}

{Permitting Note:  EU No. 027 will be constructed along with the data center that it services near the end of the 2018 calendar year.}

- EU Nos. 024 and 027 are SI ICE that fire different fuels.  To reflect this, Specific Condition I.1 has been revised as follows:

- Authorized Fuel.

- EU No. 024.  These Stationary Spark Ignition Internal Combustion Engines (SI-ICE) are EU No. 024 is fueled by Natural Gas.  This engine may be fired using propane for a maximum of 100 hours per year as an alternative fuel solely during emergency operations, but must keep records of such use.  If propane is used for more than 100 hours per year in an engine that is not certified to the emission standards when using propane, you are required to conduct a performance test to demonstrate compliance with the emission standards of Specific Conditions I.3 and I.4.  [40 CFR 60.4243(e) and Application No. 0850001-33-AV]

- EU No. 027.  EU No. 027 is fueled by propane.  [Application No. 0850001-042-AV]

- On May 1, 2015, the EPA vacated 40 CFR 60.4243(d)(2)(ii)-(iii).  To reflect the vacation of these paragraphs, Specific Condition I.2 has been revised as follows:

- Restricted Hours of Operation.  You must operate these emergency engines according to the requirements in paragraphs a. through d.  In order for these engines to be considered emergency stationary ICE under Subpart JJJJ, any operation other than emergency operation, maintenance and testing, emergency demand response, and operation in non-emergency situations for 50 hours per year, as described in the paragraphs below, is prohibited.  If you do not operate these engines according to the requirements in paragraphs a. through d. below, these engines will not be considered emergency engines and must meet all requirements for non-emergency engines pursuant to 40 CFR 60, Subpart JJJJ.  [40 CFR 60.4243(d)]

- Emergency Situations.  There is no time limit on the use of these engines in emergency situations.  [40 CFR 60.4243(d)(1)]

- Non-Emergency Situations.  You may operate these engines for any combination of the purposes specified in paragraphs (1) through (3) for a maximum of 100 hours per calendar year.  Any operation for non-emergency situations as allowed by paragraphs c. and d. below counts as part of the 100 hours per calendar year allowed.  [40 CFR 60.4243(d)(2)]

- Maintenance and Testing.  Each engine is authorized to operate for a maximum of 100 hours per calendar year for the purpose of maintenance checks and readiness testing, provided that the tests are recommended by federal, state or local government, the manufacturer, the vendor, regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine.  The owner or operator may petition the Administrator for approval of additional hours to be used for maintenance checks and readiness testing, but a petition is not required if the owner or operator maintains records indicating that Federal, State, or local standards require maintenance and testing of emergency ICE beyond 100 hours per year.  [40 CFR 60.4243(d)(2)(i)]

- Emergency Demand Response.  Each engine may be operated for emergency demand response for periods in which the Reliability Coordinator under the North American Electric Reliability Corporation (NERC) Reliability Standard EOP-002-3, Capacity and Energy Emergencies (incorporated by reference, see 40 CFR 60.17), or other authorized entity as determined by the Reliability Coordinator, has declared an Energy Emergency Alert Level 2 as defined in the NERC Reliability Standard EOP-002-3.  [40 CFR 60.4243(d)(2)(ii)]

- Voltage or Frequency Deviations.  Each engine may be operated for periods where there is a deviation of voltage or frequency of 5 percent or greater below standard voltage or frequency.  [40 CFR 63. 60.4243(d)(2)(iii)]

- Other Non-emergency Situations.  These engines may be operated for up to 50 hours per calendar year in nonemergency situations.  The 50 hours of operation in non-emergency situations are counted as part of the 100 hours per calendar year for maintenance and testing and emergency demand response provided in paragraph b above.  Except as provided in paragraph d. below, the 50 hours per year for non-emergency situations cannot be used for peak shaving or non-emergency demand response, or to generate income for a facility to supply power to an electric grid or otherwise supply power as part of a financial arrangement with another entity.  [40 CFR 60.4243(d)(3)]

- Limited Non-emergency 50 hours Operation.  The 50 hours per year for non-emergency situations can be used to supply power as part of a financial arrangement with another entity if all of the following conditions are met:

(1)	The engine is dispatched by the local balancing authority or local transmission and distribution system operator.

(2)	The dispatch is intended to mitigate local transmission and/or distribution limitations so as to avert potential voltage collapse or line overloads that could lead to the interruption of power supply in a local area or region.

(3)	The dispatch follows reliability, emergency operation or similar protocols that follow specific NERC, regional, state, public utility commission or local standards or guidelines.

(4)	The power is provided only to the facility itself or to support the local transmission and distribution system.

(5)	The owner or operator identifies and records the entity that dispatches the engine and the specific NERC, regional, state, public utility commission or local standards or guidelines that are being followed for dispatching the engine.  The local balancing authority or local transmission and distribution system operator may keep these records on behalf of the engine owner or operator.

[40 CFR 60.4243(d)(3)(i)]

Section IV. Changes

- The Acid Rain section has been updated with the application submitted with this renewal.

Section V. Changes

- Section V. has been deleted to reflect Title V air operation permit format standards.  The appendices are a separate attachment as stated in the Table of Contents.

Changes to Attached Appendices

- All NSPS and NESHAP appendices have been updated to their current versions and formats.

- Table H has been updated with information about this permit and concurrent Permit No. 0850001-041-AC/PSD-FL-146J and 327G.

Conclusion

This project renews Title V air operation permit No. 0850001-033-AV, which was effective on December 10, 2013.  This Title V air operation permit renewal is issued under the provisions of Chapter 403, Florida Statues (F.S.), and Chapters 62-4, 62-210, and 62-213, F.A.C.