# Orlando Utilities Commission

# Stanton Energy Center

# Facility ID No. 0950137

# Orange County

# Title V Air Operation Permit Renewal

Permit No. 0950137-047-AV

# Permitting Authority:

State of Florida

Department of Environmental Protection

Division of Air Resource Management

Office of Permitting and Compliance

2600 Blair Stone Road

Mail Station #5505

Tallahassee, Florida  32399-2400

# Telephone:  (850) 717-9000

Fax:  (850) 717-9097

# Compliance Authority:

Central District Office

3319 Maguire Boulevard, Suite 232

Orlando, FL 32803-3767

Telephone:  (407) 897-4100

Fax:  (407) 412-0455

Title V Air Operation Permit Renewal

Permit No. 0950137-047-AV

Table of Contents

Section	Page Number

- Facility Information.

- Facility Description. 	 2

- Summary of Emissions Units. 	 3

- Applicable Regulations. 	 4

- Facility-wide Conditions. 	 6

- Emissions Units and Conditions.

- EUs 001 and 002, Coal Fired Steam Generators. 	 9

- [Reserved]	 18

- EUs 004-016 and 029, Fly Ash Silos. 	 19

- EUs 025 and 026, Stanton Unit A - Combined-Cycle Combustion Turbines. 	 22

- [Reserved]	31

- EU 037, Stanton Unit B - Combined Cycle Combustion Turbine (300 MW). 	 32

- EU 038, Stanton Unit B - Cooling Tower. 	 43

- [Reserved]	44

- EU 024, 3,740 BHP Emergency Generator. 	45

- EU 041, 563 kW Emergency Generator at the Stanton A Plant Site. 	48

- EU 044, Emergency Fire Pump Engines. 	51

- EU 021, Surface Coating and Solvent Cleaning. 	54

- Acid Rain Part. 	 55

Phase II Acid Rain Application/Compliance Plan.

Phase II Acid Rain NOX Compliance Plan.

- Clean Air Interstate Rule Part. 	 68

- Transport Rule Part. 	 79

- Appendices. 	 See Appendix Document

Appendix A, Glossary.

Appendix CAM, Compliance Assurance Monitoring Plan.

Appendix CEMS, Continuous Emissions Monitoring Requirements.

Appendix CP, Compliance Plan.

Appendix I, List of Insignificant Emissions Units and/or Activities.

Appendix NESHAP, Subpart A – General Provisions.

Appendix NESHAP, Subpart ZZZZ.

Appendix NESHAP Subpart UUUUU, National Emission Standards for Hazardous Air Pollutants:  Coal- and Oil-Fired Electric Utility Steam Generating Units.

Appendix NSPS, Subpart A – General Provisions.

Appendix NSPS, Subpart Da.

Appendix NSPS, Subpart GG.

Appendix NSPS, Subpart IIII.

Appendix NSPS Subpart Kb.

Appendix NSPS Subpart KKKK.

Appendix NSPS, Subpart Y.

Appendix RR, Facility-wide Reporting Requirements.

Appendix TR, Facility-wide Testing Requirements.

Appendix TV, Title V General Conditions.

Appendix U, List of Unregulated Emissions Units and/or Activities.

Referenced Attachments. 	 At End

Figure 1, Summary Report-Gaseous and Opacity Excess Emission and

Monitoring System Performance (40 CFR 60, July, 1996).

Table H, Permit History.

Table 1, Summary of Air Pollutant Standards.

Table 2, Compliance Requirements.

| Permittee: Orlando Utilities Commission P.O. Box 3193 Orlando, Florida 32802-3193 | Permit No. 0950137-047-AV Curtis H. Stanton Energy Center Facility ID No. 0950137 Title V Air Operation Permit Renewal |
| --- | --- |

The purpose of this permit is to revise the Title V air operation permit for the above referenced facility.  The existing Curtis H. Stanton Energy Center (the Stanton Plant) is located in Orange County at 5100 South Alafaya Trail, Orlando.  The UTM Coordinates are:  Zone 17, 483.6 km East and 3151.1 km North.  Latitude is:  28° 29’ 17” North; and, Longitude is:  81° 10’ 03” West.

The Title V air operation permit is issued under the provisions of Chapter 403, Florida Statutes (F.S.), and Florida Administrative Code (F.A.C.) Chapters 62-4, 62-210, 62-213 and 62-214.  The above named permittee is hereby authorized to operate the facility in accordance with the terms and conditions of this permit.

Executed in Tallahassee, Florida.

0950137-044-AV Effective Date:  January 1, 2015

0950137-047-AV Effective Date:  Day 55

Renewal Application Due Date:  May 20, 2019

Expiration Date:  December 31, 2019

(Draft)

For:

Syed Arif, P.E., Program Administrator

Office of Permitting and Compliance

Division of Air Resource Management

SA/dlr/pks

Subsection A.  Facility Description.

Orlando Utilities Commission (OUC) operates the Curtis H. Stanton Energy Center, which is an existing power plant (SIC No. 4911).  The facility site is located 144 km southeast from the Chassahowitzka National Wildlife Area; the nearest Federal Prevention of Significant Deterioration (PSD) Class I Area.  The placard page above indicates the exact geographical coordinates.

This facility consists of two fossil fuel fired steam electric generating stations, emissions unit (E.U.) identification (ID) No. 001 (Unit No. 1) and 002 (Unit No. 2); also, there are storage and handling facilities for solid fuels, fly ash, limestone, gypsum, slag, and bottom ash.  Unit No. 1 consists of a Babcock and Wilcox boiler/steam generator (Model RB 611) and steam turbine, which drives a generator with a nameplate rating of 468 megawatts (MW).  Unit No. 2 consists of a Babcock and Wilcox boiler/steam generator (Model RB 621) and steam turbine, which drives a generator with a nameplate rating of 468 MW.  Each boiler/steam generator is a wall fired dry bottom unit.  Unit Nos. 1 and 2 are fired with coal.  Each unit has their individual stacks.  Particulate matter emissions generated during the operation of the unit are controlled by a dry electrostatic precipitator (ESP) manufactured by Wheelabrator-Frye Inc.  The control efficiency of the ESP is 99.7%.  Units 1 and 2 are each equipped with low NOX burners and overfire air equipment.  The burner design provides accurate fuel-air ratio control and thorough mixing of fuel and air at all ratings.  Unit 2 is also equipped with a selective catalytic reduction (SCR) system for further control of NOX emissions.

Emission Units 001 and 002 are subject to compliance assurance monitoring (CAM) for particulate matter (PM) emissions controlled by an ESP.  Because the continuous opacity monitoring system (COMS) is required to be used at the facility (for Phase II Acid Rain Program purposes), it must also be used as part of the CAM plan.  A CAM plan is included for the ESP.  See Appendix CAM.

Emission Units 025 and 026 (Stanton Unit A) are nominal 170 MW, General Electric “F” Class (PG7241FA) combustion turbine-electrical generators, fired with pipeline natural gas or diesel and equipped with evaporative coolers on the inlet air system, two supplementary fired heat recovery steam generators (HRSG), each with a 160 ft. stack, and one steam turbine-electrical generator rated at approximately 300 MW.  Units 25 and 26 have a total nominal capacity of 640 MW and will achieve approximately 700 MW during extreme winter peaking conditions.

The combustion turbines are equipped with dry low nitrogen oxides (NOX) combustors as well as selective catalytic reduction (SCR) in order to control NOX emissions to 3.5 parts per million by volume dry (ppmvd) at 15% oxygen (O2) while firing natural gas.  During fuel oil firing, emissions shall be held to 10 ppmvd at 15% O2 using SCR plus water injection.  Pipeline quality natural gas, 0.05% sulfur, by weight, fuel oil, and good combustion practices shall be employed to control all pollutants.

These emissions units (the combustion turbines) are not subject to continuous assurance monitoring (CAM) because the NOX continuous emissions monitoring system (CEMS) is used for continuance compliance determination.  Thus no CAM plan is included for these units in this permit.

Emission Unit 037 (Stanton Unit B) consists of:  one nominal 150 megawatts (MW) General Electric 7241 FA combustion turbine-electrical generator (CTG); a supplementary fired heat recovery steam generator (HRSG) with natural gas fueled duct burners; a nominal 150 MW steam turbine generator (STG); and auxiliary equipment.  The unit includes highly automated controls, described as the GE Mark VI Gas Turbine Control System to fulfill all of the gas turbine control requirements.

Unit B is equipped with dry low nitrogen oxides (NOX) combustors as well as selective catalytic reduction (SCR) in order to control NOX emissions to 2 parts per million by volume dry (ppmvd) at 15% oxygen (O2) while firing natural gas.  During fuel oil firing, emissions shall be held to 8 ppmvd at 15% O2 using SCR plus water injection.  Pipeline quality natural gas, 0.0015% sulfur, by weight, fuel oil, and good combustion practices shall be employed to control all pollutants.

Unit B is not subject to continuous assurance monitoring (CAM) because the NOX continuous emissions monitoring system (CEMS) is used for continuance compliance determination.  Thus no CAM plan is included for this unit in this permit.

Also included in this permit are miscellaneous unregulated emissions units and insignificant emissions units and/or activities.

Subsection B.  Summary of Emissions Units.

| EU No. | ## Brief Description |
| --- | --- |
| Regulated Emissions Units |  |
| 001 | Fossil Fuel Fired Steam Electric Generator No. 1 |
| 002 | Fossil Fuel Fired Steam Electric Generator No. 2 |
| 004 | Coal Transfer Baghouse |
| 005 | Coal Crusher Building Baghouse |
| 006 | Coal Plant Transfer and Silo Fill Area #1 Baghouse |
| 007 | Coal Plant Transfer and Silo Fill Area #2 Baghouse |
| 008 | Limestone Day Bin Baghouse |
| 009 | Pebble Lime Receiving Hopper Baghouse |
| 010 | Coal Reclaim Hopper Baghouse |
| 011 | Flyash Exhauster Filter #1 Baghouse |
| 012 | Flyash Exhauster Filter #2 Baghouse |
| 013 | Flyash Exhauster Filter #3 Baghouse |
| 014 | Flyash Exhauster Filter #4 Baghouse |
| 015 | Flyash Silo Bin Vent Filter Baghouse |
| 016 | Adipic Acid Storage Baghouse |
| 021 | Surface Coating and Solvent Cleaning |
| 024 | 3,740 BHP Emergency Generator |
| 025 | Stanton Unit A- Combined-Cycle Combustion Turbine |
| 026 | Stanton Unit A- Combined-Cycle Combustion Turbine |
| 029 | Flyash Silo Bin Vent Filter Baghouse |
| 037 | Stanton Unit B - 300 MW Combined Cycle Combustion Turbine |
| 038 | Stanton Unit B - Cooling Tower |
| 041 | 563 kW Emergency Generator at the Stanton A Plant Site |
| 044 | Emergency Fire Pump Engines |
| Unregulated Emissions Units and Activities (see Appendix U, List of Unregulated Emissions Units and/or Activities) |  |
| 017 | Material Handling |
| 019 | Water Treatment |
| 020 | Unconfined Emissions |
| 022 | General Purpose Engines |
| 023 | Helper Cooling Towers |
| 027 | Mechanical Draft Cooling Tower |
| 036 | Inline Insertable Dust Collector |
| 040 | Natural Draft Cooling Towers |

Subsection C.  Applicable Regulations.

Based on the Title V Air Operation Revision application received on April 21, 2016, this facility is a major source of hazardous air pollutants (HAP).  Unit B is potentially subject to 40 CFR 63, Subpart YYYY - National Emission Standards for Hazardous Air Pollutants for Stationary Combustion Turbines.  The applicability of this rule has been stayed for lean premix and diffusion flame gas-fired combustion turbines.  The existing facility is a PSD major source of air pollutants in accordance with Rule 62-212.400, F.A.C.

A summary of applicable regulations is shown in the following table.

| Regulation | ## EU No(s). |
| --- | --- |
| Federal Rule Citations |  |
| 40 CFR 60, Subpart A, NSPS General Provisions | ## 001, 002, 025, 026 |
| 40 CFR 60, Subpart Da, Standards of Performance for Fossil-Fuel Fired Steam Generators | ## 001, 002 |
| NSPS - 40 CFR 60, Subpart GG, Standards of Performance for Stationary Gas Turbines, adopted and incorporated by reference in Rule 62-204.800 | 025, 026 |
| NSPS - 40 CFR 60, Subpart KKKK, Standards of Performance for Stationary Combustion Turbines that Commence Construction after February 18, 2005, adopted and incorporated by reference in Rule 62-204.800 | 037 |
| 40 CFR 60, Subpart Y, Standards of Performance for Coal Preparation Plants | 004 through 016 and 029 |
| 40 CFR 60, Subpart IIII, Standards of Performance for Stationary Compression Ignition Internal Combustion Engines | 041 |
| Federal Acid Rain Program, Phase II | 001, 002, 025, 026 |
| 40 CFR 75 Acid Rain Monitoring Provisions |  |
| 40 CFR 63, Subpart ZZZZ, National Emission Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines (RICE) | 024, 041, 044 |
| 40 CFR 63, Subpart UUUUU, National Emission Standards for Hazardous Air Pollutants: Coal- and Oil-Fired Electric Utility Steam Generating Units | 001, 002 |
| State Rule Citations |  |
| Rule 62-4, F.A.C. (Permitting Requirements) | 001, 002, 004 through 016, 025, 026,and 029 |
| Rule 62-204, F.A.C. (Ambient Air Quality Requirements, PSD Increments, and Federal Regulations Adopted by Reference) |  |
| Rule 62-210, F.A.C. (Permits Required, Public Notice, Reports, Stack Height Policy, Circumvention, Excess Emissions, and Forms) |  |
| Rule 62-212, F.A.C. (Preconstruction Review, PSD Review and BACT) |  |
| Rule 62-213, F.A.C. (Title V Air Operation Permits for Major Sources of Air Pollution) |  |
| Rule 62-214, F.A.C. (Requirements For Sources Subject To The Federal Acid Rain Program) | 001, 002, 025, 026 |
| Rule 62-296, F.A.C. (Emission Limiting Standards) | 001, 002, 004 through 016, 025, 026,and 029 |
| Rule 62-297, F.A.C. (Test Methods and Procedures, Continuous Monitoring Specifications, and Alternate Sampling Procedures) |  |
| Rule 62-296.511, F.A.C. (Solvent Metal Cleaning) | 021 |
| PSD-FL-084 | 001, 002 |
| PPS PA 81-14/SA2 | 01, 002, 025, 026 |
| PSD-FL-313, 0950137-002-AC | 025, 026 |

The following conditions apply facility-wide to all emission units and activities:

- Appendices.  The permittee shall comply with all documents identified in Section VII, Appendices, listed in the Table of Contents.  Each document is an enforceable part of this permit unless otherwise indicated.  [Rule 62-213.440, F.A.C.]

Emissions and Controls

- Not federally Enforceable.  Objectionable Odor Prohibited.  No person shall cause, suffer, allow or permit the discharge of air pollutants, which cause or contribute to an objectionable odor.  An “objectionable odor” means any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance.  [Rule 62-296.320(2) and 62-210.200(Definitions), F.A.C.]

- General Volatile Organic Compounds (VOC) Emissions or Organic Solvents (OS) Emissions.  The permittee shall allow no person to store, pump, handle, process, load, unload or use in any process or installation, volatile organic compounds or organic solvents without applying known and existing vapor emission control devices or systems deemed necessary and ordered by the Department.  [Rule 62-296.320(1), F.A.C.]

{Permitting Note:  Nothing is deemed necessary and ordered at this time.}

- General Visible Emissions.  No person shall cause, let, permit, suffer or allow to be discharged into the atmosphere the emissions of air pollutants from any activity equal to or greater than 20% opacity.  EPA Method 9 is the method of compliance pursuant to Chapter 62-297, F.A.C.  This regulation does not impose a specific testing requirement.  [Rule 62-296.320(4)(b), F.A.C.]

- Unconfined Particulate Matter.  No person shall cause, let, permit, suffer or allow the emissions of unconfined particulate matter from any activity, including vehicular movement; transportation of materials; construction; alteration; demolition or wrecking; or industrially related activities such as loading, unloading, storing or handling; without taking reasonable precautions to prevent such emissions.  Reasonable precautions to prevent emissions of unconfined particulate matter at this facility include:

- Paving and maintenance of roads, parking areas, and yards.

- Chemical (dust suppressants) or water application to unpaved roads, and unpaved yard areas.

- Removal of particulate matter (PM) from roads and other paved areas to prevent re-entrainment, and from buildings or work areas to prevent airborne PM.

- Landscaping or planting of vegetation.

- Confining abrasive blasting where possible.

- Other techniques, as necessary.

[Rule 62-296.320(4)(c), F.A.C.]

Annual Reports and Fees

See Appendix RR, Facility-wide Reporting Requirements for additional details.

- Annual Operating Report.  The permittee shall submit an annual report that summarizes the actual operating rates and emissions from this facility.  Annual operating reports shall be submitted to the Compliance Authority by April 1st of each year.  [Rule 62-210.370(3), F.A.C.]

- Electronic Annual Operating Report and Title V Annual Emissions Fees.  The information required by the Annual Operating Report for Air Pollutant Emitting Facility [Including Title V Source Emissions Fee Calculation] (DEP Form No. 62-210.900(5)) shall be submitted by April 1 of each year, for the previous calendar year, to the Department of Environmental Protection’s Division of Air Resource Management.  Each Title V source shall submit the annual operating report using the DEP’s Electronic Annual Operating Report (EAOR) software, unless the Title V source claims a technical or financial hardship by submitting DEP Form No. 62-210.900(5) to the DEP Division of Air Resource Management instead of using the reporting software. Emissions shall be computed in accordance with the provisions of subsection 62-210.370(2), F.A.C.  Each Title V source must pay between January 15 and April 1 of each year an annual emissions fee in an amount determined as set forth in subsection 62-213.205(1), F.A.C.  The annual fee shall only apply to those regulated pollutants, except carbon monoxide and greenhouse gases, for which an allowable numeric emission-limiting standard is specified in the source’s most recent construction permit or operation permit.  Upon completing the required EAOR entries, the EAOR Title V Fee Invoice can be printed by the source showing which of the reported emissions are subject to the fee and the total Title V Annual Emissions Fee that is due.  The submission of the annual Title V emissions fee payment is also due (postmarked) by April 1st of each year.  A copy of the system-generated EAOR Title V Annual Emissions Fee Invoice and the indicated total fee shall be submitted to:  Major Air Pollution Source Annual Emissions Fee, P.O. Box 3070, Tallahassee, Florida  32315-3070.  Additional information is available by accessing the Title V Annual Emissions Fee On-line Information Center at the following Internet web site:  http://www.dep.state.fl.us/air/emission/tvfee.htm.  [Rules 62-210.370(3), 62-210.900 & 62-213.205, F.A.C.; and, §403.0872(11), Florida Statutes (2013)]

{Permitting Note:  Resources to help you complete your AOR are available on the electronic AOR (EAOR) website at:  http://www.dep.state.fl.us/air/emission/eaor.  If you have questions or need assistance after reviewing the information posted on the EAOR website, please contact the Department by phone at (850) 717-9000 or email at eaor@dep.state.fl.us.}

{Permitting Note:  The Title V Annual Emissions Fee form (DEP Form No. 62-213.900(1)) has been repealed.  A separate Annual Emissions Fee form is no longer required to be submitted by March 1st each year.}

- Annual Statement of Compliance.  The permittee shall submit an annual statement of compliance to the compliance authority at the address shown on the cover of this permit and to the US. EPA at the address shown below within 60 days after the end of each calendar year during which the Title V air operation permit was effective.  (See also Appendix RR, Conditions RR1 and RR7.)  [Rules 62-213.440(3)(a)2. & 3. and (b), F.A.C.]

U.S. Environmental Protection Agency, Region 4

Atlanta Federal Center

61 Forsyth Street, SW

Atlanta, Georgia  30303

Attn:  Air Enforcement Branch

- Prevention of Accidental Releases (Section 112(r) of CAA).

- As required by Section 112(r)(7)(B)(iii) of the CAA and 40 CFR 68, the owner or operator shall submit an updated Risk Management Plan (RMP) to the Chemical Emergency Preparedness and Prevention Office (CEPPO) RMP Reporting Center.  (See paragraph e., below.)

- As required under Section 252.941(1)(c), F.S., the owner or operator shall report to the appropriate representative of the Division of Emergency Management, as established by department rule, within one working day of discovery of an accidental release of a regulated substance from the stationary source, if the owner or operator is required to report the release to the United States Environmental Protection Agency under Section 112(r)(6) of the CAA.

- The owner or operator shall submit the required annual registration fee to the Division of Emergency Management on or before April 1, in accordance with Part IV, Chapter 252, F.S., and Rule 27P-21, F.A.C.

- Any required written reports, notifications, certifications, and data required to be sent to the Division of Emergency Management, should be sent to:  Division of Emergency Management, 2555 Shumard Oak Boulevard, Tallahassee, FL  32399-2100, Telephone:  (850) 413-9970, Fax:  (850) 488-1739.

- Any Risk Management Plans, original submittals, revisions, or updates to submittals, should be sent electronically through EPA’s Central Data Exchange system at the following address:  https://cdx.epa.gov.  Information on electronically submitting risk management plans using the Central Data Exchange system is available at:  http://www2.epa.gov/rmp.  The RMP Reporting Center can be contacted at:  RMP Reporting Center, Post Office Box 10162, Fairfax, VA  22038, Telephone:  (703) 227-7650.

- Any required reports to be sent to the National Response Center, should be sent to:  U.S. Environmental Protection Agency, Office of Solid Waste and Emergency Response, 1200 Pennsylvania Ave. NW, Mail Code:  US EPA (5101T), Washington, DC  20460, Telephone:  (800) 424-8802.

- Send the required annual registration fee using approved forms made payable to:  Cashier, Division of Emergency Management, State Emergency Response Commission, 2555 Shumard Oak Boulevard, Tallahassee, FL  32399-2149

[Part IV, Chapter 252, F.S.; and, Rule 27P-21, F.A.C.]

The specific conditions in this section apply to the following emissions unit(s):

| EU No. | Brief Description |
| --- | --- |
| 001 | Fossil Fuel Fired Steam Generator No. 1 |
| 002 | Fossil Fuel Fired Steam Generator No. 2 |

Fossil fuel fired steam generator #1 is a nominal 468 megawatt steam generator designated as Unit #1.  The emission unit is fired primarily on bituminous coal with a maximum heat input of 4,800 MMBtu per hour.  Stack height is 550 feet, stack exit diameter is 19.0 feet, flow rate is 1,420,000 actual cubic feet per minute (acfm) at 127 degrees Fahrenheit, stack exit velocity is 83.5 feet per second.

Fossil fuel fired steam generator #2 is a nominal 468 megawatt steam generator designated as Unit #2.  The emission unit is fired primarily on bituminous coal with a maximum heat input of 4,800 MMBtu per hour. Stack height is 550 feet, stack exit diameter is 19.0 feet, flow rate is 1,310,120 acfm at 124 degrees Fahrenheit, stack exit velocity is 77.0 feet per second.

The original Permit No. PSD-FL-084 authorized the construction of Units 1 and 2 and the use of fuel oil as a secondary fuel to coal.  Although not restricted in the original permit, the oil was used to ignite the coal.  Permit No.  0950137-039-AC authorized the replacement of the fuel oil igniter systems with natural gas igniter systems.   Fuel oil is no longer allowed as an authorized fuel in these units.

Each boiler/steam generator, Units 1 and 2, drives a turbine generator and both units have an individual 550 foot exhaust stack.  Particulate matter emissions generated during the operation of the unit are controlled by a dry electrostatic precipitator (ESP) manufactured by Wheelabrator-Frye Inc.  The control efficiency of the ESP is 99.7%.  Sulfur dioxide emissions are controlled by wet scrubber flue gas desulfurization (WFGD) equipment manufactured by Combustion Engineering.

Units 1 and 2 are each equipped with low NOX burners and overfire air equipment.  The burner design provides accurate fuel-air ratio control and thorough mixing of fuel and air at all ratings.  Both an air and coal flow monitoring system are provided at each burner.  Unit 2 is also equipped with a selective catalytic reduction (SCR) system for further control of NOX emissions.

The WFGD systems for Units 1 and 2 include a dibasic acid (DBA) delivery system, and a neural network-based combustion optimization system that interfaces with the existing plant distributed control system for the purpose of optimizing boiler operations.  The DBA system includes three metering pumps, one DBA storage tank, associated piping, valves, components, instrumentation and controls.

Permit No. 0950137-014-AC authorized the addition of forced oxidation to Units 1 and 2 FGD systems.

Project No. 0950137-034-AC modified the Unit 1 Flue Gas Desulfurization (FGD) system with an upgrade to the mist eliminator vanes and fixed grid wash system.  This upgrade was only to the mist eliminator part of the FGD system.

Permit No. 0950137-039-AC authorized the replacement of the fuel oil igniter systems with natural gas igniter systems.

Permit No.  0950137-040-AC authorized the construction/installation, operation and maintenance of a new distribution tray or wall rings on the Unit 1 WFGD scrubber and the modification of the spray headers and nozzles and their arrangement.  The permit also authorized the construction/installation, operation and maintenance of a dry sorbent injection (DSI) systems for the facility’s Unit Nos. 1 and 2 boilers. The permit also authorized the installation and operation of an SCR system on Unit 1, which has not yet been undertaken. If deemed appropriate, OUC will request an extension to the permit or re-apply for a new air construction permit that would allow for SCR installation and operation on Unit 1 in the future.

Permit No. 0950137-041-AC authorized to replacement of the high pressure and intermediate pressure portions of the Unit 2 steam turbine with improved technology.  It was expected that this turbine blade replacement effort would increase the efficiency, providing an increase in power generation output capability without a corresponding increase in fuel consumption or annual generation potential.

Each boiler/steam generator (i.e., Units 1 and 2) are regulated under the federal Acid Rain Program, Phase II, adopted and incorporated by reference in Rule 62-204.800, F.A.C.  These units hold ORIS code 0564.

Emission Units 1 and 2 are subject to compliance assurance monitoring (CAM) for particulate matter (PM) emissions controlled by an ESP.  Because the continuous opacity monitoring system (COMS) is required to be used at the facility (for Phase II Acid Rain Program purposes), it must also be used as part of the CAM plan.  A CAM plan is included for the ESP.  See Appendix CAM.

{Permitting Note(s): The emissions units are regulated under Acid Rain, Phase II; NSPS-40 CFR 60, Subpart Da, Standards of Performance for Fossil-Fuel Fired Steam Generators for Which Construction is Commenced After

September 18, 1978, adopted and incorporated by reference in Rule 62-204.800(7)(b)2, F.A.C.; Rule 62-212.400, F.A.C., Prevention of Significant Deterioration (PSD); and Rule 62-212.400(6), F.A.C., Best Available Control Technology (BACT), and Compliance Assurance Monitoring (CAM).  Fossil fuel fired steam generator # 1 began commercial operation on May 12, 1987; and fossil fuel fired steam generator # 2 began commercial operation on June 1, 1996.}

Orlando Utilities Commission plans to comply with the Utility Mercury and Air Toxics Standards (MATS) under the NESHAP, Subpart UUUUU when the requirements become applicable on April 15, 2015 (see Specific Condition A.36. of this subsection).

Essential Potential to Emit (PTE) Parameters

- Permitted Capacity.  As determined by the Acid Rain CEMS, the maximum allowable heat input rate for each unit, based on a 4-hour block average, is as follows:

| Unit Nos. | MMBtu/hr Heat Input | Fuel Type |
| --- | --- | --- |
| 001 | 4,800 | Coal, landfill gas from the Orange County Landfill and natural gas as supplied by commercial pipeline. |
| 002 | 4,800 |  |

[Rules 62-4.160(2), 62-204.800 and 62-210.200(PTE), F.A.C.; PSD-FL-084; Department Order Modifying Conditions of Power Plant Certification dated December 24, 1997; and permit No. 0950137-032-AC, Specific Condition 1.]

- Emissions Unit Operating Rate Limitation After Testing.  See the related testing provisions in Appendix TR, Facility-wide Testing Requirements.  [Rule 62-297.310(2), F.A.C.]

- Methods of Operation.

a.	Fuels.  The fuels that are allowed to be burned in this unit/these units are:

(1)	Coal, primary fuel,

(2)	Natural gas, and

(3)	Landfill gas from the Orange County Landfill.

b.	Flue Gas Desulfurization System (FGD).  No fraction of flue gas shall be allowed to bypass the FGD system to reheat the gases exiting from the FGD system, if the bypass will cause overall SO2 removal efficiency less than 90 percent (or 70 percent for mass SO2 emission rates less than or equal to 0.6 lb/million Btu 30 day rolling average).  The percentage and amount of flue gas bypassing the FGD system shall be documented and records kept for a minimum of two years available for Department’s inspection.    The flue-gas desulfurization system and mist eliminators for Unit 2 will be maintained and operated in a manner consistent with good air pollution practice for minimizing emissions pursuant to the requirements of 40 C.F.R. 60.11(d).

[Rules 62-4.070(3) and 62-213.410, F.A.C.; 40 CFR 60.40Da, and PSD-FL-084;]

- Hours of Operation.  These emissions units may operate continuously (8,760 hours/year).  [Rule 62-210.200(PTE), F.A.C.]

Emission Limitations and Standards

{Permitting Note:  The attached Table 1, Summary of Air Pollutant Standards, summarizes information for convenience purposes only.  This table does not supersede any of the terms or conditions of this permit.}

Unless otherwise specified, the averaging times for Specific Conditions A.5. – A.16. are based on the specified averaging time of the applicable test method.

- Particulate Matter (PM).

a.	Unit 1.  PM emissions shall not exceed any of the following:

(1)	0.03 lb/million Btu heat input and 1 percent of the potential combustion concentration (99 percent reduction) when combusting solid fuel.  This standard applies at all times except during periods of startup, shutdown, or malfunction.

b.	Unit 2.  PM emissions shall not exceed any of the following:

(1)	0.02 lb/million Btu heat input and 1 percent of the potential combustion concentration (99 percent reduction) when combusting solid fuel.  This standard applies at all times except during periods of startup, shutdown, or malfunction.

(2)	85.7 lbs/hr.

c.	Unit 2.  Particulate Matter Less Than 10 Microns (PM10) shall not exceed:

(1)	0.02 lb/MMBtu heat input.

(2)	85.7 lb/hr.

[Rules 62-204.800(8)(b)2., F.A.C.; 40 CFR 60.42Da; and PSD-FL-084/PA 81-14/SA1]

- Visible Emissions.  Visible emissions from Units No. 1 and 2 shall not exceed 20 percent opacity (6-minute average), except for one 6-minute period per hour of not more than 27 percent opacity.  [Rule 62-204.800(8), F.A.C.; 40 CFR 60.42Da; and, PSD-FL-084]

- Sulfur Dioxide.  Sulfur dioxide emissions shall not exceed any of the following:

  - Unit No. 1.

(1)	When Combusting solid fuel:

(a)	1.2 lb/million Btu heat input and 10 percent of the potential combustion concentration (90 percent reduction); or,

(b)	30 percent of the potential combustion concentration (70 percent reduction) when emissions are less than 0.60 lb/million Btu heat input.

(c)	1.2 lb/MMBtu heat input, maximum two hour average, and 1.14 lb/MMBtu, heat input maximum three hour average.

b.	Unit No. 2.

(1)	When Combusting solid fuel.

(a)	0.25 lb/million Btu (30-day rolling average) heat input;

(b)	0.67 lb/million Btu (24-hour emission rate) heat input; or

(c)	0.85 lb/million Btu (3-hour emission rate) heat input.

c.	Unit 1 and 2 Averaging Time.  Except as specified in paragraphs a.(1)(c) and b.(1)(b) & (c), above, compliance with the PSD and NSPS sulfur dioxide emission limitations and percent reduction requirements are both determined on a 30-day rolling average basis.

[Rule 62-204.800(8), F.A.C.; 40 CFR 60.43Da; PSD-FL-084/PPS PA 81-14/SA1; and, PA 81-14C & PA81-14SA issued 12/24/97]

- Nitrogen Oxides.  Nitrogen oxide emissions shall not exceed any of the following:

  - Unit 1.

(1)	When combusting bituminous coal:

(a)	0.60 lb./million Btu heat input (30 day rolling average), nor

(b)	0.46 lb./million Btu heat input on an annual average.

b.	Unit 2.

(1)	When combusting bituminous coal, nitrogen oxide emissions shall not exceed 0.17 lb./million Btu heat input (30-day rolling average).

c.	Units 1 and 2.  The above standards apply at all times except during periods of startup, shutdown, or malfunction.

[Rule 62-204.800(8) and 62-214, F.A.C.; and 40 CFR 60.44Da]

- Ammonia Slip.  Ammonia slip from the NOX control system for Unit 2 shall be limited to less than 30 ppmv, uncorrected.  [PSD-FL-084 (EPA Revision Issued 3/2/93]

- Carbon Monoxide (CO).  As demonstrated by the required continuous emissions monitoring system (CO-CEMS), excluding allowable periods of excess emissions related to startup, shutdown and malfunction, emissions of CO shall not exceed:

a.	Unit 1.  0.18 lb/MMBtu heat input on a 30-operating day rolling average.

b.	Unit 2.

(1)	0.15 lb/million Btu heat input on a 30-operating day rolling average.

(2)	643 lb/hr.

[Permit Nos. PSD-FL-084, PA 81-14/SA1, 0950137-015-AC (PSD-FL-395), Specific Condition 9, and 0950137-036-AC (PSD-FL-395A, PSD-FL-373B), Specific Condition A.3.]

- Volatile Organic Compounds.  Volatile Organic Compounds (VOC) emissions from Unit No. 2 shall not exceed:

a.	0.015 lb/million Btu heat input.

b.	64 lb/hr

[PSD-FL-084 and PPS PA 81-14/SA1]

- Sulfuric Acid Mist.  Sulfuric acid mist (H2SO4) emissions from Unit No. 2 shall not exceed:

a.	0.033 lb/million Btu heat input.

b.	140 lb/hr.

[PPS PA 81-14/SA1]

- Beryllium.  Beryllium (Be) emissions from Unit No. 2 shall not exceed:

a.	5.2x10-6 lb./million Btu heat input.

b.	0.022 lb./hr.

[PPS PA 81-14/SA1]

- Mercury.  Mercury (Hg) emissions from Unit No. 2 shall not exceed:

a.	1.1x10-5 lb/million Btu heat input.

b.	0.046 lb/hr .

[PPS PA 81-14/SA1]

- Lead.  Lead (Pb) emissions from Unit No. 2 shall not exceed:

a.	1.5x10-4 lb/million Btu heat input.

b.	0.64 lb/hr.

[PPS PA 81-14/SA1]

- Fluorides.  Fluorides (Fl) emissions from Unit No. 2 shall not exceed:

a.	4.2x10-4 lb/million Btu heat input.

b.	1.8 lb/hr.

[PPS PA 81-14/SA1]

Excess Emissions

Rule 62-210.700 (Excess Emissions), F.A.C., cannot vary any requirement of an NSPS, NESHAP or Acid Rain program provision.

- Excess Emissions Allowed.  Excess emissions resulting from malfunction shall be permitted provided that best operational practices to minimize emissions are adhered to and the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C.]

- Excess Emissions Allowed.  Excess emissions resulting from startup or shutdown shall be permitted provided that best operational practices to minimize emissions are adhered to and the duration of excess emissions shall be minimized.  [Rule 62-210.700(2), F.A.C.]

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C.]

Monitoring of Operations

- CAM Plan.  These emissions units are subject to the Compliance Assurance Monitoring (CAM) requirements contained in the attached Appendix CAM.  Failure to adhere to the monitoring requirements specified does not necessarily indicate an exceedance of a specific emissions limitation; however, it may constitute good reason to require compliance testing pursuant to Rule 62-297.310(7)(b), F.A.C.  [40 CFR 64; Rules 62-204.800 and 62-213.440(1)(b)1.a., F.A.C.]

Continuous Monitoring Requirements

- Opacity Monitor.  The permittee shall calibrate, maintain, and operate a continuous monitoring system, and record the output of the system, for measuring the opacity of emissions discharged to the atmosphere.  Opacity interference exists due to water droplets in the stack from the use of an FGD system, therefore the opacity is monitored upstream of the interference (at the inlet to the FGD system).  This monitoring method has been approved by the Department through permitting actions.  [Rule 62-204.800(8), F.A.C.; 40 CFR 60.49Da; and PSD-FL-084]

- Sulfur Dioxide Monitor.  The permittee shall calibrate, maintain, and operate a continuous monitoring system, and record the output of the system, for measuring sulfur dioxide emissions as follows:

a.	Sulfur dioxide emissions are monitored at both the inlet and outlet of the sulfur dioxide control device.

b.	An "as fired" fuel monitoring system (upstream of coal pulverizers) meeting the requirements of Method 19, Determination of Sulfur Dioxide Removal Efficiency and Particulate Matter, Sulfur Dioxide, and Nitrogen Oxides Emission Rates, may be used to determine potential sulfur dioxide emissions in place of a continuous sulfur dioxide emission monitor at the inlet to the sulfur dioxide control device as required in the preceding Specific Condition A.22.a.

c.	Within 90 days of commencement of operations, the applicant will determine and submit to EPA and FDER the pH level in the scrubber effluent that correlates with 90% removal of the SO2 in the flue gas (or 70% for mass SO2 emission rates less than or equal to 0.6 lb./MMBtu).  Moreover, the applicant is required to operate a continuous pH meter equipped with and upset alarm to ensure that the operator becomes aware when pH value of the scrubber effluent rises above certain limited value.  The value of the scrubber pH may be revised at a later date provided notification to EPA and FDER is made demonstrating that the minimum removal will be achieved on a continuous basis.  Further, if compliance data show that higher FGD performance is necessary to maintain the minimum removal efficiency limit, a different pH value will be determined and maintained.

[PSD-FL-084, Rule 62-204.800(8), F.A.C.; 40 CFR 60.49Da; and 40 CFR 60, Appendix A, Method 19]

- Nitrogen Oxides.  The permittee shall calibrate, maintain, and operate a continuous monitoring system, and record the output of the system, for measuring nitrogen oxide emissions discharged to the atmosphere.  [Rule 62-204.800(8), F.A.C.; 40 CFR 60.49Da]

- Oxygen or Carbon Dioxide.  The permittee shall calibrate, maintain, and operate a continuous monitoring system, and record the output of the system, for measuring the oxygen or carbon dioxide content of the flue gases at each location where sulfur dioxide or nitrogen oxide emissions are monitored. The oxygen monitor shall be used with automatic feedback or manual controls to continuously maintain optimum air/fuel ratio parameters.  [PSD-FL-084, Rule 62-204.800(8), F.A.C.; 40 CFR 60.49Da]

- Continuous Compliance with CO limits.  The permittee shall calibrate, maintain and operate a carbon monoxide (CO) continuous emissions monitor system (CO-CEMS) and record the output of the system for measuring CO emissions discharged to the atmosphere.  Compliance with the 30-operating day rolling average shall be demonstrated using data collected from the required CO-CEMS.  [Rule 62-4.070(3), F.A.C.; 0950137-015-AC, Specific Condition 10.]

- Performance Specifications and Quality Assurance.  The acceptability of the CO-CEMS shall be evaluated by conducting the appropriate performance specification, as follows.

The CO monitor shall be certified pursuant to 40 CFR 60, Appendix B, Performance Specification 4 or 4A.  Quality assurance procedures shall conform to the requirements of 40 CFR 60, Appendix F.  The required RATA tests shall be performed using EPA Method 10 in Appendix A of 40 CFR 60 and shall be based on a continuous sampling train.  The CO monitor span values shall be set appropriately, considering the expected range of emissions and corresponding emission standards.

[Rules 62-4.070(3), 62-210.200(BACT), F.A.C.; 0950137-015-AC, Specific Condition 15.]

- CEMS Data Requirements for CO BACT Standard.

- Data Collection:  The CO-CEMS shall monitor and record emissions during all operations and whenever emissions are being generated, including during episodes of startups, shutdowns, and malfunctions.  All data shall be used, except for invalid measurements taken during monitor system breakdowns, repairs, calibration checks, zero adjustments, and span adjustments.

- Operating Hours and Operating Days:  An hour is the 60-minute period beginning at the top of each hour.  Any hour during which an emissions unit is in operation for more than 15 minutes is an operating hour for that emission unit.  A day is the 24-hour period from midnight to midnight.  Any day with at least one operating hour for an emissions unit is an operating day for that emission unit.

- Valid Hourly Averages:  The CO-CEMS shall be designed and operated to sample, analyze, and record data evenly spaced over the hour at a minimum of one measurement per minute. All valid measurements collected during an hour shall be used to calculate a 1-hour block average that begins at the top of each hour.

(1)	Hours that are not operating hours are not valid hours.

(2)	For each operating hour, the 1-hour block average shall be computed from at least two data points separated by a minimum of 15 minutes.  If less than two such data points are available, there is insufficient data, the 1-hour block average is not valid, and the hour is considered as “monitor unavailable.”

- Rolling 30-day average:  Compliance shall be determined after each operating day by calculating the arithmetic average of all the valid hourly averages from that operating day and the prior 29 operating days.

- Monitor Availability:  The quarterly excess emissions report shall identify monitor availability for each quarter in which the unit operated.  Monitor availability for the CO-CEMS shall be 95% or greater in any calendar quarter in which the unit operated for more than 760 hours.  In the event the applicable availability is not achieved, the permittee shall provide the Department with a report identifying the problems in achieving the required availability and a plan of corrective actions that will be taken to achieve 95% availability.  The permittee shall implement the reported corrective actions within the next calendar quarter.  Failure to take corrective actions or continued failure to achieve the minimum monitor availability shall be violations of this permit.

[Rules 62-4.070(3) and 62-210.200(BACT), F.A.C. ; 0950137-015-AC, Specific Condition 16.]

Test Methods and Procedures

{Permitting Note:  The attached Table 2, Summary of Compliance Requirements, summarizes information for convenience purposes only.  This table does not supersede any of the terms or conditions of this permit.}

- Test Methods.  Required tests shall be performed in accordance with the following reference methods:

| Method | Description of Method and Comments |
| --- | --- |
| 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| 3A | Gas Analysis for the Determination of Emission Rate Correction Factor or Excess Air |
| 5, 5B, modified 5, or 0010 | Method for Determining Particulate Matter Emissions (All PM is assumed to be PM10.) |
| 6, 6A, 6B or 6C | Determination of Sulfur Dioxide Emissions from Stationary Sources |
| 7, 7A, 7C, 7D or 7E | Determination of Nitrogen Oxides Emissions from Stationary Sources |
| 8, 8A or CTM-013 | Determination of Sulfuric Acid Mist Emissions |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |
| 10 | Determination of Carbon Monoxide Emissions from Stationary Sources {Note: The method shall be based on a continuous sampling train.} |
| 12 | Determination of Lead Emissions |
| 13A, 13B | Determination of Fluoride Emissions |
| 17 | Determination of In-Stack Particulate Matter (PM) Emissions |
| 18 | Determination of VOC Emissions |
| 19 | Determination of Sulfur Dioxide Removal Efficiency and Particulate Matter, Sulfur Dioxide, and Nitrogen Oxides Emission Rates (Optional F-factor method may be used to determine flow rate and gas analysis to calculate mass emissions in lieu of Methods 1-4.) |
| 20 | Determination of Nitrogen Oxides, Sulfur Dioxide and Diluent Emissions from Stationary Gas Turbines |
| 25, 25A, 25B | Method for Determining Gaseous Organic Concentrations (Flame Ionization) |
| 29, 101A or 30B | Determination of Hg Emissions |
| 104 | Determination of Be Emissions |
| 108 | Determination of Hg Emissions |

The above methods are described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [62-297.401, F.A.C.; PPS PA 81-14/SA1; PSD-FL-084; and 40 CFR 60.49Da]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- Annual Compliance Tests Required.  During each federal fiscal year (October 1st to September 30th), each EU shall be tested to demonstrate compliance with the emissions standards for particulate matter, NOX , SO2 and visible emissions.  [Rule 62-297.310(7), F.A.C.; and PPS PA 81-14/SA1]

- Compliance Tests Prior To Renewal.  Compliance tests shall be performed for both Unit 1 and Unit 2 for particulate matter, NOX, SO2, visible emissions and carbon monoxide once every 5 years.  Compliance tests shall be performed for Unit 2 for volatile organic compounds, sulfuric acid mist, mercury, beryllium, lead and fluoride once every 5 years.  The tests shall occur prior to obtaining a renewed operating permit to demonstrate compliance with the emission limits in Specific Conditions A.5. – A.16.  [Rules 62-210.300(2)(a) and 62-297.310(7)(a), F.A.C.]

Recordkeeping and Reporting Requirements

- Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for reporting requirements.

- Fuel Sampling Record.  Samples of all coal fired in the boilers shall be taken and analyzed for sulfur content, ash content, and heating value.  Coal sulfur content shall be determined and recorded on a daily basis in accordance with EPA Reference Method 19.  Records of all the analyses shall be kept for public inspection for a minimum of five years.  [Rule 62-213.440, F.A.C. and PSD-FL-084; 0950137-043-AC, Specific Condition 4.]

- CO-CEMS Annual Emissions Requirement.  The owner or operator shall use data from the CO-CEMS when calculating annual emissions for purposes of computing actual emissions, baseline actual emissions, and net emissions increase, as defined at Rule 62-210.200, F.A.C., and for purposes of computing emissions pursuant to the reporting requirements of Rule 62-210.370(3), F.A.C.  In computing the emissions of a pollutant, the owner or operator shall account for the emissions during periods of startup and shutdown of the emissions unit.  [Rules 62-210.200, and 62-210.370(3), F.A.C.; 0950137-015-AC, Specific Condition 17.]

- Excess Emissions Reporting.

- Malfunction Notification:  If emissions in excess of a standard (subject to the specified averaging period) occur due to malfunction, the permittee shall notify the Compliance Authority within (1) working day of:  the nature, extent, and duration of the excess emissions; the cause of the excess emissions; and the actions taken to correct the problem.  The Department may request a written summary report of the incident.

- SIP Quarterly Report:  Within 30 days following the end of each calendar-quarter, the permittee shall submit a report to the Compliance Authority summarizing periods of CO emissions in excess of the BACT permit standard following the NSPS format in 40 CFR 60.7(c), Subpart A.  In addition, the report shall summarize the CO-CEMS system monitor availability for the previous quarter.

- NSPS Reporting:  Within 30 days following the calendar quarter, the permittee shall submit the written reports required by 40 CFR 60 Subpart Da (Standards of Performance for Fossil-Fuel Fired Steam Generators) for the previous semi-annual period to the Compliance Authority.

{Note:  If there are no periods of excess emissions as defined in 40 CFR, Part 60, Subpart Da, a statement to that effect may be submitted with the SIP Quarterly Report to suffice for the NSPS Semi-Annual Report.}

[Rules 62-4.130, 62-204.800, 62-210.700(6) and 62-212.400(BACT), F.A.C., and 40 CFR 60.7; 0950137-015-AC, Specific Condition 19.]

40 CFR 63, Subpart UUUUU - National Emission Standards for Hazardous Air Pollutants: Coal- and Oil-Fired Electric Utility Steam Generating Units

- Subpart UUUUU Requirements.  In addition to the emissions limits shown above, the permittee shall also comply with the following emissions limits no later than April 16, 2015.

  - Filterable Particulate Matter (PM).  Emissions of PM shall not exceed either 0.030 pound/million British thermal unit (lb/MMBtu) or 0.30 pound per megawatt-hour (lb/MWh).  In lieu of the filterable PM emission limit, the permittee may select to meet a total non-Hg HAP metals emission limit of either 5.0 x 10-5 lb/MMBtu or 0.50 pounds per gigawatt-hour (lb/GWH).  Finally, in lieu of ether filterable PM or total non-Hg HAP metals emission limits the permittee my meet the following individual HAP metal emission limits:

    - Antimony (Sb) – 0.80 pounds per terra Btu (lb/TBtu) or 8.0 x 10-3 lb/GWh.

    - Arsenic (As) – 1.1 lb/TBtu or 0.020 lb/GWh.

    - Beryllium (Be) – 0.20 lb/TBtu or 2.0 x 10-3 lb/GWh.

    - Cadmium (Cd) – 0.30 lb/TBtu or 3.0 x 10-3 lb/GWh.

    - Chromium (Cr) – 2.8 lb/TBtu or 0.030 lb/GWh.

    - Cobalt (Co) – 0.80 lb/TBtu or 8.0 x 10-3 lb/GWh.

    - Lead (Pb) – 1.2 lb/TBtu or 0.020 lb/GWh.

    - Manganese (Mn) – 4.0 lb/TBtu or 0.050 lb/GWh.

    - Nickel (Ni) – 3.5 lb/TBtu or 0.040 lb/GWh.

    - Selenium (Se) – 5.0 lb/TBtu or 0.060 lb/GWh.

  - Hydrogen Chloride (HCl).  Emissions of HCl shall not exceed either 2.0 x 10-3 lb/MMBtu or 0.020 lb/MWh.  In lieu of HCl emission limit, the permittee may select to meet a SO2 emission limit of either 0.20 lb/MMBtu or 1.5 lb/GWH.

  - Mercury (Hg).  Emissions of Hg shall not exceed either 1.2 lb/TBtu (30day rolling average) or 0.013 lb/GWh.  Also, 1.0 lb/TBtu with both units on a 90 day rolling average.

Compliance with the above emissions limits shall be demonstrated pursuant to one of the available options specified in 40 CFR 63, Subpart UUUUU (see attached Appendix NESHAP Subpart UUUUU, National Emission Standards for Hazardous Air Pollutants:  Coal- and Oil-Fired Electric Utility Steam Generating Units).  The permittee shall also comply with the recordkeeping and reporting requirements specified Subpart UUUUU, as applicable.  [40 CFR 63.9991 and Table 2 to Subpart UUUUU]

{Permitting Note:  Power output is on a gross basis for compliance with applicable emission limits.  You may not use the alternate SO2 emission limit in lieu of the HCl limit if your Electric Utility Steam Generating Unit does not have some form of FGD system and SO2 CEMS installed.}

The specific conditions in this section apply to the following emissions units:

| EU No. | Brief Description |
| --- | --- |
| 004 | Coal Transfer Baghouse |
| 005 | Coal Crusher Building Baghouse |
| 006 | Coal Plant Transfer and Silo Fill Area #1 Baghouse |
| 007 | Coal Plant Transfer and Silo Fill Area #2 Baghouse |
| 008 | Limestone Day Bin Baghouse |
| 009 | Pebble Lime Receiving Hopper Baghouse |
| 010 | Coal Reclaim Hopper Baghouse |
| 011 | Flyash Exhauster Filter #1 Baghouse |
| 012 | Flyash Exhauster Filter #2 Baghouse |
| 013 | Flyash Exhauster Filter #3 Baghouse |
| 014 | Flyash Exhauster Filter #4 Baghouse |
| 015 | Flyash Silo Bin Vent Filter Baghouse |
| 016 | Adipic Acid Storage Baghouse |
| 029 | Flyash Silo Bin Vent Filter Baghouse |

Fly ash silos handle fly ash from Steam Generators No. 1 and No. 2 respectively.  Fly ash is pneumatically conveyed from the individual electrostatic precipitators to Silos and then is gravity fed by tubing into totally enclosed tanker trucks.  Particulate matter (PM) emissions generated by silo loading and unloading to a tanker truck are controlled by baghouses in addition to reasonable precautions.  These units are subject to the applicable requirements under 40 CFR 60 Subpart Y - Standards of Performance for Coal Preparation Plants, since the facility has coal processing and conveying equipment (including breakers and crushers) and the facility commenced construction after October 24, 1974, per 40 CFR 60.250.

{Permitting notes:  The emissions units are regulated under Rule 62-210.300, F.A.C., Permits Required.  Because the potential to emit PM is below the major source threshold, these emissions units are not subject to CAM.}

Essential Potential to Emit (PTE) Parameters

- Hours of Operation.  Fly ash silos are each allowed to operate continuously (i.e., 8,760 hrs./yr.).  [Rule 62-210.200, F.A.C., Definition (PTE)]

Emission Limitations and Standards

{Permitting Note:  The attached Table 1, Summary of Air Pollutant Standards, summarizes information for convenience purposes only.  This table does not supersede any of the terms or conditions of this permit.}

Unless otherwise specified, the averaging times for Specific Conditions C.2 – C.3. are based on the specified averaging times of the applicable test method.

- Particulate Matter and Visible Emissions.  Particulate emissions from fly ash handling system shall be limited to 0.02 gr./acf.  A visible emission reading of 5% opacity or less may be used to establish compliance with this emission limit.  A visible emission reading greater than 5% opacity will not create a presumption that the 0.02 gr./acf emission limit is being violated.  However, a visible emission reading greater than 5% opacity will require the permittee to perform a stack test for particulate emissions.  [PPS PA 81-14/SA1]

- Fugitive Emissions.  The following requirements shall be met to minimize fugitive dust emissions from the coal storage and handling facilities, the limestone storage and handling facilities, haul roads and general plant operations:

a.	All conveyors and conveyor transfer points will be enclosed to preclude PM emissions (except those directly associated with the coal stacker/reclaimer and the emergency stockout facilities for which enclosure is operationally infeasible).  All coal and limestone conveyors not underground or within buildings will be enclosed (roof and sides) with steel grating or concrete floors (except the stacker/reclaimer which will have windscreen protection);

b.	Inactive coal storage piles will be shaped, compacted and oriented to minimize wind erosion.

c.	Water sprays or chemical wetting agents and stabilizers will be applied to storage piles, handling equipment, etc. during dry periods and as necessary to all facilities to maintain an opacity of less than or equal to 5 percent except when adding, transferring and/or removing coal from the coal pile during which the opacity allowed shall be 20%.

d.	The limestone handling receiver hopper will be equipped with water spray dust control facilities.  Limestone conveyors not underground or within buildings will be enclosed with open grating floors (except where concrete floors are provided over roads or other facilities).  Limestone day silos and associated transfer points will be maintained at negative pressures during filling operations with the exhaust vented to a control system.  Lime will be handled with a totally enclosed pneumatic system.  Exhaust from the lime silos during filling will be vented to a collector system.

e.	The fly ash handling system (including transfer and silo storage) will be totally enclosed and vented (including pneumatic system exhaust) through fabric filters.  Particulate emissions from fly ash handling system shall be limited to 0.02 gr./acf.  A visible emission reading of 5% opacity or less may be used to establish compliance with this emission limit.  A visible emission reading greater than 5% opacity will not create a presumption that the 0.02 gr./acf emission limit is being violated.  However, a visible emission reading greater than 5% opacity will require the permittee to perform a stack test for particulate emissions.

[PSD-FL-084]

Test Methods and Procedures

{Permitting Note:  The attached Table 2, Summary of Compliance Requirements, summarizes information for convenience purposes only.  This table does not supersede any of the terms or conditions of this permit.}

- Test Methods.  Required tests shall be performed in accordance with the following reference methods:

| Method | Description of Method and Comments |
| --- | --- |
| 5 | Method for Determining Particulate Matter Emissions (All PM is assumed to be PM10.) |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |

The above methods are described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [62-297.401, F.A.C.; PPS PA 81-14/SA1; and PSD-FL-084]

- Visible Emissions.  During each federal fiscal year (October 1 - September 30), unless otherwise specified by rule, order, or permit, the permittee shall have formal compliance test conducted on each silo baghouse for opacity.  Additionally, each baghouse shall be visually inspected on a daily basis to ensure that emissions are not visible.  Records shall be maintained documenting that such inspections took place.  Should emissions from a baghouse be visible, corrective action should be undertaken as well as conducting a Method 9 V.E.  Records should include color, duration, and density of the plume of any abnormal visible emissions detected, as well as the cause and corrective action taken for any abnormal visible emissions.  [Rule 62-297.310(7)(a)4., F.A.C., Rule 62-213.440, F.A.C.]

{Permitting note:  It is presumed that the threshold of visibility for opacity is equal to 5%.}

- Visible Emissions.  Compliance with the opacity limit listed in C.2. will be determined by EPA Reference Method 9.  [PPS PA 81-14/SA1]

Recordkeeping and Reporting Requirements

- Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for reporting requirements.

The specific conditions in this section apply to the following emissions units:

| EU No. | Brief Description |
| --- | --- |
| 025 | Stanton Unit A- Combined-Cycle Combustion Turbine |
| 026 | Stanton Unit A- Combined-Cycle Combustion Turbine |

These emissions units include two nominal 170 MW, General Electric “F” Class (PG7241FA) combustion turbine-electrical generators, fired with pipeline natural gas or diesel fuel oil and equipped with evaporative coolers on the inlet air system, two supplementary fired heat recovery steam generators (HRSG), each with a 160 ft. stack, and one steam turbine-electrical generator rated at approximately 300 MW.  Units 25 and 26 have a total nominal capacity of 640 MW and will achieve approximately 700 megawatts during extreme winter peaking conditions.

The combustion turbines are equipped with dry low NOX combustors and a selective catalytic reduction (SCR) system in order to control NOX emissions to 3.5 ppmvd at 15% O2 while firing natural gas.  During fuel oil firing, emissions shall be held to 10 ppmvd at 15% O2 using SCR plus water injection.  Pipeline quality natural gas, 0.05% sulfur fuel oil, by weight, and good combustion practices shall be used to control all pollutants.

The combustion turbines are subject to the requirements of Phase II of the federal Acid Rain Program.  These units hold ORIS code 55821.  Unit 025 commercial start date was April 28, 2003, and Unit 026 commercial start date was April 28, 2003.  Stack parameters are the same for both units:  stack height is 160 feet, exit diameter is 19 feet, exit temperature is 287 degrees Fahrenheit (F) and volumetric flow rate is 1,280,130 actual cubic feet per minute (acfm).

These emissions units are not subject to compliance assurance monitoring (CAM) because the NOX  CEMS is used for continuance compliance determination.  Thus, no CAM plan is included in this permit.

General

- NSPS Requirements.  Each combustion turbine (CT) shall comply with all applicable requirements of 40 CFR 60, adopted by reference in Rule 62-204.800(7)(b), F.A.C.

- Subpart A, General Provisions (see Specific Condition D.2)

- Subpart GG, Standards of Performance for Stationary Gas Turbines.  [See attached Appendix GG.]

[0950137-002-AC, Specific Condition 2.]

- General Provisions.  These emission units shall comply with all applicable requirements of 40 CFR 60, Subpart A, General Provisions, including:

- 40 CFR 60.7, Notification and Recordkeeping

- 40 CFR 60.8, Performance Tests

- 40 CFR 60.11, Compliance with Standards and Maintenance Requirements

- 40 CFR 60.12, Circumvention

- 40 CFR 60.13, Monitoring Requirements

- 40 CFR 60.19, General Notification and Reporting Requirements

[0950137-002-AC, Specific Condition 4.]

- Subpart GG.  Each emissions unit shall comply with all applicable provisions of 40 CFR 60, Subpart GG, Standards of Performance for Stationary Gas Turbines, adopted by reference in Rule 62-204.800(8), F.A.C.  The Subpart GG requirement to correct test data to International Organization for Standardization (ISO) conditions applies.  However, such correction is not used for compliance determinations with the BACT standard(s).  Compliance determination for BACT standards shall comply with all applicable provisions of 40 CFR 60, Subpart Da, Standards of Performance for Electric Utility Steam Generating Units Which Construction is Commenced After September 18, 1978, adopted by reference in Rule 62-204.800(8), F.A.C.  [0950137-002-AC, Specific Condition 5.]

- Operating Procedures.  Operating procedures shall include good operating practices and proper training of all operators and supervisors.  The good operating practices of pollution control equipment shall meet the guidelines and procedures as established by the equipment manufacturers.  All operators (including supervisors) of air pollution control devices shall be properly trained in plant specific equipment.  [Rule 62-4.070(3), F.A.C. and 0950137-002-AC, Specific Condition 14.]

- Circumvention.  The owner or operator shall not circumvent the air pollution control equipment or allow the emission of air pollutants without this equipment operating properly.  [Rule 62-210.650, F.A.C. and 0950137-002-AC, Specific Condition 15.]

Control Technology

- Equipment.  Dry low NOX (DLN) combustors and water injection capability are installed on each stationary combustion turbine.  The permittee has installed a selective catalytic reduction system to comply with the NOX and ammonia limits listed in Specific Condition D.13.  Additionally, space is provided for the installation of oxidation catalysts.  [Rules 62-4.070 and 62-212.400, F.A.C.; and 0950137-002-AC, Specific Condition 18.]

- Testing Locations.  The permittee shall design these units to accommodate adequate testing and sampling locations for compliance with the applicable emission limits (per each unit) listed in Specific Conditions D.13. - D.17.  [Rules 62-4.070 and 62-204.800, F.A.C.; 40 CFR 60.40Da; and 0950137-002-AC, Specific Condition 19.]

- Drift Eliminators.  Drift eliminators are installed on the cooling tower to reduce PM/PM10 emissions.  A certification letter, following installation (and prior to startup) shall be submitted that the drift eliminators were installed and that the installation is capable of meeting 0.002-gallons/100 gallons recirculation water flowrate.  [0950137-002-AC, Specific Condition 20.]

Essential Potential to Emit (PTE) Parameters

- Permitted Capacity.

- Combustion Turbine.  The maximum heat input rates to each CT/HRSG shall not exceed 2,402 million Btu (HHV) per hour (MMBtu/hr) when firing natural gas with duct burner firing and power augmentation or peak fire mode.  The maximum heat input rates to each CT/HRSG shall not exceed 2,068 MMBtu/hr (HHV) when firing fuel oil.  Manufacturer’s curves corrected for ISO conditions were provided to the Department of Environmental Protection (DEP) within 45 days prior to the completion of the initial compliance testing.

- Heat Recovery Steam Generator equipped with Duct Burner.  The maximum heat input rate of the natural gas fired duct burner shall not exceed 533 MMBtu/hour (LHV) (590 MMBtu/hour (HHV)) at any temperature or under any scenario.

[Rule 62-210.200, F.A.C. (Definitions - Potential Emissions); and 0950137-002-AC, Specific Conditions 10 and 11 and 0950137-046-AC, Specific Condition 2.]

{Permitting note:  Heat input capacity shall be determined by CEMS database used for the acid rain program.  CEMS data availability shall meet 40 CFR Part 75 requirements at greater than 95% of the time. Only valid hourly data shall be used to determine compliance with this provision. The source shall maintain this database for up to 5 years and make the information available upon request by the Department.}

- Emissions Unit Operating Rate Limitation After Testing.  See the related testing provisions in Appendix TR, Facility-wide Testing Requirements.  [Rule 62-297.310(2), F.A.C.]

- Hours of Operation.  Maximum allowable hours of operation for each CT/HRSG Emissions Unit are 8,760 hours per year while firing natural gas.  Fuel oil firing is permitted for 1,000 hours during any consecutive 12-month period in each CT.  [Rule 62-210.200, F.A.C. (Definitions - Potential Emissions); and 0950137-002-AC, Specific Condition 16.]

- Methods of Operation.

- Fuels.  Only pipeline natural gas or (up to) 1000 hours per year of 0.05%, by weight, distillate fuel oil shall be fired in each CT emissions unit.  Only natural gas shall be fired in each duct burner.

- Simple Cycle Operation.  The plant may not be operated without the use of the SCR system except during periods of startup and shutdown.

[Rule 62-210.200, F.A.C. (Definitions - Potential Emissions); and 0950137-002-AC, Specific Conditions 9 and 17.]

Emission Limitations and Standards

Unless otherwise specified, the averaging times for Specific Conditions D.13. through D.17. are based on the specified averaging time of the applicable test method.

- Nitrogen Oxides (NOx) and Ammonia Emissions.

- The concentration of NOx in the stack exhaust gas, with the combustion turbine operating on natural gas, shall not exceed 3.5 ppmvd @15% O2 on a 3-hour block average.  This limit shall apply whether or not the unit is operating with duct burner on and/or in power augmentation mode or peak fire mode.  Compliance shall be determined by the continuous emission monitor (CEMS).

- The emissions of NOx in the stack exhaust gas, with the combustion turbine operating on fuel oil shall not exceed 10.0 ppmvd @15% O2 on a 3-hour block average.  Compliance shall be determined by the continuous emission monitor (CEMS).

- Emissions of NOx from the duct burner shall not exceed 0.1 lb/MMBtu, which is more stringent than the NSPS .

- The concentration of ammonia in the exhaust gas from each CT/HRSG shall not exceed 5.0 ppmvd @15% O2.

[BACT Determination; Rules 62-4.070, 62-204.800(8), 62-212.400, and 62-4.070, F.A.C.; and 0950137-002 046-AC, Specific Condition 21 3.]

- Carbon Monoxide (CO) Emissions.  Emissions of CO in the stack exhaust gas with the combustion turbine operating on natural gas shall not exceed 17 ppmvd @15% O2 on a 24-hour block average to be demonstrated by CEMS; or 14 ppmvd @15% O2 with the CT operating on fuel oil on a 24-hr block average to be demonstrated by CEMS.  These limits shall also be demonstrated by annual stack test using EPA Method 10 or through annual relative accuracy test audit (RATA) testing.  [BACT Determination; Rule 62-212.400, F.A.C.; and Permit No. 0950137-043-AC, Specific Condition 2.]

- Volatile Organic Compounds (VOC) Emissions.  Emissions of VOC in the stack exhaust gas (baseload at ISO conditions) shall not exceed 2.7 ppmvd @15% O2 with the CT firing fuel oil or 6.3 ppmvd @15% O2 with the CT firing natural gas (with maximum duct burner firing and operating in power augmentation mode or peak fire mode).  [BACT Determination; Rule 62-212.400, F.A.C.; and 0950137-002 046-AC, Specific Condition 23 4.]

- Sulfur Dioxide (SO2) Emissions.  SO2 emissions shall be limited by firing pipeline natural gas (sulfur content not greater than 1.5 grains per 100 standard cubic feet) and up to 1,000 hours per consecutive 12-month period of 0.05% sulfur, by weight, fuel oil.  Compliance with these fuel limits in conjunction with implementation of the attached Appendix GG will demonstrate compliance with the applicable NSPS SO2 emissions limitations from the duct burner and the combustion turbine.  Note:  This will effectively limit the combined SO2 emissions for EU-025 and EU-026 to approximately 134 tons per year.  [BACT Determination; 40 CFR 60 Subpart GG; Rules 62-4.070, 62-212.400, and 62-204.800(8), F.A.C.; and 0950137-002-AC, Specific Condition 24.]

- PM/PM10 and Visible Emissions (VE).  Visible emissions shall not exceed 10 percent opacity from the stack in use.  [BACT Determination; Rules 62-4.070, 62-212.400 and 62-204.800(8), F.A.C.; and, 0950137-002-AC, Specific Condition 25.]

Excess Emissions

The Excess Emissions Rule at Rule 62-210.700, F.A.C., cannot vary any requirement of a NSPS or NESHAP provision.

- Excess Emissions Allowed.  Excess emissions resulting from startup, shutdown, fuel switching, or malfunction shall be permitted provided that best operational practices are adhered to and the duration of excess emissions shall be minimized.  Excess emissions occurrences shall in no case exceed two hours in any 24-hour period.  During any 24-hour period in which an hour of start-up or shutdown occurs, the following alternative emission limits shall apply on the basis of a 24-hour rolling average:

- An alternative NOx limit of 127 lb/hr shall apply if natural gas is the exclusively fired fuel;

- An alternative NOx limit of 370 lb/hr shall apply if any fuel oil is fired; and,

- An alternative CO limit of 155 lb/hr firing either natural gas or fuel oil.

The 24-hour averages shall be based on all available data excluding calibration data.  Operation below 50% output per turbine shall otherwise be limited to 2 hours in any 24-hour period.

[BACT Determination; Rule 62-210.700, F.A.C.; and 0950137-002-AC, Specific Condition 26., modified on May 16, 2003.].

- Excess Emissions Prohibited.  Excess emissions entirely or in part by poor maintenance, poor operation, or any other equipment or process failure that may reasonably be prevented during startup, shutdown or malfunction, shall be prohibited pursuant to Rule 62-210.700, F.A.C.  These emissions shall be included in the 3-hr average for NOX and the 24-hr average for CO.  [0950137-002-AC, Specific Condition 27.]

Monitoring of Operations

- Subpart Da Monitoring and Recordkeeping Requirements.  The permittee shall comply with all applicable requirements of 40 CFR 60 Subpart Da.  [40 CFR 60, Subpart Da; and 0950137-002-AC, Specific Condition 44.].

- Selective Catalytic Reduction System (SCR) Compliance Procedures.

- At permit renewal a test for nitrogen oxides and ammonia from the CT/HRSG pair shall be simultaneously conducted while operating in the power augmentation mode with the duct burner and operating on the primary fuel.  The RATA for NOX may be used in lieu of stack testing.  The ammonia injection rate necessary to comply with the NOX standard shall be established and reported during the each performance test.

- The SCR shall operate at all times that the turbine is operating, except during turbine start-up and shutdown periods, as dictated by manufacturer's guidelines and in accordance with this permit.

- The permittee shall install and operate an ammonia flow meter to measure and record the ammonia injection rate to the SCR system of the CT/HRSG set.  It shall be maintained and calibrated according to the manufacturer’s specifications.

- During the stack test, the permittee (at each tested load condition) shall determine and report the ammonia flow rate required to meet the emissions limitations.  During NOX CEM downtimes or malfunctions, the permittee shall operate at the ammonia flow rate, which was established during the last stack test.

- In the event of a complaint or concern by an inspector, the permittee shall be capable of making an instantaneous measurement using inlet and outlet NOX concentrations from the SCR system and ammonia flow supplied to the SCR system to determine ammonia slip.  This determination shall not be used as a compliance method but only as an indicator to determine if a special compliance test is needed to demonstrate NOX and ammonia slip requirements of the permit.  The calculation procedure shall be provided with the CEM monitoring plan required by 40 CFR Part 75.  The following calculation represents one means by which the permittee may demonstrate compliance with this condition:

Ammonia slip @ 15%O2 = (A-(BxC/1,000,000)) x (1,000,000/B) x D,

where:  	A= ammonia injection rate (lb/hr)/ 17 (lb/lb.mol)

B = dry gas exhaust flow rate (lb/hr) / 29 (lb/lb.mol)

C = change in measured NOX (ppmv@15%O2) across catalyst

D = correction factor, derived annually during compliance testing by comparing actual to tested ammonia slip

[Note:  exhaust gas flow rate may be back calculated using heat input and F factor.]

- The calculation along with each newly determined correction factor shall be submitted with each annual compliance test.  Calibration data (“as found” and “as left”) shall be provided for each measurement device utilized to make the ammonia emission measurement and submitted with each annual compliance test.

- Upon specific request by the Department, a special re-test shall occur as described in the previous conditions concerning annual test requirements, in order to demonstrate that all NOX and ammonia slip related permit limits can be complied with.

[0950137-002-AC, Specific Condition 45; and 0950137-043-AC, Specific Condition 4.]

Continuous Monitoring Requirements

- Continuous Monitoring Systems.  The permittee shall calibrate, maintain, and operate a continuous emission monitor in the stack to measure and record the emissions of NOX and CO from these emissions units, and the Carbon Dioxide (CO2) content of the flue gas at the location where NOX and CO are monitored, in a manner sufficient to demonstrate compliance with the emission limits of this permit.  The CEM system shall be used to demonstrate compliance with the emission limits for NOX and CO established in this permit.  Compliance with the emission limits for NOX shall be based on a 3-hour block average.  The 3-hour block average shall be calculated from 3 consecutive hourly average emission rate values.  Compliance with the emission limits for CO shall be based on a 24-hour block average starting at midnight of each operating day.  The 24-hour block average shall be calculated from 24 consecutive hourly average emission rate values.  Each hourly value shall be computed using at least one data point in each fifteen-minute quadrant of an hour, where the unit combusted fuel during that quadrant of an hour.  Notwithstanding this requirement, an hourly value shall be computed from at least two data points separated by a minimum of 15 minutes (where the unit operates for more than one quadrant of an hour).  The owner or operator shall use all valid measurements or data points collected during an hour to calculate the hourly averages.  All data points collected during an hour shall be, to the extent practicable, evenly spaced over the hour.  The permittee may use the inlet SCR NOX monitor as a backup analyzer in determining excess emissions during startup. If the CEM system measures concentration on a wet basis, the CEM system shall include provisions to determine the moisture content of the exhaust gas and an algorithm to enable correction of the monitoring results to a dry basis (0% moisture).  Alternatively, the owner or operator may develop through manual stack test measurements a curve of moisture contents in the exhaust gas versus load for each allowable fuel, and use these typical values in an algorithm to enable correction of the monitoring results to a dry basis (0% moisture).  Final results of the CEM system shall be expressed as ppmvd, corrected to 15% oxygen.

- NOX  Monitor.  The NOX monitor shall be certified and operated in accordance with the following requirements.  The NOX monitor shall be certified pursuant to 40 CFR Part 75 and shall be operated and maintained in accordance with the applicable requirements of 40 CFR Part 75, Subparts B and C.  For purposes of determining compliance with the emission limits specified within this permit, missing data shall not be substituted.  Instead the block average shall be determined using the remaining hourly data in the 3-hour block.  However, in the event that the permittee maintains 95% or greater availability of the continuous emission monitoring systems used for determining NOX emissions compliance for the previous quarter, then compliance with the emission limits for NOX shall be based on 3 valid consecutive hours of data for a 3-hour block average.  Record keeping and reporting shall be conducted pursuant to 40 CFR Part 75, Subparts F and G.  The RATA tests required for the NOX monitor shall be performed using EPA Method 20 or 7E, of Appendix A of 40 CFR 60.  The NOX monitor shall be a dual range monitor.  The span for the lower range shall be between or inclusive of the values of 10 and 20 ppm, and the span for the upper range shall be between or inclusive of the values of 200 and 250 ppm, as corrected to 15% O2.

- CO Monitor.  The CO monitor and CO2 monitor shall be certified and operated in accordance with the following requirements.  The CO monitor shall be certified pursuant to 40 CFR 60, Appendix B, Performance Specification 4.  The CO2 monitor shall be certified pursuant to 40 CFR 60, Appendix B, Performance Specification 3.  Quality 	assurance procedures shall conform to the requirements of 40 CFR 60, Appendix F, and the Data Assessment 	Report of section 7 shall be made each calendar quarter, and reported semi-annually to the Department’s Central District Office.  The RATA tests required for the CO monitor shall be performed using EPA Method 10, of Appendix A of 40 CFR 60.  The Method 10 analysis shall be based on a continuous sampling train, and the ascarite trap may be omitted or the interference trap of section 10.1 may be used in lieu of the silica gel and ascarite traps.  The CO monitor shall be a dual range monitor.  The span for the lower range shall be between or inclusive of the values of 20 and 30 ppm, and the span for the upper range shall be between or inclusive of the values of 500 and 1000 ppm, as corrected to 15% O2.  The RATA tests required for the CO2 monitor shall be performed using EPA Method 3A, of Appendix A of 40 CFR 60.

- NOX, CO and CO2 emissions data shall be recorded by the CEM system during episodes of startup, shutdown and malfunction.  NOX and CO emissions data recorded during malfunctions may be excluded from the block average calculated to demonstrate compliance with the emission limits specified within this permit.

- Best operational practices shall be used to minimize hourly emissions that occur during episodes of startup, shutdown and malfunction.  Emissions of any quantity or duration that occur entirely or in part from poor maintenance, poor operation, or any other equipment or process failure, which may reasonably be prevented, shall be prohibited.

- A summary report of duration of data excluded from the block average calculation, and all instances of missing data from monitor downtime, shall be reported to the Department’s Central District office semi-annually, and shall be consolidated with the report required pursuant to 40 CFR 60.7.  For purposes of reporting “excess emissions” pursuant to the requirements of 40 CFR 60.7, excess emissions shall be defined as the hourly emissions which are recorded by the CEM system during periods of data excluded for episodes of startup, shutdown and malfunction, allowed above.  The duration of excess emissions shall be the duration of the periods of data excluded for such episodes.  Reports required by this paragraph and by 40 CFR 60.7 shall be submitted no less than semi-annually, including semi-annual periods in which no data is excluded or no instances of missing data occur.  Upon request from the Department, the CEMS emission rates shall be corrected to ISO conditions to demonstrate compliance with the applicable standards of 40 CFR 60.332.

[Note:  Compliance with these requirements will ensure compliance with the other CEM system requirements of this permit to comply with Subpart GG requirements, as well as the applicable requirements of Rule 62-297.520, F.A.C., 40 CFR 60.7(a)(5) and 40 CFR 60.13, and with 40 CFR Part 51, Appendix P, 40 CFR 60, Appendix B, Performance Specifications and 40 CFR 60, Appendix F, Quality Assurance Procedures].

[Rules 62-4.070(3) and 62-212.400., F.A.C.; BACT Determination; and 0950137-004-AC, Specific Condition 41., modified on May 16, 2003.]

- Continuous Monitoring System Requirements.  The monitoring devices shall comply with the certification and quality assurance, and any other applicable requirements of Rule 62-297.520, F.A.C., 40 CFR 60.13, including certification of each device in accordance with 40 CFR 60, Appendix B, Performance Specifications and 40 CFR 60.7(a)(5) or 40 CFR Part 75.  Quality assurance procedures must conform to all applicable sections of 40 CFR 60, Appendix F or 40 CFR 75.  [0950137-002-AC, Specific Condition 42.]

Test Methods and Procedures

{Permitting Note:  The attached Table 2, Summary of Compliance Requirements, summarizes information for convenience purposes only.  This table does not supersede any of the terms or conditions of this permit.}

- Test Methods.  Required tests shall be performed in accordance with the following reference methods:

| Method | Description of Method and Comments |
| --- | --- |
| 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| 7E | Determination of Nitrogen Oxide Emissions from Stationary Sources |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |
| 10 | Determination of Carbon Monoxide Emissions from Stationary Sources {Note: The method shall be based on a continuous sampling train.} |
| 18 | Measurement of Gaseous Organic Compound Emissions by Gas Chromatography |
| 20 | Determination of Nitrogen Oxides, Sulfur Dioxide and Diluent Emissions from Stationary Gas Turbines |
| 25, 25A | Method for Determining Gaseous Organic Concentrations (Flame Ionization) |
| CTM-027, 320 | Conditional EPA Test Method 027, Measurement of Ammonia Slip (or equivalent method) |

The above methods are described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Rule 62-297.401, F.A.C.; 0950137-002-AC]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- Annual Compliance Tests Required.  During each federal fiscal calendar year (October 1st to September 30th January 1st to December 31st), each EU shall be tested to demonstrate compliance with the emissions standards for visible emissions, carbon monoxide, and nitrogen oxides.  The Relative Accuracy Test Audits (RATA) for NOX and CO CEMS may be used in lieu of annual stack testing for these pollutants.  No annual stack test is required for NOx and CO so long as NOx and CO CEMS are utilized that meet the applicable quality assurance and quality control requirements of 40 CFR Part 60 and Part 75.   A VE tests is not required when firing fuel oil so long as total fuel oil firing during the fiscal year is less than 400 hours.  An annual VE test is required when firing the primary fuel.  Ammonia Slip testing while firing the primary fuel is required prior to the renewal of each operation permit. [Rule 62-297.310(7 8), F.A.C.; and Permit No.0950137-043 046-AC, Specific Condition 3 6.]

- Compliance Tests Prior To Renewal.  Compliance tests shall be performed for visible emissions, carbon monoxide, nitrogen oxides, and ammonia slip and volatile organic compounds once every 5 years.  No annual stack test is required for NOx and CO so long as NOx and CO CEMS are utilized that meet the applicable quality assurance and quality control requirements of 40 CFR Part 60 and Part 75.  Tests shall not be required for any unit with emissions generated solely from the combustion of fuel oil provided that during the previous permit cycle, the unit did not burn any fuel oil for more than 400 hours, other than during startup, during each calendar year included in the five-year period of permitted operation.  The tests shall occur prior to obtaining a renewed operating permit to demonstrate compliance with the emission limits in Specific Conditions D.13 - D.17.  [Rules 62-210.300(2)(a) and 62-297.310(7 8)(a), F.A.C. and 0950137-046-AC, Specific Condition 7]

- Performance Tests.  Performance tests shall be conducted after any replacement of the major components of the air pollution control equipment (and shake down period not to exceed 100 days after re-starting the CT), such as replacement of SCR catalyst or addition of oxidation catalyst (or change of combustors, if specifically requested by the DEP on a case-by-case basis).  Annual compliance tests shall be performed during every federal fiscal calendar year (October 1st to September 30th January 1st to December 31st) pursuant to Rule 62-297.310(7 8), F.A.C.  The reference methods listed in Specific Condition D.24. shall be used.  No other test methods may be used for compliance testing unless prior DEP approval is received in writing.  The applicant shall calculate and report the ppmvd ammonia slip (@ 15% O2) at the measured lb/hr NOX emission rate as a means of compliance with the BACT standard.  The applicant shall also be capable of calculating ammonia slip at the Department’s request.  [0950137-002 046-AC, Specific Condition 30. 5; and Applicant request in an e-mail memorandum received on October 7, 2004.]

- Continuous Compliance with the CO and NOX Emission Limits.  Continuous compliance with the CO and NOX emission limits shall be demonstrated by the CEMS equipment on the specified hourly average basis.  Based on CEMS data, a separate compliance determination is conducted at the end of each period and a new average emission rate is calculated from the arithmetic average of all valid hourly emission rates from the previous period.  [Rules 62-4.070 F.A.C., 62-210.700, F.A.C., 40 CFR 75 and BACT; and 0950137-002-AC, Specific Condition 31.]

- Compliance with the SO2 and PM/PM10 Emission Limits.  For the purposes of demonstrating compliance with the 40 CFR 60.333 SO2 standard, the applicant is responsible for ensuring that the procedures outlined in attached Appendix GG are complied with.  [0950137-002-AC, Specific Condition 32.]

- Compliance with CO Emission Limit.  An annual test for CO shall be conducted at 100% capacity with the duct burners off.  The NOX and CO test results shall be the average of three valid one-hour runs.  Annual RATA testing for the CO and NOX CEMS shall be required pursuant to 40 CFR 75 and may substitute for the annual CO stack testing requirement.  [0950137-002-AC, Specific Condition 33.]

- Compliance with the VOC Emission Limit.  An initial test was required to demonstrate compliance with the VOC emission limit.  Thereafter, the CO emission limit shall be employed as a surrogate and no annual testing or permit renewal testing is required.  [0950137-002 046-AC, Specific Condition 34 8.]

- Testing Procedures.  Unless otherwise specified, testing of emissions shall be conducted with the combustion turbine operating at permitted capacity.  Permitted capacity is defined as 90-100 percent of the maximum heat input rate allowed by the permit, corrected for the average inlet air temperature during the test (with 100 percent represented by a curve depicting heat input vs. inlet temperature).  Procedures for these tests shall meet all applicable requirements (i.e., testing time frequency, minimum compliance duration, etc.) of Chapters 62-204 and 62-297, F.A.C.  [0950137-002-AC, Specific Condition 35.]

Recordkeeping and Reporting Requirements

- Reporting Schedule.  The following reports and notifications shall be submitted to the Compliance Authority:

| Report | Reporting Deadline | Related Condition(s) |
| --- | --- | --- |
| Notice of Excess Emissions | Quarterly | D.37. |

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.

- Records.  All measurements, records, and other data required to be maintained by the applicant shall be recorded in a permanent form and retained for at least five (5) years following the date on which such measurements, records, or data are recorded.  These records shall be made available to Department representatives upon request.  The applicant will be required to maintain records indicating the daily hours of operation of each CT/HRSG unit.  These records shall specify which type of fuel is being combusted and the records shall be available for review at the site.  Each calendar month, a compilation of the hours of operation for each CT/HRSG unit combusting fuel oil shall be made and totalized for the most recent consecutive 12-month period.  Each annual operating report (AOR) submitted by the applicant shall include a compilation of each consecutive 12-month period during the preceding calendar year.  [0950137-002-AC, Specific Condition 39.]

- Excess Emissions Report.  If excess emissions occur for more than two hours due to malfunction, the owner or operator shall notify the Department’s Central District Office within (1) working day of:  the nature, extent, and duration of the excess emissions; the cause of the excess emissions; and the actions taken to correct the problem.  In addition, the Department may request a written summary report of the incident.  Pursuant to the New Source Performance Standards, all excess emissions shall also be reported in accordance with 40 CFR 60.7, Subpart A.  Following this format, 40 CFR 60.7, and using the monitoring methods listed in this permit, periods of startup, shutdown, malfunction, shall be monitored, recorded, and reported as excess emissions when emission levels exceed the permitted standards listed in Specific Conditions D.14. through D.17.  [Rules 62-4.130, 62-204.800, 62-210.700(6), F.A.C.; 40 CFR 60.7; and 0950137-002-AC, Specific Condition 28.]

- Quarterly Reports.  Quarterly excess emission reports, in accordance with 40 CFR 60.7, shall be submitted to the Department’s Central District Office.  [0950137-002-AC, Specific Condition 14., Section II.]

- Actual Emissions Reporting.  Because the review and issuance of permit No. 0950137-046-AC was based on an analysis that compared baseline actual emissions to projected actual emissions which was relied upon to avoid the requirements of subsections 62-212.400(4) through (12), F.A.C., for emissions of nitrogen oxides (NOX), the permittee is subject to the following monitoring, reporting and recordkeeping provisions:

- The permittee shall monitor the emissions of NOX emitted by EUs 025 and 026; and, using the most reliable information available, calculate and maintain a record of the annual emissions, in tons per year on a calendar year basis, for a period of 5 years following resumption of regular operations after the change (Calendar years 2016 through 2020).  Emissions shall be computed in accordance with the provisions in Rule 62-210.370, F.A.C., which are provided in Appendix RR of this permit.

- The permittee shall submit a report to the Department within 60 days after the end of each calendar year specified in paragraph D.39a., documenting the unit’s annual emissions of NOX during the previous calendar year.  The report shall contain the following:

  - The name, address and telephone number of the owner or operator of the major stationary source;

  - The annual emissions calculations pursuant to the provisions of 62-210.370, F.A.C., which are provided in Appendix RR of this permit;

  - If the emissions differ from the preconstruction projection, an explanation as to why there is a difference; and

  - Any other information that the owner or operator wishes to include in the report.

[Rules 62-212.300(1)(e) & 62-210.370, F.A.C.; and, Permit No. 0950137-046-AC]

{Permitting note:  Actual Emissions - 92.93 TPY (Baseline Actual Emissions) = < 40 TPY of NOX emissions.  According to the applicant, the changes authorized by project 0950137-046-AC became effective on December 4, 2015.  Therefore, the 5 year reporting period for these EUs shall be for operations during calendar years 2016 through 2020, reported in calendar years 2017 through 2021.}

This section of the permit addresses the following emissions unit.

| EU ID No. | Emission Unit Description |
| --- | --- |
| 037 | Stanton Unit B - 300 MW Combined Cycle Combustion Turbine |

Unit B consists of:  one nominal 150 megawatts (MW) General Electric 7241 FA combustion turbine-electrical generator (CTG); a supplementary fired heat recovery steam generator (HRSG) with natural gas fueled duct burners (DB); and a nominal 150 MW steam turbine generator (STG) for an overall nominal rating of 300 MW.  This unit includes highly automated controls, described as the GE Mark VI Gas Turbine Control System to fulfill all of the gas turbine control requirements.  The stack height is 205 feet, exit diameter is 20 feet, stack exit temperature is 262 (gas) and 272 (oil) degrees Fahrenheit (F) and volumetric flow rate is 1,239,934 (gas) and 1,031,061 (oil) actual cubic feet per minute (acfm).

Unit B uses natural gas as the primary fuel, and Ultra Low Sulfur Diesel (ULSD) fuel oil (0.0015% Sulfur) as a backup fuel.  Carbon monoxide (CO) and particulate matter  (PM/PM10/PM2.5) emissions are minimized by the efficient combustion of natural gas and ULSD fuel oil at high temperatures.  Emissions of sulfuric acid mist (SAM) and sulfur dioxide (SO2) are minimized by firing natural gas and ULSD fuel oil.  Nitrogen oxide (NOX) emissions are reduced with dry low-NOX (DLN) combustion technology for gas firing and water injection for oil firing.  In combination with these NOX controls, a selective catalytic reduction (SCR) system further reduces NOX emissions during combined cycle operation.

Unit B is required to continuously monitor NOX emissions in accordance with the acid rain provisions.  The same CEMS as well as CO CEMS are employed for demonstration of continuous compliance with certain Best Available Control Technology (BACT) determinations.  Flue gas oxygen content or carbon dioxide content are monitored as a diluent gas.

Unit B is subject to the requirements of Phase II of the federal Acid Rain Program.  This unit holds ORIS code 0564.  This emissions unit is not subject to compliance assurance monitoring (CAM) because the NOX CEMS is used for continuous compliance determination.  Thus, no CAM plan is included in this permit for this unit.  Unit B began commercial operation on October 27, 2009.

{Permitting Note:  This emissions unit and its auxiliary equipment were reviewed under the rules for the Prevention of Significant Deterioration (PSD), Rule 62-212.400, F.A.C.  Permit No. 0950137-020-AC/PSD-FL-373A was issued on May 9, 2008.  Best Available Control Technology (BACT) determinations were made for nitrogen oxides (NOX), carbon monoxide (CO), volatile organic compounds (VOC), particulate matter (PM/PM10/PM2.5), sulfuric acid mist (SAM), and sulfur dioxide (SO2)in accordance with Rule 62-210.200 (Definitions).  This unit is also regulated under Rule 62-212.400 (PSD), F.A.C., Acid Rain-Phase II and  40 CFR 60 - NSPS, Subpart KKKK.  Because the existing facility is a major source of hazardous air pollutants (HAP), Unit B is potentially subject to 40 CFR63 - NESHAP, Subpart YYYY - National Emission Standards for Hazardous Air Pollutants for Stationary Combustion Turbines.  However, the applicability of this rule has been stayed for lean premix and diffusion flame gas-fired combustion turbines such as planned for this project.}

General

- BACT Requirements.  Unit B is subject to BACT requirements for carbon monoxide (CO), nitrogen oxides (NOX), particulate matter (PM/PM10/PM2.5), sulfuric acid mist (SAM), and sulfur dioxide (SO2).  [Rule 62-212.400, F.A.C.; and, Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.1.]

- NSPS Requirements.  Unit B shall comply with all applicable requirements of 40 CFR 60, listed below, adopted by reference in Rule 62-204.800(7)(b), F.A.C.  The Department determines that compliance with the BACT emissions performance requirements also assures compliance with the NSPS for Subpart KKKK.  Some separate reporting and monitoring may be required by these subparts.

- Subpart A, General Provisions, including:

      - 40 CFR 60.7, Notification and Record Keeping

      - 40 CFR 60.8, Performance Tests

      - 40 CFR 60.11, Compliance with Standards and Maintenance Requirements

(4)	40 CFR 60.12, Circumvention

(5)	40 CFR 60.13, Monitoring Requirements

(6)	40 CFR 60.19, General Notification and Reporting Requirements

- Subpart KKKK, Standards of Performance for Stationary Gas Turbines:  These provisions include standards for combustion gas turbines and duct burners.

[Rule 62-204.800, F.A.C.; and, Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.2.]

Equipment

- CTG.  The permittee is authorized to tune, operate, and maintain one natural gas-fueled GE Model 7FA CTG with a nominal generating capacity of 150 MW.  The CTG is equipped with Dry Low NOx (DLN) combustors, an inlet air filtration system with evaporative coolers, power (steam) augmentation capability and the capability to fire ULSD fuel oil.  The unit shall be equipped with the SpeedtronicTM Mark VI (or more recent version) automated gas turbine control system.  [Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.3.]

- HRSG.  The permittee is authorized to operate, and maintain one HRSG with a HRSG exhaust stack.  The HRSG shall be designed to recover heat energy from the gas turbine and deliver steam to the steam turbine electrical generator with a nominal generating capacity of 150 MW.  The HRSG is equipped with supplemental gas-fired DB having a nominal heat input rate of 531 MMBtu (higher heating value (HHV)).  [Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.4.]

Control Technology

- DLN Combustion.  The permittee shall operate and maintain the GE DLN 2.6 combustion system (or better) to control NOX emissions from the CTG when firing natural gas.  The system shall be maintained and tuned in accordance with the manufacturer’s recommendations.  [Rule 62-212.400(BACT), F.A.C.; and, Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.5.]

- Wet Injection.  The permittee shall operate, and maintain a wet injection system (water or steam) to reduce NOX emissions from the CTG when ULSD fuel oil is fired.  The system shall be maintained and tuned in accordance with the manufacturer’s recommendations.  [Rule 62-212.400(BACT), F.A.C.; and, Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.6.]

- Selective Catalytic Reduction (SCR) System.  The permittee shall, tune, operate, and maintain an SCR system to control NOX emissions from the gas turbine when firing either natural gas or ULSD fuel oil.  The SCR system consists of an ammonia (NH3) injection grid, catalyst, ammonia storage, monitoring and control system, electrical, piping and other ancillary equipment.  The SCR system shall be designed, constructed and operated to achieve the permitted levels for NOX and NH3 emissions.

Ammonia Storage:  In accordance with 40 CFR 68.130, the storage of ammonia shall comply with all applicable requirements of the Chemical Accident Prevention Provisions in 40 CFR 68.

[Rule 62-212.400(BACT), F.A.C.; and, Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.7.]

Performance Restrictions

- Capacity – CTG.  The nominal heat input rating excluding steam for power augmentation of the CTG is 1,765 MMBtu per hour when firing natural gas and 1,935 MMBtu per hour when firing ULSD fuel oil based on a compressor inlet air temperature of 70° F, the higher heating value (HHV) of each fuel, and 100% load.  Heat input rates will vary depending upon gas turbine characteristics, ambient conditions, alternate methods of operation, and evaporative cooling.  The permittee shall have provided manufacturer’s performance curves (or equations) that correct for site conditions to the Permitting and Compliance Authorities within 45 days of completing the initial compliance testing and shall provide updated curves following any maintenance or tuning sessions that results in a change to the previously submitted curves.  Operating data may be adjusted for the appropriate site conditions in accordance with the performance curves and/or equations on file with the Department.  [Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.8.]

- Capacity - DB.  The nominal heat input rating of the DB located within the HRSG is 531 MMBtu per hour based on the higher heating value (HHV) of natural gas.  Only natural gas shall be fired in the DB.  [Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.9.]

- Hours of Operation.  The gas turbine may operate throughout the year (8760 hours per year).  Restrictions on individual methods of operation are specified in separate conditions.  [Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.10.]

- Authorized Fuels.  The CTG turbine shall fire natural gas as the primary fuel, which shall contain no more than 2.0 grains of sulfur per 100 standard cubic feet (gr S/100 SCF) of natural gas.  As a restricted alternate fuel, the CTG may fire ULSD fuel oil containing no more than 0.0015% sulfur by weight.  The CTG shall fire no more than 1000 hours of ULSD fuel oil, regardless of mode, during any calendar year.  [Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.11.]

- Methods of Operation.  Subject to the restrictions and requirements of this permit, the gas turbine may operate under the following methods of operation.

- Combined Cycle Operation.  The CTG/HRSG system may operate to produce direct, shaft-driven electrical power and steam-generated electrical power from the steam turbine-electrical generator as a combined cycle unit subject to the restrictions of this permit.  In accordance with the specifications of the SCR and HRSG manufacturers, the SCR system shall be on line and functioning properly during combined cycle operation or when the HRSG is producing steam.

- Pseudo Simple Cycle Operation.  The CTG/HRSG system may operate in a pseudo simple cycle mode where steam from the HRSG bypasses the steam turbine electrical generator and is dumped directly to the condenser.  This is not considered a separate mode of operation with respect to emission limits (i.e. emission limits of combined cycle operation still apply).

- Evaporative Cooling.  Evaporative cooling is the passing of gas turbine compressor inlet air through a wetted media, which reduces the inlet air temperature through evaporative cooling.  Lower compressor inlet temperatures result in more mass flow rate through the gas turbine with a boost in electrical power production.  The emissions performance remains within the normal profile of the gas turbine for the lower compressor inlet temperatures.  Evaporative cooling may be implemented at ambient temperatures of 60° F or higher.

- Power Augmentation (PA).  PA provides additional direct, shaft-driven electrical power by increasing the mass flow rate through the compressor by the injection of steam.  Steam for PA is taken from the HRSG and is introduced into the gas turbine compressor discharge, thus increasing the power produced by the expander portion of the turbine.

- DB Firing.  The HRSG system may fire natural gas in the DB to provide additional steam-generated electrical power.

[Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.12.]

Emissions Standards

- Emission Standards.  Emissions from the CTG/HRSG system shall not exceed the following standards.

| Pollutant | Fuel | Method of Operation | Annual Stack Tests 3-Run Average |  |  | CEMS Block Average |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | ppmvd @15% O2 |  | lb/hr f | ppmvd @ 15% O2 |
| CO a | Oil | Combustion Turbine (CTG) | 8.0 |  | 36.7 | 8.0, 24-hr |
|  | Gas | CTG Normal | 4.1 |  | 15.9 |  |
|  |  | CTG & Duct Burner (DB) | 7.6 |  | 37.2 |  |
|  |  | CTG Low Load | N/A |  | N/A |  |
|  |  | CTG & PA with or w/o DB | N/A |  | N/A | 14, 24-hr |
|  | Oil/Gas | All Modes | N/A |  | N/A | 6.0, 12-month |
| NOX b | Oil | CTG | 8.0 |  | 60.3 | 8.0, 24-hr |
|  | Gas | CTG Normal | 2.0 |  | 12.7 | 2.0, 24-hr |
|  |  | CTG & DB | 2.0 |  | 16.1 |  |
|  |  | CTG & PA with or w/o DB | N/A |  | N/A |  |
| PM/PM10/PM2.5 c | Oil/Gas | All Modes | 2 gr S/100 SCF of gas, 0.0015% sulfur fuel oil |  |  |  |
|  |  |  | Visible emissions shall not exceed 10% opacity for each 6-minute block average. |  |  |  |
| SAM/SO2 d | Oil/Gas | All Modes | 2 gr S/100 SCF of gas, 0.0015% sulfur fuel oil |  |  |  |
| Ammonia e | Oil/Gas | CTG, All Modes | 5.0 | N/A |  | N/A |

- Continuous compliance with the 24-hour CO standards shall be demonstrated based on data collected by the required CEMS.  The annual EPA Method 10 tests associated with the certification of the CEMS instruments shall also be used to demonstrate compliance with the individual standards for natural gas, fuel oil, and basic duct burner mode.  Compliance with the 24-hour CO CEMS standards shall be determined separately for the PA mode and all other modes based on the hours of operation for each mode.

- Continuous compliance with the 24-hr NOX standards shall be demonstrated based on data collected by the required CEMS.  The annual EPA Method 7E or Method 20 tests associated with demonstration of compliance with 40 CFR 60, Subpart KKKK or certification of the CEMS instruments shall also be used to demonstrate compliance with the individual standards for natural gas, fuel oil, and duct burner modes during the time of those tests.  NOX mass emission rates are defined as oxides of nitrogen expressed as nitrogen dioxide (NO2).

- The fuel sulfur specifications combined with the efficient combustion design and operation of the gas turbine represents (BACT) for PM/PM10/PM2.5 emissions.  Compliance with the fuel specifications, CO standards, and visible emissions standards shall serve as indicators of good combustion.  Compliance with the fuel specifications shall be demonstrated by keeping records of the fuel sulfur content as detailed in Specific Condition F.31.  Compliance with the visible emissions standard shall be demonstrated by conducting tests in accordance with EPA Method 9.

- The fuel sulfur specifications effectively limit the potential emissions of SAM and SO2 from the gas turbines and represent BACT for these pollutants.  Compliance with the fuel sulfur specifications shall be determined by the ASTM methods for determination of fuel sulfur as detailed Specific Condition F.31.

- Compliance with the ammonia slip standard shall be demonstrated by conducting tests in accordance with EPA Method CTM-027 or EPA Method 320.

- The mass emission rate standards are based on a turbine inlet condition of 70 °F, evaporative cooling on, and using the HHV of the fuel.  Mass emission rate may be adjusted to actual test conditions in accordance with the performance curves and/or equations on file with the Department.

[Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.13]

Excess Emissions

{Permitting Note:  The following conditions apply only to the SIP-based emissions standards specified in Condition No. F. 13 of this section.  Rule 62-210.700, F.A.C. (Excess Emissions) cannot vary or supersede any federal provision of the NSPS, or Acid Rain programs.}

- Operating Procedures.  BACT determinations established by this permit rely on “good operating practices” to reduce emissions.  Therefore, all operators and supervisors shall be properly trained to operate and ensure maintenance of the CTG, DB, HRSG, and pollution control systems in accordance with the guidelines and procedures established by each manufacturer.  The training shall include good operating practices as well as methods for minimizing excess emissions.  [Rules 62-4.070(3) and 62-212.400(BACT), F.A.C.; and, Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.14]

- Definitions.

    - Startup is defined as the commencement of operation of any emissions unit which has shut down or ceased operation for a period of time sufficient to cause temperature, pressure, chemical or pollution control device imbalances, which result in excess emissions.  [Rule 62-210.200(245), F.A.C.]

    - Shutdown is the cessation of the operation of an emissions unit for any purpose.
[Rule 62-210.200(230), F.A.C.]

    - Malfunction is defined as any unavoidable mechanical and/or electrical failure of air pollution control equipment or process equipment or of a process resulting in operation in an abnormal or unusual manner.  [Rule 62-210.200(159), F.A.C.]

[Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.15]

- Excess Emissions Prohibited.  Excess emissions caused entirely or in part by poor maintenance, poor operation or any other equipment or process failure that may reasonably be prevented during startup, shutdown or malfunction shall be prohibited.  All such preventable emissions shall be included in any compliance determinations based on CEMS data.  [Rule 62-210.700(4), F.A.C.; and, Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.16]

- Alternate Visible Emissions Standard.  Visible emissions due to startups, shutdowns, and malfunctions shall not exceed 10% opacity except for up to ten, 6-minute averaging periods during a calendar day, which shall not exceed 20% opacity.  [Rule 62-212.400(BACT), F.A.C.; and, Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.17]

- Excess Emissions Allowed.  Excess emissions resulting from startup, shutdown, and documented malfunctions shall be permitted, provided that operators employ the best operational practices to minimize the amount and duration of emissions during such incidents.  For the CTG/HRSG system, excess NOX and CO emissions resulting from startup, shutdown, or documented malfunctions shall not exceed two hours in any 24-hour period except for the following specific cases.  A “documented malfunction” means a malfunction that is documented within one working day of detection by contacting the Compliance Authority by telephone, facsimile transmittal, or electronic mail.

  - CTG/HRSG System Cold Startup.  For cold startup of the CTG/HRSG system, excess NOX and CO emissions from the CTG/HRSG system shall not exceed six hours (up to 360 minutes) during the startup period.  A “cold startup of the CTG/HRSG system” is defined as startup of the combined cycle system following a shutdown of the steam turbine lasting at least 48 hours.

{Permitting Note:  During a cold startup of the steam turbine system, the CTG/HRSG system is brought on line at low load to gradually increase the temperature of the steam turbine generator (STG) and prevent thermal metal fatigue}

  - CTG/HRSG System Warm Startup.  For warm startup of the CTG/HRSG system, excess NOX and CO emissions shall not exceed four hours (up to 240 minutes) during the startup period.  A “warm startup of the CTG/HRSG system” is defined as a startup of the combined cycle system following a shutdown of the steam turbine lasting at least 8 hours and less than 48 hours.

  - CTG/HRSG System Hot Startup.  For hot startup of the CTG/HRSG system, excess NOX and CO emissions shall not exceed 2 hours (up to 120 minutes) during the startup period.  A “hot startup of the CTG/HRSG system” is defined as a startup of the combined cycle system following a shutdown of the steam turbine for 8 hours or less.

  - Documented Malfunctions During Startup Periods.  In the event that a documented malfunction occurs during a startup period, the excess emissions period for the startup may be extended for up to 2 additional hours (as provided above) for purposes of resolving the malfunction, as long as the excess emissions period due to a malfunction has not been previously consumed during the current 24-hour period.

e.	Shutdown.  For shutdown of the combined cycle operation, excess NOX and CO emissions from the CTG/HRSG system shall not exceed three hours (up to 180 minutes) during the shutdown period.

f.	Fuel Switching.  Excess NOX and CO emissions due to oil-to-gas or gas-to-oil fuel switching shall not exceed 2 hours (up to 120 minutes) each, respectively, in a 24-hour block period.

[Permit Nos. 0950137-020-AC/PSD-FL-373A, Specific Condition A.18. and 0950137-036-AC (PSD-FL-395A, PSD-FL-373B), Specific Condition B.3.]

- Ammonia Injection.  Ammonia injection shall begin as soon as operation of the CTG/HRSG SCR emission control system achieves the operating parameters specified by the SCR manufacturer.  As authorized by Rule 62-210.700(5), F.A.C., the above condition allows excess emissions only for specifically defined periods of startup, shutdown, fuel switching, and documented malfunction of the CTG/HRSG system including the pollution control equipment.  [Rules 62-212.400(BACT) and 62-210.700, F.A.C.; and, Permit Nos. 0950137-020-AC/PSD-FL-373A, Specific Condition A.19. and 0950137-036-AC (PSD-FL-395A, PSD-FL-373B), Specific Condition B.4.]

- DLN Tuning.  CEMS data collected during major DLN or wet injection tuning sessions shall be excluded from the CEMS compliance demonstration provided the tuning session is performed in accordance with the manufacturer’s specifications.  A “major tuning session” would occur after a combustor change-out, a major repair or maintenance to a combustor, as required to maintain compliance, or other circumstances identified or requested by the equipment vendor.  Prior to performing any major tuning session, the permittee shall provide the Compliance Authority with an advance notice of at least 14 days that details the activity and proposed tuning schedule.  The notice may be by telephone, facsimile transmittal, or electronic mail.  [Rule 62-4.070(3), F.A.C.; and, Permit Nos. 0950137-020-AC/PSD-FL-373A, Specific Condition A.20. and 0950137-036-AC (PSD-FL-395A, PSD-FL-373B), Specific Condition B.5.]

Emissions Performance Testing

- Test Methods.  Required tests shall be performed in accordance with the following reference methods.

| Method | Description of Method and Comments |
| --- | --- |
| CTM-027 or 320 | Procedure for Collection and Analysis of Ammonia in Stationary Source. This is an EPA conditional test method. The minimum detection limit shall be 1 ppm. Measurement of Vapor Phase Organic and Inorganic Emissions by Extractive Fourier Transform Infrared (FTIR) Spectroscopy |
| 7E | Determination of Nitrogen Oxide Emissions from Stationary Sources |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |
| 10 | Determination of Carbon Monoxide Emissions from Stationary Sources. The method shall be based on a continuous sampling train. The ascarite trap may be omitted or the interference trap of section 10.1 may be used in lieu of the silica gel and ascarite traps. |
| 20 | Determination of Nitrogen Oxides, Sulfur Dioxide and Diluent Emissions from Stationary Gas Turbines |

No other methods may be used for compliance testing unless prior written approval is received from the administrator of the Department’s Emissions Monitoring Section in accordance with an alternate sampling procedure pursuant to 62-297.620, F.A.C.  [Rules 62-204.800 and 62-297.100, F.A.C.; 40 CFR 60, Appendix A; and, Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.21]

- Subsequent Compliance Test Determinations After Major Replacement or Major Repair.  The Department may, for good reason, require the permittee to conduct additional stack tests after major replacement or major repair of any air pollution control equipment, such as the SCR catalyst, oxidation catalyst, DLN combustors, etc.  When requested, the CTG shall be stack tested to demonstrate compliance with the emission standards for CO, NOX, visible emissions, and ammonia slip.  The tests shall be conducted within 60 days after bringing the unit back on-line.  The unit shall be tested when firing natural gas, when using the duct burners, and when firing ULSD fuel oil.  For each run during tests for visible emissions and ammonia slip, emissions of CO and NOX recorded by the CEMS shall also be reported.  NOX and CO emissions data collected during the required continuous monitor Relative Accuracy Test Audits (RATAs) may be used to demonstrate initial compliance with the CO and NOX standards.  With appropriate flow measurements (or fuel measurements and approved F-factors), CEMS data may be used to demonstrate compliance with the CO and NOX mass rate emissions standards.  [Rule 62-297.310(7)(a)1, F.A.C.; 40 CFR 60.8.; and, Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.22]

- Annual Compliance Tests.  During each federal fiscal year (October 1st, to September 30th) in which the combustion turbine unit operates for more than 400 hours, the CTG shall be tested to demonstrate compliance with the emission standard for visible emissions.  NOX and CO emissions data collected during the required continuous monitor Relative Accuracy Test Audits (RATAs) may be used to demonstrate compliance with the CO and NOX standards.  CO emissions recorded by the CEMS shall be reported for the visible emissions observation period.  If normal operation on fuel oil is less than 400 hours per calendar year, then annual compliance testing on fuel oil is not required for that year.  [Rules 62-212.400 (BACT) and 62-297.310(7)(a)(4) & (8), F.A.C.; and, Permit Nos. 0950137-020-AC/PSD-FL-373A, Specific Condition A.23. and 0950137-036-AC (PSD-FL-395A, PSD-FL-373B), Specific Condition B.6.; and 0950137-043-AC, Specific Condition 5.]

F.23.a.  Compliance Tests Prior to Renewal.  At permit renewal a stack emission test for nitrogen oxides and ammonia slip from the CT/HRSG pair shall be simultaneously conducted while operating in the power augmentation mode with the duct burner and operating on the primary fuel.  The RATA for NOX may be used in lieu of stack testing.  The ammonia injection rate necessary to comply with the NOX standard shall be established and reported during each performance test.  The test shall occur prior to obtaining a renewed operating permit to demonstrate compliance with the ammonia limit specified in Specific Condition F.13.  [0950137-043-AC, Specific Condition 5.]

- Continuous Compliance.  The permittee shall demonstrate continuous compliance with the 24-hour and 12-month average CO emissions standards, and with the 24-hour average NOX emission standard based on data collected by the certified CEMS.  Within 45 days of conducting any Relative Accuracy Test Assessments (RATA) on a CEMS, the permittee shall submit a report to the Compliance Authority summarizing results of the RATA.  Compliance with the CO emission standards also serves as an indicator of efficient fuel combustion, which reduces emissions of particulate matter.  See Appendix CEMS for additional requirements.  [Rule 62-212.400 (BACT), F.A.C.; and, Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.24]

- Compliance for SAM, SO2 and PM/PM10/PM2.5.  In stack compliance testing is not required for SAM, SO2 and PM/PM10/PM2.5.  Compliance with the limits and control requirements for SAM, SO2 and PM/PM10/PM2.5 is based on the recordkeeping required in Specific Condition F.30 and F.31, visible emissions testing and CO continuous monitoring.  [Rule 62-212.400 (BACT), F.A.C.; and, Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.25]

Continuous Monitoring Requirements

- CEM Systems.  The permittee shall calibrate, maintain, and operate CEMS to measure and record the emissions of CO and NOX from the combined cycle gas turbine in a manner sufficient to demonstrate continuous compliance with the CEMS emission standards of this section.  Within one working day of discovering emissions in excess of a CO or NOX standard (and subject to the specified averaging period), the permittee shall notify the Compliance Authority.

- CO Monitor.  The CO monitor shall be properly operated and maintained in order to retain the certification pursuant to 40 CFR 60, Appendix B, Performance Specification 4 or 4A.  Quality assurance procedures shall conform to the requirements of 40 CFR 60, Appendix F, and the Data Assessment Report of Section 7 shall be made each calendar quarter, and reported semiannually to the Compliance Authority.  The RATA tests required for the CO monitor shall be performed using EPA Method 10 in Appendix A of 40 CFR 60 and shall be based on a continuous sampling train.  The CO monitor span values shall be set appropriately, considering the allowable methods of operation and corresponding emission standards.

- NOX Monitor.  The NOX monitor shall be certified, operated, and maintained in accordance with the requirements of 40 CFR 75.  Record keeping and reporting shall be conducted pursuant to Subparts F and G in 40 CFR 75.  The RATA tests required for the NOX monitor shall be performed using EPA Method 20 or 7E in Appendix A of 40 CFR 60.

- Diluent Monitor.  The oxygen (O2) or carbon dioxide (CO2) content of the flue gas shall be monitored at the location where CO and NOX are monitored to correct the measured emissions rates to 15% oxygen.  If a CO2 monitor is installed, the oxygen content of the flue gas shall be calculated using F-factors that are appropriate for the fuel fired.  Each monitor shall comply with the performance and quality assurance requirements of 40 CFR 75.

[Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.26. and 62-213.440(1), F.A.C.]

- CEMS Data Requirements.

  - Data Collection.  Emissions shall be monitored and recorded at all times including startup, operation, shutdown, and malfunction except for continuous monitoring system breakdowns, repairs, calibration checks, and zero and span adjustments.  The CEMS shall be designed and operated to sample, analyze, and record data evenly spaced over an hour.  If the CEMS measures concentration on a wet basis, the CEM system shall include provisions to determine the moisture content of the exhaust gas and an algorithm to enable correction of the monitoring results to a dry basis (0% moisture).  Alternatively, the owner or operator may develop through manual stack test measurements a curve of moisture contents in the exhaust gas versus load for each allowable fuel, and use these typical values in an algorithm to enable correction of the monitoring results to a dry basis (0% moisture).  Final results of the CEMS shall be expressed as ppmvd corrected to 15% oxygen.  The CEMS shall be used to demonstrate compliance with the CEMS emission standards for CO and NOX as specified in this permit.  For purposes of determining compliance with the CEMS emissions standards of this permit, missing (or excluded) data shall not be substituted.

  - Valid Hour.  Hourly average values shall begin at the top of each hour.  Each hourly average value shall be computed using at least one data point in each fifteen-minute quadrant of an hour, where the unit combusted fuel during that quadrant of an hour.  Notwithstanding this requirement, an hourly value shall be computed from at least two data points separated by a minimum of 15 minutes (where the unit operates for more than one quadrant of an hour).  If less than two such data points are available, the hourly average value is not valid.  An hour in which any oil is fired is attributed towards compliance with the permit standards for oil firing.  An hour in which power augmentation is utilized is attributed towards compliance with the permit standards for power augmentation.  The permittee shall use all valid measurements or data points collected during an hour to calculate the hourly average values.

  - 24-hour Block Averages.  A 24-hour block shall begin at midnight of each operating day and shall be calculated from 24 consecutive hourly average emission rate values.  If a unit operates less than 24 hours during the block, the 24-hour block average shall be the average of all available valid hourly average emission rate values for the 24-hour block.  For the CEMS compliance demonstration, hourly average emission rates calculated during episodes of startup, shutdown, malfunction, DLN tuning, or fuel switching subject to the provisions of Conditions 19 and 20 of this section will exclude the one-minute average data corresponding to emissions in excess of the emissions limiting standards during these episodes.  For purposes of determining compliance with the 24-hour CEMS standards, the missing data substitution methodology of 40 CFR Part 75, Subpart D, shall not be utilized.  Instead, the 24-hour block average shall be determined using the remaining hourly data in the 24-hour block.

{Permitting Note:  There may be more than one 24-hour compliance demonstration required for CO and NOX emissions depending on the use of alternate methods of operation}

  - 12-month Rolling Averages.  Compliance with the long-term emission limit for CO shall be based on a 12-month rolling average.  Each 12-month rolling average shall be the arithmetic average of all valid hourly averages collected during the current calendar month and the previous 11 calendar months.

  - Data Exclusion.  Each CEMS shall monitor and record emissions during all operations including episodes of startup, shutdown, malfunction, fuel switches and DLN tuning.  Some of the one minute average CEMS emissions data recorded during these episodes may be excluded from the corresponding CEMS compliance demonstration subject to the provisions of Conditions 18 and 20 of this section.  All periods of one minute average data excluded shall be consecutive for each such episode and only data obtained during the described episodes (startup, shutdown, malfunction, fuel switches, DLN tuning) may be used for the appropriate exclusion periods.  The permittee shall minimize the duration of data excluded for such episodes to the extent practicable.  Data recorded during such episodes shall not be excluded if the episode was caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure, which may reasonably be prevented.  Best operational practices shall be used to minimize hourly emissions that occur during such episodes.  Emissions of any quantity or duration that occur entirely or in part from poor maintenance, poor operation, or any other equipment or process failure, which may reasonably be prevented, shall be prohibited.

  - Availability.  Monitor availability for the CEMS shall be 95% or greater in any calendar quarter.  The quarterly excess emissions report shall be used to demonstrate monitor availability.  In the event 95% availability is not achieved, the permittee shall provide the Department with a report identifying the problems in achieving 95% availability and a plan of corrective actions that will be taken to achieve 95% availability.  The permittee shall implement the reported corrective actions within the next calendar quarter.  Failure to take corrective actions or continued failure to achieve the minimum monitor availability shall be violations of this permit, except as otherwise authorized by the Department’s Compliance Authority.

[Rules 62-4.070(3) and 62-212.400(BACT), F.A.C.; and, Permit Nos. 0950137-020-AC/PSD-FL-373A, Specific Condition A.27. and 0950137-036-AC (PSD-FL-395A, PSD-FL-373B), Specific Condition B.7.]

- Ammonia Monitoring Requirements.  In accordance with the manufacturer’s specifications, the permittee shall calibrate, operate and maintain an ammonia flow meter to measure and record the ammonia injection rate to the SCR system prior to the initial compliance tests.  The permittee shall document and periodically update the general range of ammonia flow rates required to meet permitted emissions levels over the range of load conditions allowed by this permit by comparing NOX emissions recorded by the CEM system with ammonia flow rates recorded using the ammonia flow meter.  During NOX monitor downtimes or malfunctions, the permittee shall operate at the ammonia flow rate and, as applicable for fuel oil firing, the water-to-fuel ratio, that is consistent with the documented flow rate for the combustion turbine load condition.  [Rules 62-4.070(3) and 62-212.400(BACT), F.A.C.; and, Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.28]

Records and Reports

- Monitoring of Capacity.  The permittee shall monitor and record the operating rate (in units of MMBtu/hr) of the CTG and HRSG DB system on a daily average basis, considering the number of hours of operation during each day (including the times of startup, shutdown, malfunction, and fuel switching).  Such monitoring shall be made using a monitoring component of the CEM system required above, or by monitoring daily rates of consumption and heat content of each allowable fuel in accordance with the provisions of 40 CFR 75 Appendix D.  [Rules 62-4.070(3) and 62-212.400(BACT), F.A.C.; and, Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.29]

- Monthly Operations Summary.  By the fifth calendar day of each month, the permittee shall record the following for each fuel in a written or electronic log for the gas turbine for the previous month of operation:  fuel consumption, hours of operation, hours of duct firing, and the updated 12-month rolling totals for each.  Information recorded and stored as an electronic file shall be available for inspection and printing within at least three days of a request by the Department.  The fuel consumption shall be monitored in accordance with the provisions of 40 CFR 75 Appendix D.  [Rules 62-4.070(3) and 62-212.400(BACT), F.A.C.; and, Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.30]

- Fuel Sulfur Records.  The permittee shall demonstrate compliance with the fuel sulfur limits specified in this permit by maintaining the following records of the sulfur contents.

- Natural Gas.  Compliance with the fuel sulfur limit for natural gas shall be demonstrated by keeping reports obtained from the vendor indicating the average sulfur content of the natural gas being supplied from the pipeline for each month of operation.  Methods for determining the sulfur content of the natural gas shall be ASTM methods D4084-82, D4468-85, D5504-01, D6228-98 and D6667-01, D3246-81 or more recent versions.

- ULSD Fuel Oil.  Compliance with the ULSD fuel oil sulfur limit shall be demonstrated by sampling and analysis of the fuel by the permittee or vendor for sulfur, and reporting the results to the Compliance Authority before initial startup.  Sampling the fuel oil sulfur content shall be conducted in accordance with ASTM D4057-88, Standard Practice for Manual Sampling of Petroleum and Petroleum Products, and one of the following test methods for sulfur in petroleum products:  ASTM methods D5453-00, D129-91, D1552-90, D2622-94, or D4294-90.  More recent versions of these methods may be used.  For each fuel delivery, the permittee shall maintain a permanent file of the certified fuel sulfur analysis from the fuel vendor, or from an analysis conducted by the permittee, in accordance with the above methods.  At the request of a Compliance Authority, the permittee shall perform additional sampling and analysis for the fuel sulfur content.

The above methods shall be used to determine the fuel sulfur content in conjunction with the provisions of 40 CFR 75 Appendix D.  [Rules 62-4.070(3) and 62-4.160(15), F.A.C.; and, Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.31]

- Emissions Performance Test Reports.  A report indicating the results of any required emissions performance test shall be submitted to the Compliance Authority no later than 45 days after completion of the last test run.  The test report shall provide sufficient detail on the tested emission unit and the procedures used to allow the Department to determine if the test was properly conducted and if the test results were properly computed.  At a minimum, the test report shall provide the applicable information listed in Rule 62-297.310(8)(c), F.A.C. and in Appendix SC of this permit.  [Rule 62-297.310(8), F.A.C.; and, Permit No. 0950137-020-AC/PSD-FL-373A ,Specific Condition A.32].

- Excess Emissions Reporting.

- Malfunction Notification.  If emissions in excess of a standard (subject to the specified averaging period) occur due to malfunction, the permittee shall notify the Compliance Authority within (1) working day of:  the nature, extent, and duration of the excess emissions; the cause of the excess emissions; and the actions taken to correct the problem.  In addition, the Department may request a written summary report of the incident.

- SIP Quarterly Permit Limits Excess Emissions Report:  Within 30 days following the end of each calendar-quarter, the permittee shall submit a report to the Compliance Authority summarizing periods of CO and NOX emissions in excess of the BACT permit standards following the NSPS format in 40 CFR 60.7(c), Subpart A.  Excess emissions that occur during periods of startup, shutdown, malfunction, fuel switching and DLN tuning shall be monitored, recorded and reported as excess emissions when emission levels exceed the standards specified in this permit for those hourly periods during which they occur and not for the entire averaging period.  These hourly excess emissions periods shall then be excluded from the block averages calculated to demonstrate compliance with the emissions limits specified within this permit.  The duration of excess emissions shall be the duration of the periods of data excluded for such episodes.  In addition, the report shall summarize the CEMS systems monitor availability for the previous quarter.

- NSPS Semi-Annual Excess Emissions Reports.  Within thirty (30) days following each calendar semi-annual period, the permittee shall submit a report on any periods of excess emissions that occurred during the previous semi-annual period to the Compliance Authority.

{Note:  If there are no periods of excess emissions as defined in NSPS Subpart KKKK, a statement to that effect may be submitted with the SIP Quarterly Report to suffice for the NSPS Semi-Annual Report.}

[Rules 62-4.130, 62-204.800, 62-210.700(6), F.A.C.; 40 CFR 60.7 and 60.332(j)(1); and, Permit Nos. 0950137-020-AC/PSD-FL-373A, Specific Condition A.33. and 0950137-036-AC (PSD-FL-395A, PSD-FL-373B), Specific Condition B.8.]

- Annual Operating Report.  The permittee shall submit an annual report that summarizes the actual operating hours and emissions from this facility.  The permittee shall also keep records sufficient to determine the annual throughput of distillate fuel oil for the fuel oil storage tank for use in the Annual Operating Report.  Annual operating reports shall be submitted to the Compliance Authority by April 1st of each year.  [Rule 62-210.370(2), F.A.C.; and, Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition A.34]

This section of the permit addresses the following new emissions unit.

| ID | Emission Unit Description |
| --- | --- |
| 038 | Cooling Tower – consisting of six cells with six individual exhaust fans |

This emissions unit is a six-cell mechanical draft cooling tower, equipped with drift eliminators, that serves Unit B.  This unit commenced operation on October 27, 2009.

{Permitting Note:  This emissions unit was reviewed under the rules for the Prevention of Significant Deterioration (PSD), Rule 62-212.400, F.A.C.  This unit is regulated under Rule 62-04.070 (3), and Rule 62-212.400, F.A.C.}

Equipment

- Cooling Tower.  The permittee is authorized to operate a 6-cell wet evaporative mechanical draft cooling tower with the following nominal design characteristics:  a circulating water flow rate of 56,000 gallons per minute; drift eliminators; and a drift rate of no more than 0.0005 percent of the circulating water flow.  [Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition B.1]

Emissions and Performance Requirements

- Drift Rate.  Within 60 days of commencing commercial operation, the permittee shall certify that the cooling tower was constructed to achieve the specified drift rate of no more than 0.0005 percent of the circulating water flow rate.  [Rule 62-212.400(BACT), F.A.C.; and, Permit No. 0950137-020-AC/PSD-FL-373A, Specific Condition B.2]

{Permitting Note:  This work practice standard is established as BACT for PM/PM10/PM2.5 emissions from the cooling tower.  Based on this design criteria, potential emissions are expected to be less than 3 tons of PM per year and less than 2 tons of PM10 per year.  Actual emissions are expected to be lower than these rates.}

| 024 | 3,740 BHP Emergency Generator |
| --- | --- |

The specific conditions in this section apply to the following emissions units:

| E.U. ID No. | Brief Description |
| --- | --- |
| 024 | 3740 HP Stationary Reciprocating Internal Combustion Engine (RICE) |

This emissions unit consists of a diesel fuel-fired emergency generator.  This emissions unit commenced operation in 1987.  It has 16 cylinders.

The following table provides important details for this emissions unit:

| E.U. ID No. | Engine Brake HP | Date of Construction | Model Year | Primary Fuel | Type of Engine | Displacement liters/cylinder(l/c) | Serial # | Date of last Modification or Reconstruction. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 024 | 3740 | 1987 | 1987 | Diesel | Emergency | 10.57 | Unknown | N/A |

{Permitting Note:  This compression ignition (CI) engine is regulated under 40 CFR 63, Subpart ZZZZ, NESHAP for Stationary RICE adopted in Rule 62.204.800(11)(b), F.A.C.  This RICE is not used for fire pumps.  This permit section addresses an “existing” stationary CI RICE greater than 500 HP that is located at a major source of HAP and that has not been modified or reconstructed after 6/12/2006.  Unless the RICE is modified or reconstructed after 7/11/2005, NSPS 40 CFR 60, Subpart IIII, will not apply.}

Essential Potential to Emit (PTE) Parameters

- Fuel Requirements.  Beginning January 1, 2015, the permittee shall use diesel fuel that meets the requirements in 40 CFR 80.510(b) for nonroad diesel fuel, except that any existing diesel fuel purchased (or otherwise obtained) prior to January 1, 2015, may be used until depleted.  [40 CFR 63.6604]

- General Requirements.  The permittee shall be in compliance with the emission limitations, operating limitations, and other requirements in 40 CFR 63, Subpart ZZZZ that apply at all times.

At all times the permittee shall operate and maintain the emissions unit, including associated air pollution control equipment and monitoring equipment, in a manner consistent with safety and good air pollution control practices for minimizing emissions. The general duty to minimize emissions does not require the permittee to make any further efforts to reduce emissions if levels required by this standard have been achieved. Determination of whether such operation and maintenance procedures are being used will be based on information available to the Department which may include, but is not limited to, monitoring results, review of operation and maintenance procedures, review of operation and maintenance records, and inspection of the source. [40 CFR 63.6605]

Monitoring Requirements

- Continuous Compliance.  The permittee shall operate the emergency stationary RICE according to the requirements in paragraphs (1) through (4) of this specific condition.  In order for the engine to be considered an emergency stationary RICE under 40 CFR 63 Subpart ZZZZ, any operation other than emergency operation, maintenance and testing, emergency demand response, and operation in non-emergency situations for 50 hours per year, as described in paragraphs (1) through (4) of this specific condition, is prohibited.  If the permittee does not operate the engine according to the requirements in paragraphs (1) through (4) of this specific condition, the engine will not be considered an emergency engine under this subpart and must meet all requirements for non-emergency engines.

(1) There is no time limit on the use of emergency stationary RICE in emergency situations.

(2) The permittee may operate the emergency stationary RICE for any combination of the purposes specified in paragraphs (2)(i) through (iii) of this specific condition for a maximum of 100 hours per calendar year.  Any operation for non-emergency situations as allowed by paragraphs (f)(3) and (4) of this section counts as part of the 100 hours per calendar year allowed by this paragraph (2).

(i) Emergency stationary RICE may be operated for maintenance checks and readiness testing, provided that the tests are recommended by federal, state or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine. The owner or operator may petition the Department for approval of additional hours to be used for maintenance checks and readiness testing, but a petition is not required if the owner or operator maintains records indicating that federal, state, or local standards require maintenance and testing of emergency RICE beyond 100 hours per calendar year.

(ii) Emergency stationary RICE may be operated for emergency demand response for periods in which the Reliability Coordinator under the North American Electric Reliability Corporation (NERC) Reliability Standard EOP-002-3, Capacity and Energy Emergencies (incorporated by reference, see 40 CFR 63.14), or other authorized entity as determined by the Reliability Coordinator, has declared an Energy Emergency Alert Level 2 as defined in the NERC Reliability Standard EOP-002-3.

(iii) Emergency stationary RICE may be operated for periods where there is a deviation of voltage or frequency of 5 percent or greater below standard voltage or frequency.

(3) Emergency stationary RICE located at major sources of HAP may be operated for up to 50 hours per calendar year in non-emergency situations.  The 50 hours of operation in non-emergency situations are counted as part of the 100 hours per calendar year for maintenance and testing and emergency demand response provided in paragraph (f)(2) of this specific condition.  The 50 hours per year for non-emergency situations cannot be used for peak shaving or non-emergency demand response, or to generate income for a facility to supply power to an electric grid or otherwise supply power as part of a financial arrangement with another entity.

[40 CFR 63.6640(f)]

Records and Reports

- Reporting.  If the permittee owns or operates an emergency stationary RICE with a site rating of more than 100 brake HP that operates or is contractually obligated to be available for more than 15 hours per calendar year for the purposes specified in Specific ConditionI.I.3.(2)(ii) and (iii), the permittee shall submit an annual report according to the requirements in paragraphs (1) through (3) of this specific condition.

(1) The report must contain the following information:

(i) Company name and address where the engine is located.

(ii) Date of the report and beginning and ending dates of the reporting period.

(iii) Engine site rating and model year.

(iv) Latitude and longitude of the engine in decimal degrees reported to the fifth decimal place.

(v) Hours operated for the purposes specified in Specific Condition I.3.(2)(ii) and (iii), including the date, start time, and end time for engine operation for the purposes specified in Specific Condition I.3.(2)(ii) and (iii).

(vi) Number of hours the engine is contractually obligated to be available for the purposes specified in Specific Condition I.3.(2)(ii) and (iii).

(vii) Reserved.

(viii) If there were no deviations from the fuel requirements in Specific Condition I.1. that apply to the engine (if any), a statement that there were no deviations from the fuel requirements during the reporting period.

(ix) If there were deviations from the fuel requirements in Specific Condition I.1. that apply to the engine (if any), information on the number, duration, and cause of deviations, and the corrective action taken.

(2) The first annual report must cover the calendar year 2015 and must be submitted no later than March 31, 2016.  Subsequent annual reports for each calendar year must be submitted no later than March 31 of the following calendar year.

(3) The annual report must be submitted electronically using the subpart specific reporting form in the Compliance and Emissions Data Reporting Interface (CEDRI) that is accessed through EPA's Central Data Exchange (CDX) (www.epa.gov/cdx). However, if the reporting form specific to this subpart is not available in CEDRI at the time that the report is due, the written report must be submitted to the Administrator at the appropriate address listed in 40 CFR 63.13.

## [40 CFR 63.6650(h)]

General Provisions

- 40 CFR 63 Subpart A, General Provisions.  RICE engines shall comply with all applicable requirements of 40 CFR 63 Subpart A, General Provisions, which have been adopted by reference in Rule 62-204.800(11)(d)1., F.A.C., except that the Secretary is not the Administrator for purposes of 40 CFR 63.5(e), 40 CFR 63.5(f), 40 CFR 63.6(g), 40 CFR 63.6(h)(9), 40 CFR 63.6(j), 40 CFR 63.13, and 40 CFR 63.14.  This engine shall comply with the applicable portions of Appendix NESHAP, Subpart A, General Provisions, included with this permit, as specified below:

| General Provisions Citation | Subject of Citation |
| --- | --- |
| §63.1 | General applicability of the General Provisions |
| §63.2 | Definitions |
| §63.3 | Units and abbreviations |
| §63.4 | Prohibited activities and circumvention |
| §63.5 | Construction and reconstruction |
| §63.6(a) | Applicability |
| §63.6(c)(1)–(2) | Compliance dates for existing sources |
| §63.9(i) | Adjustment of submittal deadlines |
| §63.9(j) | Change in previous information |
| §63.10(a) | Administrative provisions for recordkeeping/reporting |
| §63.10(b)(1) | Record retention |
| §63.10(b)(2)(vi)–(xi) | Records |
| §63.10(b)(2)(xii) | Record when under waiver |
| §63.10(b)(2)(xiv) | Records of supporting documentation |
| §63.10(b)(3) | Records of applicability determination |
| §63.10(d)(1) | General reporting requirements |
| §63.10(d)(4) | Progress Reports |
| §63.10(f) | Waiver for recordkeeping/reporting |
| §63.12 | State authority and delegations |
| §63.13 | Addresses |
| 63.15 | Availability of information |

[40 CFR 63.6665 & Rule 62-204.800(11)(d)1., F.A.C.]

The specific conditions in this section apply to the following emissions unit:

| ID No. | Emission Unit Description |
| --- | --- |
| 041 | One 563 kW Diesel Engine-Driven Emergency Engine |

This unit is an emergency diesel engine generator at Stanton A.  This engine fires ultra-low sulfur diesel fuel.

The following table provides important details for this engine.

| Engine Identification | Engine Brake HP | Date of Manufacture | Model Year | Displacement liters/cylinder (l/c) | Engine Manufacturer | Model No. |
| --- | --- | --- | --- | --- | --- | --- |
| Emergency Diesel Engine | 760 | 2009 | 2008 | 14.9 l total 2.28 l/c | Cummins, Inc. | QXS15-G9 Nonroad 2 |

{Permitting Notes:  This compression ignition reciprocating internal combustion engine (CI RICE) is regulated under 40 CFR 63, Subpart ZZZZ, NESHAP for Stationary RICE and 40 CFR 60, Subpart IIII, NSPS for Stationary Compression Ignition RICE, adopted in Rules 62.204.800(11)(b) & (8)(b), F.A.C., respectively.  This is a “new” stationary emergency CI RICE with a displacement of less than 10 liters per cylinder, located at a major source of HAP, that commenced construction on or after 6/12/2006, and that has a post-2007 model year.  In accordance with provisions of 40 CFR 63.6590(c)(6), meeting the requirements of 40 CFR 60, Subpart IIII, satisfies compliance with the requirements of Subpart ZZZZ.}

Essential Potential to Emit (PTE) Parameters

- Authorized Fuel.  This Stationary Reciprocating Internal Combustion Engine (RICE) must use diesel fuel that meets the following requirements for non-road diesel fuel:

- Sulfur Content.  The sulfur content shall not exceed = 15 ppm = 0.0015% by weight (ultra-low sulfur) for non-road fuel.

- Cetane and Aromatic.  The fuel must have a minimum cetane index of 40 or must have a maximum aromatic content of 35 volume percent.

- Marking Provisions.  The diesel fuel fired shall be free of marker solvent yellow 124 until November 30, 2014.  After December 1, 2014, there are no requirements or restrictions on the use of marker solvent yellow 124.

- Use of Existing Fuel.  Any existing diesel fuel purchased (or otherwise obtained) prior to October 1, 2010, may be used until depleted.

[40 CFR 60.4207(b), 80.510(c), 80.510(f)(2) & 80.510(f)(7)]

- Restricted Hours of Operation.

- Maintenance and Testing.  This engine is authorized to operate for the purpose of maintenance checks and readiness testing, provided that the tests are recommended by federal, state, or local government, the manufacturer, the vendor, or the insurance company associated with the engine.  Maintenance checks and readiness testing of such units is limited to 100 hours per year.

- Emergency Situations.  There is no time limit on the use of emergency stationary RICE in emergency situations.

- Non-emergency Situations.  This engine may operate up to 50 hours per year in non-emergency situations, but those 50 hours are counted towards the 100 hours per year provided for maintenance and testing.

- Other Situations.  This engine cannot be used for peak shaving or to generate income for a facility to supply power to an electric grid or otherwise supply non-emergency power as part of a financial arrangement with another entity.

[40 CFR 60.4211(f)]

- Operation and Maintenance.  Except as permitted in Specific Condition J.8., the owner or operator must operate and maintain the stationary CI internal combustion engine according to the manufacturer's written instructions or procedures developed by the owner or operator that are approved by the engine manufacturer.  In addition, owners and operators may only change those settings that are permitted by the manufacturer.  These RICE must be maintained and operated to meet the emissions limits in Specific Conditions J.4. - J.6. over the entire life of the engine.  [40 CFR 60.4206, 4211(a)(1), (2) & (3)]

Emissions Standards

- NOX + NMHC Emissions.  Emissions of NOX plus non-methane hydrocarbons shall not exceed 6.4 grams per kilowatt hour (g/kW-hr).  [40 CFR 60.4205(b), 40 CFR 60.4202(a)(2) & 40 CFR 89.112]

- CO Emissions.  Carbon monoxide (CO) emissions shall not exceed 3.5 g/kW-hr.  [40 CFR 60.4205(b), 40 CFR 60.4202(a)(2) & 40 CFR 89.112]

- PM Emissions.  Particulate matter (PM) emissions shall not exceed 0.20 g/kW-hr.  [40 CFR 60.4205(b), 40 CFR 60.4202(a)(2) & 40 CFR 89.112]

Testing and Compliance Requirements

- Engine Certification Requirements.  The owner or operator must comply with the emissions standards specified above by having purchased an engine certified by the manufacturer to meet those limits.  The engine must have been installed and configured according to the manufacturer’s emission-related specifications, except as permitted in Specific Condition J.8.  [40 CFR 60.4211(c)]

- Compliance Requirements Due to Loss of Certification.  If you do not install, configure, operate, and maintain your engine and control device according to the manufacturer's emission-related written instructions, or you change emission-related settings in a way that is not permitted by the manufacturer, you must keep a maintenance plan and records of conducted maintenance and must, to the extent practicable, maintain and operate the engine in a manner consistent with good air pollution control practice for minimizing emissions.  In addition, you must conduct an initial performance test to demonstrate compliance with the applicable emission standards within 1 year of startup, or within 1 year after an engine and control device is no longer installed, configured, operated, and maintained in accordance with the manufacturer's emission-related written instructions, or within 1 year after you change emission-related settings in a way that is not permitted by the manufacturer.  You must conduct subsequent performance testing every 8,760 hours of engine operation or 3 years, whichever comes first, thereafter to demonstrate compliance with the applicable emission standards.

[40 CFR 60.4211(g)(3)]

- Testing Requirements.  In the event performance tests are required pursuant to Specific Condition J.8., the following requirements shall be met:

  - Testing Procedures.  The performance test must be conducted according to the in-use testing procedures in 40 CFR Part 1042, Subpart F.  Link to Subpart F

  - NTE Standards.  Exhaust emissions from these engines must not exceed the not-to-exceed (NTE) numerical requirements, rounded to the same number of decimal places as the applicable standard (STD) in Specific Conditions J.4., J5. and J6., determined from the following equation:

NTE Requirement For Each Pollutant = (1.25) x (STD)  (Eq. 1)

[40 CFR 60.4212(a) & (c)]

- Common Testing Requirements.  Unless otherwise specified and if required, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

Monitoring Requirements

- Hour Meter.  The owner or operator must install a non-resettable hour meter if one is not already installed.  [40 CFR 60.4209(a)]

Records and Reports

- Hours of Operation Records.  The owner or operator must keep records of the operation of the engine in emergency and non-emergency service that are recorded through the non-resettable hour meter.  The owner or operator must record the time of operation of the engine and the reason the engine was in operation during that time.  [40 CFR 60.4214]

- Maintenance Records.  To demonstrate conformance with the manufacturer’s written instructions for maintaining the certified engine and to document when compliance testing must be performed pursuant to Specific Condition J.8., the owner or operator must keep the following records:

a.	Engine manufacturer documentation and certification indicating compliance with the standards.

b.	A copy of the manufacturer’s written instructions for operation and maintenance of the certified engine.

c.	A written maintenance log detailing the date and type of maintenance performed on the engine, as well as any deviations from the manufacturer’s written instructions.

[Rule 62-213.440(1), F.A.C.]

- Testing Notification.  At such time that the requirements of Specific Condition J.8. become applicable, the owner or operator shall notify the compliance authority of the date by which the initial compliance test must be performed.  [Rule 62-213.440(1)]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440(1)(b), F.A.C.]

General Provisions

- 40 CFR 60 Subpart A, General Provisions.  The owner or operator shall comply with the applicable requirements of 40 CFR 60 Subpart A, General Provisions, as specified below.  Link to 40 CFR 60, Subpart A - General Provisions.

| General Provisions Citation | Subject of Citation |
| --- | --- |
| § 60.1 | General applicability of the General Provisions |
| § 60.2 | Definitions (see also § 60.4219) |
| § 60.3 | Units and abbreviations |
| § 60.4 | Address |
| § 60.5 | Determination of construction or modification |
| § 60.6 | Review of plans |
| § 60.9 | Availability of information |
| § 60.10 | State Authority |
| § 60.12 | Circumvention |
| § 60.14 | Modification |
| § 60.15 | Reconstruction |
| § 60.16 | Priority list |
| § 60.17 | Incorporations by reference |
| § 60.19 | General notification and reporting requirements |

[40 CFR 60.4218]

The specific conditions in this section apply to the following emissions unit:

| ID No. | Emission Unit Description |
| --- | --- |
| 044 | Two 1675 HP Emergency Diesel Fire Pumps |

Emissions Unit 044 consists of two diesel engine-driven emergency fire pumps.

The following table provides important details for this engine:

| Engine Identification | Engine Brake HP | Date of Manufacture | Model Year | Displacement liters/cylinder (l/c) | Engine Manufacturer | Model No. |
| --- | --- | --- | --- | --- | --- | --- |
| Emergency Fire Pump | 1675 | 1987 | 1987 | 3.1 | Unknown | Unknown |

{Permitting Notes:  This compression ignition reciprocating internal combustion engine (CI RICE) is regulated under 40 CFR 63, Subpart ZZZZ, National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines (RICE) adopted in Rule 62.204.800(11)(b), F.A.C.  This permit section addresses an “existing” emergency stationary CI RICE fire pump engine greater than 500 HP with a displacement of less than 10 liters per cylinder that is located at a major source of HAPs and has commenced construction before 6/12/2006; and, it has not been modified or reconstructed after this date.

Pursuant to Subpart IIII, NSPS for Stationary Compression Ignition RICE, this is an “existing” emergency engine that commenced construction (ordered) before 7/11/2005 and has not been modified or reconstructed after 7/11/2005.  Therefore, it is not subject to Subpart IIII.

Essential Potential to Emit (PTE) Parameters

- Fuel Requirements.  Beginning January 1, 2015, the permittee shall use diesel fuel that meets the requirements in 40 CFR 80.510(b) for nonroad diesel fuel, except that any existing diesel fuel purchased (or otherwise obtained) prior to January 1, 2015, may be used until depleted.  [40 CFR 63.6604]

- General Requirements.  The permittee shall be in compliance with the emission limitations, operating limitations, and other requirements in 40 CFR 63, Subpart ZZZZ that apply at all times.

At all times the permittee shall operate and maintain the emissions unit, including associated air pollution control equipment and monitoring equipment, in a manner consistent with safety and good air pollution control practices for minimizing emissions. The general duty to minimize emissions does not require the permittee to make any further efforts to reduce emissions if levels required by this standard have been achieved. Determination of whether such operation and maintenance procedures are being used will be based on information available to the Department which may include, but is not limited to, monitoring results, review of operation and maintenance procedures, review of operation and maintenance records, and inspection of the source. [40 CFR 63.6605]

Monitoring Requirements

- Continuous Compliance.  The permittee shall operate the emergency stationary RICE according to the requirements in paragraphs (1) through (4) of this specific condition.  In order for the engine to be considered an emergency stationary RICE under 40 CFR 63 Subpart ZZZZ, any operation other than emergency operation, maintenance and testing, emergency demand response, and operation in non-emergency situations for 50 hours per year, as described in paragraphs (1) through (4) of this specific condition, is prohibited.  If the permittee does not operate the engine according to the requirements in paragraphs (1) through (4) of this specific condition, the engine will not be considered an emergency engine under this subpart and must meet all requirements for non-emergency engines.

(1) There is no time limit on the use of emergency stationary RICE in emergency situations.

(2) The permittee may operate the emergency stationary RICE for any combination of the purposes specified in paragraphs (2)(i) through (iii) of this specific condition for a maximum of 100 hours per calendar year.  Any operation for non-emergency situations as allowed by paragraphs (f)(3) and (4) of this section counts as part of the 100 hours per calendar year allowed by this paragraph (2).

(i) Emergency stationary RICE may be operated for maintenance checks and readiness testing, provided that the tests are recommended by federal, state or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine. The owner or operator may petition the Department for approval of additional hours to be used for maintenance checks and readiness testing, but a petition is not required if the owner or operator maintains records indicating that federal, state, or local standards require maintenance and testing of emergency RICE beyond 100 hours per calendar year.

(ii) Emergency stationary RICE may be operated for emergency demand response for periods in which the Reliability Coordinator under the North American Electric Reliability Corporation (NERC) Reliability Standard EOP-002-3, Capacity and Energy Emergencies (incorporated by reference, see 40 CFR 63.14), or other authorized entity as determined by the Reliability Coordinator, has declared an Energy Emergency Alert Level 2 as defined in the NERC Reliability Standard EOP-002-3.

(iii) Emergency stationary RICE may be operated for periods where there is a deviation of voltage or frequency of 5 percent or greater below standard voltage or frequency.

(3) Emergency stationary RICE located at major sources of HAP may be operated for up to 50 hours per calendar year in non-emergency situations.  The 50 hours of operation in non-emergency situations are counted as part of the 100 hours per calendar year for maintenance and testing and emergency demand response provided in paragraph (f)(2) of this specific condition.  The 50 hours per year for non-emergency situations cannot be used for peak shaving or non-emergency demand response, or to generate income for a facility to supply power to an electric grid or otherwise supply power as part of a financial arrangement with another entity.

[40 CFR 63.6640(f)]

Records and Reports

- Reporting.  If the permittee owns or operates an emergency stationary RICE with a site rating of more than 100 brake HP that operates or is contractually obligated to be available for more than 15 hours per calendar year for the purposes specified in Specific Condition K.3.(2)(ii) and (iii), the permittee shall submit an annual report according to the requirements in paragraphs (1) through (3) of this specific condition.

(1) The report must contain the following information:

(i) Company name and address where the engine is located.

(ii) Date of the report and beginning and ending dates of the reporting period.

(iii) Engine site rating and model year.

(iv) Latitude and longitude of the engine in decimal degrees reported to the fifth decimal place.

(v) Hours operated for the purposes specified in Specific Condition K.3.(2)(ii) and (iii), including the date, start time, and end time for engine operation for the purposes specified in Specific Condition I.3.(2)(ii) and (iii).

(vi) Number of hours the engine is contractually obligated to be available for the purposes specified in Specific Condition K.3.(2)(ii) and (iii).

(vii) Reserved.

(viii) If there were no deviations from the fuel requirements in Specific Condition K.1. that apply to the engine (if any), a statement that there were no deviations from the fuel requirements during the reporting period.

(ix) If there were deviations from the fuel requirements in Specific Condition K.1. that apply to the engine (if any), information on the number, duration, and cause of deviations, and the corrective action taken.

(2) The first annual report must cover the calendar year 2015 and must be submitted no later than March 31, 2016.  Subsequent annual reports for each calendar year must be submitted no later than March 31 of the following calendar year.

(3) The annual report must be submitted electronically using the subpart specific reporting form in the Compliance and Emissions Data Reporting Interface (CEDRI) that is accessed through EPA's Central Data Exchange (CDX) (www.epa.gov/cdx). However, if the reporting form specific to this subpart is not available in CEDRI at the time that the report is due, the written report must be submitted to the Administrator at the appropriate address listed in 40 CFR 63.13.

## [40 CFR 63.6650(h)]

General Provisions

- 40 CFR 63 Subpart A - General Provisions.  The owner or operator shall comply with the following applicable requirements of 40 CFR 63 Subpart A - General Provisions, which have been adopted by reference in Rule 62-204.800(11)(d)1., F.A.C., except that the Secretary is not the Administrator for purposes of 40 CFR 63.5(e), 40 CFR 63.5(f), 40 CFR 63.6(g), 40 CFR 63.6(h)(9), 40 CFR 63.6(j), 40 CFR 63.13, and 40 CFR 63.14.  Link to 40 CFR 63, Subpart A - General Provisions

| General Provisions Citation | Subject of Citation |
| --- | --- |
| §63.1 | General applicability of the General Provisions |
| §63.2 | Definitions (Additional terms defined in §63.6675) |
| §63.3 | Units and abbreviations |
| §63.4 | Prohibited activities and circumvention |
| §63.5 | Construction and reconstruction |
| §63.6(a) | Applicability |
| §63.9(a) | Applicability and State delegation of notification requirements |
| §63.9(b)(1)–(5) | Initial notifications (Except that §63.9(b)(3) is reserved) |
| §63.9(i) | Adjustment of submittal deadlines |
| §63.9(j) | Change in previous information |
| §63.10(a) | Administrative provisions for recordkeeping/reporting |
| §63.10(b)(1) | Record retention |
| §63.10(b)(2)(vi)–(xi) | Records |
| §63.10(b)(2)(xii) | Record when under waiver |
| §63.10(b)(2)(xiv) | Records of supporting documentation |
| §63.10(b)(3) | Records of applicability determination |
| §63.10(d)(1) | General reporting requirements |
| §63.10(f) | Waiver for recordkeeping/reporting |
| §63.12 | State authority and delegations |
| §63.13 | Addresses |
| §63.14 | Incorporation by reference |
| §63.15 | Availability of information |

[40 CFR 63.6665 & Table 8 to Subpart ZZZZ of Part 63]

The specific conditions in this section apply to the following emissions unit:

| ID No. | Emission Unit Description |
| --- | --- |
| 021 | Surface Coating and Solvent Cleaning |

RACT Requirements

- Cold Cleaning Control Technology.  The permittee shall comply with each of the following requirements:

(a) Equip the cleaner with a cover. The cover shall be so designed that it can be easily operated with one hand if:

1. The solvent volatility is greater than 0.3 pounds per square inch (15 millimeters of mercury or 2 kilopascals) measured at 100 degrees Fahrenheit (38 degrees Celsius);

2. The solvent is agitated;

3. The solvent is heated.

(b) Equip the cleaner with a facility for draining cleaned parts. The drainage facility shall be constructed internally so that parts are enclosed under the cover while draining if the solvent volatility is greater than 0.6 pounds per square inch (31 millimeters of mercury or 4.1 kilopascals) measured at 100 degrees Fahrenheit (38 degrees Celsius), except that the drainage facility may be external for the applications where an internal type cannot fit into the cleaning system.

(c) Install one of the following control devices if the solvent volatility is greater than 0.6 pounds per square inch (31 millimeters of mercury or 4.1 kilopascals) measured at 100 degrees Fahrenheit (38 degrees Celsius), or if the solvent is heated above 120 degrees Fahrenheit (50 degrees Celsius):

1. Freeboard that gives a freeboard ratio greater than or equal to 0.7; or,

2. Water cover (solvent must be insoluble in and heavier than water); or,

3. Other systems of equivalent control such as refrigerated chiller or carbon absorption.

(d) Provided a permanent, conspicuous label summarizing the operating requirements.

(e) Store waste solvent only in covered containers and not dispose of waste solvent or transfer it to another party, such that greater than 20 percent of the waste solvent (by weight) can evaporate into the atmosphere.

(f) Close the cover whenever parts are not being handled in the cleaner.

(g) Drain the cleaned parts for at least 15 seconds or until dripping ceases.

(h) If used, supply a solvent spray that is a solid fluid stream (not a fine, atomized, or shower-type spray) at a pressure which does not cause excessive splashing.

[Rule 62-296.511, F.A.C.]

The emissions units listed below are regulated under Acid Rain, Phase II.

Operated by:  Orlando Utilities Commission

Plant:  Stanton Energy Center

ORIS Code:  0564

| E.U. ID # | EPA ID | Brief Description |
| --- | --- | --- |
| 001 | 1 | Fossil Fuel Fired Steam Generator # 1 |
| 002 | 2 | Fossil Fuel Fired Steam Generator # 2 |
| 037 | B | 300 megawatt (MW) Combined Cycle Combustion Turbine – Stanton Unit B |

Operated by:  Southern Power – Florida, LLC

Plant: Stanton Energy Center

ORIS Code:  55821

| E.U. ID # | EPA ID | Brief Description |
| --- | --- | --- |
| 025 | 25 | Combined-Cycle Combustion Turbine – Stanton Unit A |
| 026 | 26 | Combined-Cycle Combustion Turbine – Stanton Unit A |

A.1.	The Phase II Acid Rain Part application submitted for this facility, as approved by the Department, is a part of this permit.  The owners and operators of these Phase II acid rain units must comply with the standard requirements and special provisions set forth in the application(s) listed below:

a.	DEP Form No. 62-210.900(1)(a), dated 04/29/09, received 05/21/09.

b.	DEP Form No. 62-210.900(1)(a), dated 05/13/09, received 05/21/09.

[Chapter 62-213, F.A.C. and Rule 62-214.320, F.A.C.]

A.2.	Nitrogen oxide (NOX) requirements for each Acid Rain Phase II unit are as follows:

| E.U. ID # | EPA ID | NOX Limit |
| --- | --- | --- |
| 001 | 1 | The Florida Department of Environmental Protection approves a NOX compliance plan for this unit. The compliance plan is effective for calendar year 2010 through calendar year 2014. This unit’s applicable emission limitation for each year of the plan, is 0.46 lb/MMBtu from 40 CFR 76.7(a)(2) for dry bottom wall-fired boilers. In addition to the described NOX compliance plan, this unit shall comply with all other applicable requirements of 40 CFR Part 76, including the duty to reapply for a NOX compliance plan and the requirements covering excess emissions. |
| 002 | 2 | The Florida Department of Environmental Protection approves a NOX compliance plan for this unit. The compliance plan is effective for calendar year 2010 through calendar year 2014. This unit’s applicable emission limitation for each year of the plan, is 0.46 lb/MMBtu from 40 CFR 76.7(a)(2) for dry bottom wall-fired boilers. In addition to the described NOX compliance plan, this unit shall comply with all other applicable requirements of 40 CFR Part 76, including the duty to reapply for a NOX compliance plan and the requirements covering excess emissions. |

A.3.	Sulfur Dioxide (SO2) Emission Allowances.  SO2 emissions from sources subject to the Federal Acid Rain Program (Title IV) shall not exceed any allowances that the source lawfully holds under the Federal Acid Rain Program.  Allowances shall not be used to demonstrate compliance with a non-Title IV applicable requirement of the Act.

a.	No permit revision shall be required for increases in emissions that are authorized by allowances acquired pursuant to the Federal Acid Rain Program, provided that such increases do not require a permit revision pursuant to Rule 62-213.400(3), F.A.C.

b.	No limit shall be placed on the number of allowances held by the source under the Federal Acid Rain Program.

c.	Allowances shall be accounted for under the Federal Acid Rain Program.

[Rule 62-213.440(1)(c)1., 2. & 3., F.A.C.]

A.4.	Comments, notes, and justifications:  None.

Clean Air Interstate Rule (CAIR).

Operated by:  Orlando Utilities Commission

Plant:  Stanton Energy Center

ORIS Code:  0564

The emissions units below are regulated under the Clean Air Interstate Rule.

| E.U. ID # | EPA ID | Brief Description |
| --- | --- | --- |
| 001 | 1 | Fossil Fuel Fired Steam Generator # 1 |
| 002 | 2 | Fossil Fuel Fired Steam Generator # 2 |
| 037 | B | 300 megawatt (MW) Combined Cycle Combustion Turbine – Stanton Unit B |

Operated by:  Southern Power – Florida, LLC

Plant: Stanton Energy Center

ORIS Code:  55821

The emissions units below are regulated under the Clean Air Interstate Rule.

| E.U. ID # | EPA ID | Brief Description |
| --- | --- | --- |
| 025 | 25 | Combined-Cycle Combustion Turbine – Stanton Unit A |
| 026 | 26 | Combined-Cycle Combustion Turbine – Stanton Unit A |

- Clean Air Interstate Rule Application.  The Clean Air Interstate Rule Part Form submitted for this facility is a part of this permit.  The owners and operators of these CAIR units as identified in this form must comply with the standard requirements and special provisions set forth in the CAIR Part Form (DEP Form No. 62-210.900(1)(b)) dated March 16, 2008, which is attached at the end of this section.  [Chapter 62-213, F.A.C. and Rule 62-210.200, F.A.C.]

Operated by:  Southern Power – Florida, LLC

Plant: Stanton Energy Center

ORIS Code:  55821

Description of TR Monitoring Provisions

The TR subject units, and the unit-specific monitoring provisions at this source, are identified in the following table.  These units are subject to the requirements for the TR NOX Ozone Season Trading Program.

| Unit ID: 025 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Parameter | Continuous emission monitoring system or systems (CEMS) requirements pursuant to 40 CFR part 75, subpart B (for SO2 monitoring) and 40 CFR part 75, subpart H (for NOX monitoring) | Excepted monitoring system requirements for gas- and oil-fired units pursuant to 40 CFR part 75, appendix D | Excepted monitoring system requirements for gas- and oil-fired peaking units pursuant to 40 CFR part 75, appendix E | Low Mass Emissions excepted monitoring (LME) requirements for gas- and oil-fired units pursuant to 40 CFR 75.19 | EPA-approved alternative monitoring system requirements pursuant to 40 CFR part 75, subpart E |
| SO2 | No | Yes | No | No | No |
| NOX | Yes | No | No | No | No |
| Heat input | No | Yes | No | No | No |
| Unit ID: 026 |  |  |  |  |  |
| Parameter | Continuous emission monitoring system or systems (CEMS) requirements pursuant to 40 CFR part 75, subpart B (for SO2 monitoring) and 40 CFR part 75, subpart H (for NOX monitoring) | Excepted monitoring system requirements for gas- and oil-fired units pursuant to 40 CFR part 75, appendix D | Excepted monitoring system requirements for gas- and oil-fired peaking units pursuant to 40 CFR part 75, appendix E | Low Mass Emissions excepted monitoring (LME) requirements for gas- and oil-fired units pursuant to 40 CFR 75.19 | EPA-approved alternative monitoring system requirements pursuant to 40 CFR part 75, subpart E |
| SO2 | No | Yes | No | No | No |
| NOX | Yes | No | No | No | No |
| Heat input | No | Yes | No | No | No |

- The above description of the monitoring used by a unit does not change, create an exemption from, or otherwise affect the monitoring, recordkeeping, and reporting requirements applicable to the unit under 40 CFR 97.530 through 97.535 (TR NOX Ozone Season Trading Program).  The monitoring, recordkeeping and reporting requirements applicable to each unit are included below in the standard conditions for the applicable TR trading programs.

- Owners and operators must submit to the Administrator a monitoring plan for each unit in accordance with 40 CFR 75.53, 75.62 and 75.73, as applicable.  The monitoring plan for each unit is available at the EPA’s website at http://www2.epa.gov/airmarkets/monitoring-plans.

- Owners and operators that want to use an alternative monitoring system must submit to the Administrator a petition requesting approval of the alternative monitoring system in accordance with 40 CFR 75, Subpart E, 40 CFR 75.66 and 40 CFR 97.535 (TR NOX Ozone Season Trading Program).  The Administrator’s response approving or disapproving any petition for an alternative monitoring system is available on the EPA’s website at http://www.epa.gov/airmarkets/emissions/petitions.html.  http://www2.epa.gov/airmarkets/part-75-petition-responses.

- Owners and operators that want to use an alternative to any monitoring, recordkeeping, or reporting requirement under 40 CFR 97.530 through 97.534 (TR NOX Ozone Season Trading Program) must submit to the Administrator a petition requesting approval of the alternative in accordance with 40 CFR 75.66 and 40 CFR 97.535 (TR NOX Ozone Season Trading Program).  The Administrator’s response approving or disapproving any petition for an alternative to a monitoring, recordkeeping, or reporting requirement is available on EPA’s website at http://www.epa.gov/airmarkets/emissions/petitions.html.

- The descriptions of monitoring applicable to the units included above meet the requirement of 40 CFR 97.530 through 97.534 (TR NOX Ozone Season Trading Program), and therefore minor permit modification procedures, in accordance with 40 CFR 70.7(e)(2)(i)(B) or 71.7(e)(1)(i)(B), may be used to add to or change this unit’s monitoring system description.

TR NOX Ozone Season Trading Program Requirements (40 CFR 97.506)

- Designated Representative Requirements.  The owners and operators shall comply with the requirement to have a designated representative, and may have an alternate designated representative, in accordance with 40 CFR 97.513 through 97.518.

- Emissions Monitoring, Reporting, and Recordkeeping Requirements.

- The owners and operators, and the designated representative, of each TR NOX Ozone Season source and each TR NOX Ozone Season unit at the source shall comply with the monitoring, reporting, and recordkeeping requirements of 40 CFR 97.530 (general requirements, including installation, certification, and data accounting, compliance deadlines, reporting data, prohibitions, and long-term cold storage), 97.531 (initial monitoring system certification and recertification procedures), 97.532 (monitoring system out-of-control periods), 97.533 (notifications concerning monitoring), 97.534 (recordkeeping and reporting, including monitoring plans, certification applications, quarterly reports, and compliance certification), and 97.535 (petitions for alternatives to monitoring, recordkeeping, or reporting requirements).

- The emissions data determined in accordance with 40 CFR 97.530 through 97.535 shall be used to calculate allocations of TR NOX Ozone Season allowances under 40 CFR 97.511(a)(2) and (b) and 97.512 and to determine compliance with the TR NOX Ozone Season emissions limitation and assurance provisions under Condition 8 below, provided that, for each monitoring location from which mass emissions are reported, the mass emissions amount used in calculating such allocations and determining such compliance shall be the mass emissions amount for the monitoring location determined in accordance with 40 CFR 97.530 through 97.535 and rounded to the nearest ton, with any fraction of a ton less than 0.50 being deemed to be zero.

- NOX Emissions Requirements.

- TR NOX Ozone Season Emissions Limitation.

  - As of the allowance transfer deadline for a control period in a given year, the owners and operators of each TR NOX Ozone Season source and each TR NOX Ozone Season unit at the source shall hold, in the source's compliance account, TR NOX Ozone Season allowances available for deduction for such control period under 40 CFR 97.524(a) in an amount not less than the tons of total NOX emissions for such control period from all TR NOX Ozone Season units at the source.

  - If total NOX emissions during a control period in a given year from the TR NOX Ozone Season units at a TR NOX Ozone Season source are in excess of the TR NOX Ozone Season emissions limitation set forth in paragraph (1) above, then:

    - The owners and operators of the source and each TR NOX Ozone Season unit at the source shall hold the TR NOX Ozone Season allowances required for deduction under 40 CFR 97.524(d); and

    - The owners and operators of the source and each TR NOX Ozone Season unit at the source shall pay any fine, penalty, or assessment or comply with any other remedy imposed, for the same violations, under the Clean Air Act, and each ton of such excess emissions and each day of such control period shall constitute a separate violation of 40 CFR part 97, subpart BBBBB and the Clean Air Act.

- TR NOX Ozone Season Assurance Provisions.

  - If total NOX emissions during a control period in a given year from all TR NOX Ozone Season units at TR NOX Ozone Season sources in the state (and Indian country within the borders of such state) exceed the state assurance level, then the owners and operators of such sources and units in each group of one or more sources and units having a common designated representative for such control period, where the common designated representative’s share of such NOX emissions during such control period exceeds the common designated representative’s assurance level for the state and such control period, shall hold (in the assurance account established for the owners and operators of such group) TR NOX Ozone Season allowances available for deduction for such control period under 40 CFR 97.525(a) in an amount equal to two times the product (rounded to the nearest whole number), as determined by the Administrator in accordance with 40 CFR 97.525(b), of multiplying—

    - The quotient of the amount by which the common designated representative’s share of such NOX emissions exceeds the common designated representative’s assurance level divided by the sum of the amounts, determined for all common designated representatives for such sources and units in the state (and Indian country within the borders of such state) for such control period, by which each common designated representative’s share of such NOX emissions exceeds the respective common designated representative’s assurance level; and

    - The amount by which total NOX emissions from all TR NOX Ozone Season units at TR NOX Ozone Season sources in the state (and Indian country within the borders of such state) for such control period exceed the state assurance level.

  - The owners and operators shall hold the TR NOX Ozone Season allowances required under paragraph (1) above, as of midnight of November 1 (if it is a business day), or midnight of the first business day thereafter (if November 1 is not a business day), immediately after such control period.

  - Total NOX emissions from all TR NOX Ozone Season units at TR NOX Ozone Season sources in the state (and Indian country within the borders of such state) during a control period in a given year exceed the state assurance level if such total NOX emissions exceed the sum, for such control period, of the State NOX Ozone Season trading budget under 40 CFR 97.510(a) and the state’s variability limit under 40 CFR 97.510(b).

  - It shall not be a violation of 40 CFR part 97, subpart BBBBB or of the Clean Air Act if total NOX emissions from all TR NOX Ozone Season units at TR NOX Ozone Season sources in the state (and Indian country within the borders of such State) during a control period exceed the state assurance level or if a common designated representative’s share of total NOX emissions from the TR NOX Ozone Season units at TR NOX Ozone Season sources in the state (and Indian country within the borders of such state) during a control period exceeds the common designated representative’s assurance level.

  - To the extent the owners and operators fail to hold TR NOX Ozone Season allowances for a control period in a given year in accordance with paragraphs (1) through (3) above,

    - The owners and operators shall pay any fine, penalty, or assessment or comply with any other remedy imposed under the Clean Air Act; and

    - Each TR NOX Ozone Season allowance that the owners and operators fail to hold for such control period in accordance with paragraphs (1) through (3) above and each day of such control period shall constitute a separate violation of 40 CFR part 97, subpart BBBBB and the Clean Air Act.

- Compliance Periods.

  - A TR NOX Ozone Season unit shall be subject to the requirements under paragraph (a) above for the control period starting on the later of May 1, 2015 or the deadline for meeting the unit's monitor certification requirements under 40 CFR 97.530(b) and for each control period thereafter.

  - A TR NOX Ozone Season unit shall be subject to the requirements under paragraph (b) above for the control period starting on the later of May 1, 2017 or the deadline for meeting the unit's monitor certification requirements under 40 CFR 97.530(b) and for each control period thereafter.

- Vintage of Allowances Held for Compliance.

  - A TR NOX Ozone Season allowance held for compliance with the requirements under paragraph (a)(1) above for a control period in a given year must be a TR NOX Ozone Season allowance that was allocated for such control period or a control period in a prior year.

  - A TR NOX Ozone Season allowance held for compliance with the requirements under paragraphs a.(2)(a) and b.(1) through (3) above for a control period in a given year must be a TR NOX Ozone Season allowance that was allocated for a control period in a prior year or the control period in the given year or in the immediately following year.

- Allowance Management System Requirements.  Each TR NOX Ozone Season allowance shall be held in, deducted from, or transferred into, out of, or between Allowance Management System accounts in accordance with 40 CFR part 97, subpart BBBBB.

- Limited Authorization.  A TR NOX Ozone Season allowance is a limited authorization to emit one ton of NOX during the control period in one year.  Such authorization is limited in its use and duration as follows:

  - Such authorization shall only be used in accordance with the TR NOX Ozone Season Trading Program; and

  - Notwithstanding any other provision of 40 CFR part 97, subpart BBBBB, the Administrator has the authority to terminate or limit the use and duration of such authorization to the extent the Administrator determines is necessary or appropriate to implement any provision of the Clean Air Act.

- Property Right.  A TR NOX Ozone Season allowance does not constitute a property right.

- Title V Permit Revision Requirements.

- No Title V permit revision shall be required for any allocation, holding, deduction, or transfer of TR NOX Ozone Season allowances in accordance with 40 CFR part 97, subpart BBBBB.

- This permit incorporates the TR emissions monitoring, recordkeeping and reporting requirements pursuant to 40 CFR 97.530 through 97.535, and the requirements for a continuous emission monitoring system (pursuant to 40 CFR part 75, subparts B and H), an excepted monitoring system (pursuant to 40 CFR part 75, appendices D and E), a low mass emissions excepted monitoring methodology (pursuant to 40 CFR 75.19), and an alternative monitoring system (pursuant to 40 CFR part 75, subpart E).  Therefore, the Description of TR Monitoring Provisions table for units identified in this permit may be added to, or changed, in this title V permit using minor permit modification procedures in accordance with 40 CFR 97.506(d)(2) and 70.7(e)(2)(i)(B) or 71.7(e)(1)(i)(B).

- Additional Recordkeeping and Reporting Requirements.

- Unless otherwise provided, the owners and operators of each TR NOX Ozone Season source and each TR NOX Ozone Season unit at the source shall keep on site at the source each of the following documents (in hardcopy or electronic format) for a period of 5 years from the date the document is created.  This period may be extended for cause, at any time before the end of 5 years, in writing by the Administrator.

  - The certificate of representation under 40 CFR 97.516 for the designated representative for the source and each TR NOX Ozone Season unit at the source and all documents that demonstrate the truth of the statements in the certificate of representation; provided that the certificate and documents shall be retained on site at the source beyond such 5-year period until such certificate of representation and documents are superseded because of the submission of a new certificate of representation under 40 CFR 97.516 changing the designated representative.

  - All emissions monitoring information, in accordance with 40 CFR part 97, subpart BBBBB.

  - Copies of all reports, compliance certifications, and other submissions and all records made or required under, or to demonstrate compliance with the requirements of, the TR NOX Ozone Season Trading Program.

- The designated representative of a TR NOX Ozone Season source and each TR NOX Ozone Season unit at the source shall make all submissions required under the TR NOX Ozone Season Trading Program, except as provided in 40 CFR 97.518. This requirement does not change, create an exemption from, or otherwise affect the responsible official submission requirements under a title V operating permit program in 40 CFR parts 70 and 71.

- Liability.

- Any provision of the TR NOX Ozone Season Trading Program that applies to a TR NOX Ozone Season source or the designated representative of a TR NOX Ozone Season source shall also apply to the owners and operators of such source and of the TR NOX Ozone Season units at the source.

- Any provision of the TR NOX Ozone Season Trading Program that applies to a TR NOX Ozone Season unit or the designated representative of a TR NOX Ozone Season unit shall also apply to the owners and operators of such unit.

- Effect on Other Authorities.  No provision of the TR NOX Ozone Season Trading Program or exemption under 40 CFR 97.505 shall be construed as exempting or excluding the owners and operators, and the designated representative, of a TR NOX Ozone Season source or TR NOX Ozone Season unit from compliance with any other provision of the applicable, approved state implementation plan, a federally enforceable permit, or the Clean Air Act.

- Effect on Units in Indian Country.  Notwithstanding the provisions of Conditions 6. through 12. above, Conditions 6. through 12. shall be deemed not to impose any requirements on any source or unit, or any owner, operator, or designated representative with regard to any source or unit, in Indian country within the borders of the state.

Link to 40 CFR 97