Title V Air Operation Permit Revision

Permit No. 0950137-047-AV

Applicant

The applicant for this project is Orlando Utilities Commission.  The applicant’s responsible official and mailing address are:  Benjamin Pynes, Plant Manager, Southern Power, Curtis H. Stanton Energy Center (Stanton Plant), 5100 South Alafaya Trail, Orlando, Florida  32831.

Facility Description

The applicant operates the existing Stanton Plant, which is located in Orange County at 5100 South Alafaya Trail, Orlando, Florida.

Orlando Utilities Commission (OUC) operates the Curtis H. Stanton Energy Center, which is an existing power plant (SIC No. 4911).  The facility site is located 144 km southeast from the Chassahowitzka National Wildlife Area; the nearest Federal Prevention of Significant Deterioration (PSD) Class I Area.  The placard page above indicates the exact geographical coordinates.

This facility consists of two fossil fuel fired steam electric generating stations, emissions unit (E.U.) identification (ID) No. 001 (Unit No. 1) and 002 (Unit No. 2); also, there are storage and handling facilities for solid fuels, fly ash, limestone, gypsum, slag, and bottom ash.  Unit No. 1 consists of a Babcock and Wilcox boiler/steam generator (Model RB 611) and steam turbine, which drives a generator with a nameplate rating of 468 megawatts (MW).  Unit No. 2 consists of a Babcock and Wilcox boiler/steam generator (Model RB 621) and steam turbine, which drives a generator with a nameplate rating of 468 MW.  Each boiler/steam generator is a wall fired dry bottom unit.  Unit Nos. 1 and 2 are fired with coal.  Each unit has their individual stacks.  Particulate matter emissions generated during the operation of the unit are controlled by a dry electrostatic precipitator (ESP) manufactured by Wheelabrator-Frye Inc.  The control efficiency of the ESP is 99.7%.  Units 1 and 2 are each equipped with low NOX burners and overfire air equipment.  The burner design provides accurate fuel-air ratio control and thorough mixing of fuel and air at all ratings.  Unit 2 is also equipped with a selective catalytic reduction (SCR) system for further control of NOX emissions.

Emission Units 001 and 002 are subject to compliance assurance monitoring (CAM) for particulate matter (PM) emissions controlled by an ESP.  Because the continuous opacity monitoring system (COMS) is required to be used at the facility (for Phase II Acid Rain Program purposes), it must also be used as part of the CAM plan.  A CAM plan is included for the ESP.  See Appendix CAM.

Emission Units 025 and 026 (Stanton Unit A) are nominal 170 MW, General Electric “F” Class (PG7241FA) combustion turbine-electrical generators, fired with pipeline natural gas or diesel and equipped with evaporative coolers on the inlet air system, two supplementary fired heat recovery steam generators (HRSG), each with a 160 ft. stack, and one steam turbine-electrical generator rated at approximately 300 MW.  Units 25 and 26 have a total nominal capacity of 640 MW and will achieve approximately 700 MW during extreme winter peaking conditions.

The combustion turbines are equipped with dry low nitrogen oxides (NOX) combustors as well as selective catalytic reduction (SCR) in order to control NOX emissions to 3.5 parts per million by volume dry (ppmvd) at 15% oxygen (O2) while firing natural gas.  During fuel oil firing, emissions shall be held to 10 ppmvd at 15% O2 using SCR plus water injection.  Pipeline quality natural gas, 0.05% sulfur, by weight, fuel oil, and good combustion practices shall be employed to control all pollutants.

These emissions units (the combustion turbines) are not subject to continuous assurance monitoring (CAM) because the NOX continuous emissions monitoring system (CEMS) is used for continuance compliance determination.  Thus no CAM plan is included for these units in this permit.

Emission Unit 037 (Stanton Unit B) consists of:  one nominal 150 megawatts (MW) General Electric 7241 FA combustion turbine-electrical generator (CTG); a supplementary fired heat recovery steam generator (HRSG) with natural gas fueled duct burners; a nominal 150 MW steam turbine generator (STG); and auxiliary equipment.  The unit includes highly automated controls, described as the GE Mark VI Gas Turbine Control System to fulfill all of the gas turbine control requirements.

Unit B is equipped with dry low nitrogen oxides (NOX) combustors as well as selective catalytic reduction (SCR) in order to control NOX emissions to 2 parts per million by volume dry (ppmvd) at 15% oxygen (O2) while firing natural gas.  During fuel oil firing, emissions shall be held to 8 ppmvd at 15% O2 using SCR plus water injection.  Pipeline quality natural gas, 0.0015% sulfur, by weight, fuel oil, and good combustion practices shall be employed to control all pollutants.

Unit B is not subject to continuous assurance monitoring (CAM) because the NOX continuous emissions monitoring system (CEMS) is used for continuance compliance determination.  Thus no CAM plan is included for this unit in this permit.

regulated Emissions Unit IDentification Numbers and descriptions

| EU No. | ## Brief Description |
| --- | --- |
| Regulated Emissions Units |  |
| 001 | Fossil Fuel Fired Steam Electric Generator No. 1 (FFSG 1) |
| 002 | Fossil Fuel Fired Steam Electric Generator No. 2 (FFSG 2) |
| 004 | Coal Transfer Baghouse |
| 005 | Coal Crusher Building Baghouse |
| 006 | Coal Plant Transfer and Silo Fill Area #1 Baghouse |
| 007 | Coal Plant Transfer and Silo Fill Area #2 Baghouse |
| 008 | Limestone Day Bin Baghouse |
| 009 | Pebble Lime Receiving Hopper Baghouse |
| 010 | Coal Reclaim Hopper Baghouse |
| 011 | Flyash Exhauster Filter #1 Baghouse |
| 012 | Flyash Exhauster Filter #2 Baghouse |
| 013 | Flyash Exhauster Filter #3 Baghouse |
| 014 | Flyash Exhauster Filter #4 Baghouse |
| 015 | Flyash Silo Bin Vent Filter Baghouse |
| 016 | Adipic Acid Storage Baghouse |
| 021 | Surface Coating and Solvent Cleaning |
| 024 | 3,740 BHP Emergency Generator |
| 025 | Stanton Unit A- Combined-Cycle Combustion Turbine |
| 026 | Stanton Unit A- Combined-Cycle Combustion Turbine |
| 029 | Flyash Silo Bin Vent Filter Baghouse |
| 037 | Stanton Unit B - 300 MW Combined Cycle Combustion Turbine |
| 038 | Stanton Unit B - Cooling Tower |
| 041 | 563 kW Emergency Generator at the Stanton A Plant Site |
| 044 | Emergency Fire Pump Engines |

Applicable Regulations

Based on the Title V Air Operation Revision application received on April 21, 2016, this facility is a major source of hazardous air pollutants (HAP).  The existing facility is a prevention of significant deterioration (PSD) major source of air pollutants in accordance with Rule 62-212.400, F.A.C.  A summary of applicable regulations is shown in the following table:

| Regulation | ## EU No(s). |
| --- | --- |
| Federal Rule Citations |  |
| 40 CFR 60, Subpart A, NSPS General Provisions | ## 001, 002, 025, 026 |
| 40 CFR 60, Subpart Da, Standards of Performance for Fossil-Fuel Fired Steam Generators | ## 001, 002 |
| NSPS - 40 CFR 60, Subpart GG, Standards of Performance for Stationary Gas Turbines, adopted and incorporated by reference in Rule 62-204.800 | 025, 026 |
| NSPS - 40 CFR 60, Subpart KKKK, Standards of Performance for Stationary Combustion Turbines that Commence Construction after February 18, 2005, adopted and incorporated by reference in Rule 62-204.800 | 037 |
| 40 CFR 60, Subpart Y, Standards of Performance for Coal Preparation Plants | 004 through 016 and 029 |
| 40 CFR 60, Subpart IIII, Standards of Performance for Stationary Compression Ignition Internal Combustion Engines | 041 |
| Federal Acid Rain Program, Phase II | 001, 002, 025, 026 |
| 40 CFR 75 Acid Rain Monitoring Provisions |  |
| 40 CFR 63, Subpart ZZZZ, National Emission Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines (RICE) | 024, 041, 044 |
| 40 CFR 63, Subpart UUUUU, National Emission Standards for Hazardous Air Pollutants: Coal- and Oil-Fired Electric Utility Steam Generating Units | 001, 002 |
| State Rule Citations |  |
| Rule 62-4, F.A.C. (Permitting Requirements) | 001, 002, 004 through 016, 025, 026,and 029 |
| Rule 62-204, F.A.C. (Ambient Air Quality Requirements, PSD Increments, and Federal Regulations Adopted by Reference) |  |
| Rule 62-210, F.A.C. (Permits Required, Public Notice, Reports, Stack Height Policy, Circumvention, Excess Emissions, and Forms) |  |
| Rule 62-212, F.A.C. (Preconstruction Review, PSD Review and BACT) |  |
| Rule 62-213, F.A.C. (Title V Air Operation Permits for Major Sources of Air Pollution) |  |
| Rule 62-214, F.A.C. (Requirements For Sources Subject To The Federal Acid Rain Program) | 001, 002, 025, 026 |
| Rule 62-296, F.A.C. (Emission Limiting Standards) | 001, 002, 004 through 016, 025, 026,and 029 |
| Rule 62-297, F.A.C. (Test Methods and Procedures, Continuous Monitoring Specifications, and Alternate Sampling Procedures) |  |
| Rule 62-296.511, F.A.C. (Solvent Metal Cleaning) | 021 |
| PSD-FL-084 | 001, 002 |
| PPS PA 81-14/SA2 | 01, 002, 025, 026 |
| PSD-FL-313, 0950137-002-AC | 025, 026 |

This facility also includes miscellaneous unregulated/insignificant emissions units and/or activities.

Project DESCRIPTION

The purpose of this permitting project is to revise the existing Title V permit for the above referenced facility.  This revised permit incorporates permit No. 0950137-046-AC into the facility’s current Title V air operation permit No. 0950137-044-AV.

Processing Schedule and Related Documents

The Department received an application for a Title V Air Operation Permit Revision on April 21, 2016

Primary Regulatory requirements

Standard Industrial Classification (SIC) Code:  4911 – Electrical Generation.

North American Industry Classification System (NAICS):  221112 – Fossil Fuel Electric Power Generation.

HAP:  The facility is identified as a major source of hazardous air pollutants (HAP).

Title IV:  The facility operates units subject to the acid rain provisions of the Clean Air Act.

Title V:  The facility is a Title V major source of air pollution in accordance with Chapter 62-213, Florida Administrative Code (F.A.C.).

PSD:  The facility is a Prevention of Significant Deterioration (PSD)-major source of air pollution in accordance with Rule 62-212.400, F.A.C.

NSPS:  The facility operates units subject to the New Source Performance Standards (NSPS) of 40 Code of Federal Regulations (CFR) 60.

NESHAP:  The facility operates units subject to the National Emissions Standards for Hazardous Air Pollutants (NESHAP) of 40 CFR 63

CAIR:  The facility is subject to the Clean Air Interstate Rule (CAIR) set forth in Rule 62-296.470, F.A.C.

Siting:  The facility operates units that were certified under the Florida Power Plant Siting Act, 403.501-518, F.S., and Chapter 62-17, F.A.C.

CAM:  Compliance Assurance Monitoring (CAM) applies to emissions units 001 and 002 (FFSG 1 and 2 ) for the controlled emissions of particulate matter (PM) emissions controlled by an ESP.  Because the continuous opacity monitoring system (COMS) is required to be used at the facility (for Phase II Acid Rain Program purposes), it must also be used as part of the CAM plan.  A CAM plan is included for the ESP.  FFSG No.1 and No. 2 are not subject to CAM for the controlled emissions of sulfur dioxide (SO2) because the SO2 CEMS are used as a continuous compliance determination method.

The combined cycle combustion turbines (Emissions Units 025 and 026) and the combined cycle Unit B (Emission Unit 037) are not subject to CAM because the NOX CEMS is used for continuous compliance determination.  Thus no CAM plan is included for these units in this permit.

GHG:  The facility is not identified as a major source of green house gas (GHG) pollutants.

PROJECT REVIEW

Specific changes were made to the previous Title V Air Operation Permit No. 0950137-044-AV, and are in this Title V Air Operation Permit Revision.  For ease of identification, all changes to the permit have been highlighted in yellow within the permit document. Deletions are in strike through format while additions are in double underline format.  The revisions shown below are the only portions of the permit that are open for public comment or challenge.  Comments received related to the remainder of the permit will not be addressed during this permitting action.

- To reflect the change to EUs 025 and 026, (Stanton Unit A) authorized by Permit No. 0950137-046-AC, Specific Conditions of Section III, Subsection D. are modified as follows:

- Permitted Capacity.

- Combustion Turbine.  The maximum heat input rates to each CT/HRSG shall not exceed 2,402 million Btu (HHV) per hour (MMBtu/hr) when firing natural gas with duct burner firing and power augmentation or peak fire mode.  The maximum heat input rates to each CT/HRSG shall not exceed 2,068 MMBtu/hr (HHV) when firing fuel oil.  Manufacturer’s curves corrected for ISO conditions were provided to the Department of Environmental Protection (DEP) within 45 days prior to the completion of the initial compliance testing.

- Heat Recovery Steam Generator equipped with Duct Burner.  The maximum heat input rate of the natural gas fired duct burner shall not exceed 533 MMBtu/hour (LHV) (590 MMBtu/hour (HHV)) at any temperature or under any scenario.

[Rule 62-210.200, F.A.C. (Definitions - Potential Emissions); and 0950137-002-AC, Specific Conditions 10 and 11 and 0950137-046-AC, Specific Condition 2.]

{Permitting note:  Heat input capacity shall be determined by CEMS database used for the acid rain program.  CEMS data availability shall meet 40 CFR Part 75 requirements at greater than 95% of the time. Only valid hourly data shall be used to determine compliance with this provision. The source shall maintain this database for up to 5 years and make the information available upon request by the Department.}

- Nitrogen Oxides (NOx) and Ammonia Emissions.

- The concentration of NOx in the stack exhaust gas, with the combustion turbine operating on natural gas, shall not exceed 3.5 ppmvd @15% O2 on a 3-hour block average.  This limit shall apply whether or not the unit is operating with duct burner on and/or in power augmentation mode or peak fire mode.  Compliance shall be determined by the continuous emission monitor (CEMS).

- The emissions of NOx in the stack exhaust gas, with the combustion turbine operating on fuel oil shall not exceed 10.0 ppmvd @15% O2 on a 3-hour block average.  Compliance shall be determined by the continuous emission monitor (CEMS).

- Emissions of NOx from the duct burner shall not exceed 0.1 lb/MMBtu, which is more stringent than the NSPS .

- The concentration of ammonia in the exhaust gas from each CT/HRSG shall not exceed 5.0 ppmvd @15% O2.

[BACT Determination; Rules 62-4.070, 62-204.800(8), 62-212.400, and 62-4.070, F.A.C.; and 0950137-002 046-AC, Specific Condition 21 3.]

- Volatile Organic Compounds (VOC) Emissions.  Emissions of VOC in the stack exhaust gas (baseload at ISO conditions) shall not exceed 2.7 ppmvd @15% O2 with the CT firing fuel oil or 6.3 ppmvd @15% O2 with the CT firing natural gas (with maximum duct burner firing and operating in power augmentation mode or peak fire mode).  [BACT Determination; Rule 62-212.400, F.A.C.; and 0950137-002 046-AC, Specific Condition 23 4.]

- Annual Compliance Tests Required.  During each federal fiscal calendar year (October 1st to September 30th January 1st to December 31st), each EU shall be tested to demonstrate compliance with the emissions standards for visible emissions, carbon monoxide, and nitrogen oxides.  The Relative Accuracy Test Audits (RATA) for NOX and CO CEMS may be used in lieu of annual stack testing for these pollutants.  No annual stack test is required for NOx and CO so long as NOx and CO CEMS are utilized that meet the applicable quality assurance and quality control requirements of 40 CFR Part 60 and Part 75.   A VE tests is not required when firing fuel oil so long as total fuel oil firing during the fiscal year is less than 400 hours.  An annual VE test is required when firing the primary fuel.  Ammonia Slip testing while firing the primary fuel is required prior to the renewal of each operation permit. [Rule 62-297.310(7 8), F.A.C.; and Permit No.0950137-043 046-AC, Specific Condition 3 6.]

- Compliance Tests Prior To Renewal.  Compliance tests shall be performed for visible emissions, carbon monoxide, nitrogen oxides, and ammonia slip and volatile organic compounds once every 5 years.  No annual stack test is required for NOx and CO so long as NOx and CO CEMS are utilized that meet the applicable quality assurance and quality control requirements of 40 CFR Part 60 and Part 75.  Tests shall not be required for any unit with emissions generated solely from the combustion of fuel oil provided that during the previous permit cycle, the unit did not burn any fuel oil for more than 400 hours, other than during startup, during each calendar year included in the five-year period of permitted operation.  The tests shall occur prior to obtaining a renewed operating permit to demonstrate compliance with the emission limits in Specific Conditions D.13 - D.17.  [Rules 62-210.300(2)(a) and 62-297.310(7 8)(a), F.A.C. and 0950137-046-AC, Specific Condition 7]

- Performance Tests.  Performance tests shall be conducted after any replacement of the major components of the air pollution control equipment (and shake down period not to exceed 100 days after re-starting the CT), such as replacement of SCR catalyst or addition of oxidation catalyst (or change of combustors, if specifically requested by the DEP on a case-by-case basis).  Annual compliance tests shall be performed during every federal fiscal calendar year (October 1st to September 30th January 1st to December 31st) pursuant to Rule 62-297.310(7 8), F.A.C.  The reference methods listed in Specific Condition D.24. shall be used.  No other test methods may be used for compliance testing unless prior DEP approval is received in writing.  The applicant shall calculate and report the ppmvd ammonia slip (@ 15% O2) at the measured lb/hr NOX emission rate as a means of compliance with the BACT standard.  The applicant shall also be capable of calculating ammonia slip at the Department’s request.  [0950137-002 046-AC, Specific Condition 30. 5; and Applicant request in an e-mail memorandum received on October 7, 2004.]

- Compliance with the VOC Emission Limit.  An initial test was required to demonstrate compliance with the VOC emission limit.  Thereafter, the CO emission limit shall be employed as a surrogate and no annual testing or permit renewal testing is required.  [0950137-002 046-AC, Specific Condition 34 8.]

- Actual Emissions Reporting.  Because the review and issuance of permit No. 0950137-046-AC was based on an analysis that compared baseline actual emissions to projected actual emissions which was relied upon to avoid the requirements of subsections 62-212.400(4) through (12), F.A.C., for emissions of nitrogen oxides (NOX), the permittee is subject to the following monitoring, reporting and recordkeeping provisions:

- The permittee shall monitor the emissions of NOX emitted by EUs 025 and 026; and, using the most reliable information available, calculate and maintain a record of the annual emissions, in tons per year on a calendar year basis, for a period of 5 years following resumption of regular operations after the change (Calendar years 2016 through 2020).  Emissions shall be computed in accordance with the provisions in Rule 62-210.370, F.A.C., which are provided in Appendix RR of this permit.

- The permittee shall submit a report to the Department within 60 days after the end of each calendar year specified in paragraph D.39a., documenting the unit’s annual emissions of NOX during the previous calendar year.  The report shall contain the following:

  - The name, address and telephone number of the owner or operator of the major stationary source;

  - The annual emissions calculations pursuant to the provisions of 62-210.370, F.A.C., which are provided in Appendix RR of this permit;

  - If the emissions differ from the preconstruction projection, an explanation as to why there is a difference; and

  - Any other information that the owner or operator wishes to include in the report.

[Rules 62-212.300(1)(e) & 62-210.370, F.A.C.; and Permit No. 0950137-046-AC]

{Permitting note:  Actual Emissions - 92.93 TPY (Baseline Actual Emissions) = < 40 TPY of NOX emissions.  According to the applicant, the changes authorized by project 0950137-046-AC became effective on December 4, 2015.  Therefore, the 5 year reporting period for these EUs shall be for operations during calendar years 2016 through 2020, reported in calendar years 2017 through 2021.}

- A new section was added to the permit to incorporate the Transport Rule (Section VI, Transport Rule Part).

- Appendix RR was revised to incorporate the latest revisions to Rule 62-297.310, F.A.C.

Conclusion

This project revises Title V air operation permit No. 0950137-044-AV, which was effective on January 1, 2015.  This Title V air operation permit revision is issued under the provisions of Chapter 403, Florida Statues (F.S.), and Chapters 62-4, 62-210, 62-213 and 214, F.A.C.