# South Florida Water Management District

# Pump Station S-319

# Facility ID No. 0990620

# Pam Beach County, Florida

# Title V Air Operation Permit Renewal

# DRAFT Permit No. 0990620-008-AV

(Renewal of Title V Air Operation Permit No.0990620-007-AV)

# Permitting & Compliance Authority:

State of Florida

Florida Department of Health Palm Beach County

Division of Environmental Public Health

Air & Waste Section

P.O. Box 29 (800 Clematis Street)

West Palm Beach, FL 33402-0029

# Telephone:  (561) 837-5900

Fax:  (561) 837-5295

Title V Air Operation Permit Renewal

DRAFT Permit No. 0990620-008-AV

Table of Contents

Section	Page Number

Placard Page 	 i

- Facility Information.

- Facility Description. 	 2

- Summary of Emissions Units. 	 2

- Applicable Regulations. 	 3

- Facility-wide Conditions. 	 4

- Emission Unit Specific Conditions

- EU-002 to EU-006:  Two 1,210-BHP and Three 2,005-BHP Fairbanks-Morse pumps.	                        7

- EU-007: Two 685-BHP Cummins emergency generator. 	 17

IV	Appendices.

Appendix A, Abbreviations, Acronyms, Citations and Identification Numbers.

Appendix I, List of Insignificant Emissions Units and/or Activities.

Appendix NESHAP, Subpart A – General Provisions. (Include for all units that are subject to a NESHAP)

Appendix ZZZZ, “National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines (RICE)”

Appendix RR, Facility-wide Reporting Requirements.

Appendix TR, Facility-wide Testing Requirements.

Appendix TV, Title V General Conditions.

Referenced Attachments. At End

Table H, Permit History.

Statement of Basis

Permittee:		Permit No. 0990620-008-AV

| South Florida Water Management District | Facility ARMS ID No.: 0990620 |
| --- | --- |
| 3301 Gun Club Road | SIC Nos.: 9511 |
| West Palm Beach, FL 33406 | Project: Title V Air Operation Permit Renewal for SFWMD Pump Station S-319 |

The purpose of this permit is to renew the Title V air operation permit for the above referenced facility.  The facility,  SFWMD Pump Station S-319 is located in Palm Beach County at Northern edge of Storm water Treatment Area 1 East (STA-1E); one mile west of Flying Cow Road and South of the C-51 Canal in Palm Beach County UTM Coordinates: Zone 17; 567.020 km E; 2951.385 km N; Latitude: 26º 40′ 55″ North / Longitude: 80º 19′ 35″ West.

The Title V air operation permit is issued under the provisions of Chapter 403, Florida Statutes (F.S.), and Florida Administrative Code (F.A.C.) Chapters 62-4, 62-210, and 62-213.  The above named permittee is hereby authorized to operate the facility in accordance with the terms and conditions of this permit.

Effective Date:  DRAFT

Renewal Application Due Date:  DRAFT

Expiration Date:  DRAFT

DRAFT

__________________________________________________

Laxmana Tallam, P.E., Environmental Administrator

Air and Waste Section

Division of Environmental Public Health

Subsection A.  Facility Description.

The Title V Source, identified as Pump Station S-319 (SIC Code 9511), has been assigned AIRS ID No. 0990620. It is located at the Northern edge of Stormwater Treatment Area 1 East (STA-1E); one mile west of Flying Cow Road and South of the C-51 Canal in Palm Beach County. UTM Coordinates: Zone 17; 567.020 km E; 2951.385 km N; Latitude: 26 40′ 55″ North / Longitude: 80 19′ 35″ West. Pump Station S-319 has been operating since the year 2003. The site can be accessed from State Road 80.

The facility includes two Fairbanks-Morse 1,210-BHP (brake horse power) water pumps, three Fairbanks-Morse 2,005-BHP water pumps, two Cummins 685-BHP emergency power generators, four 20,000-gallons above ground storage tanks (ASTs), two 200-gallon above ground day tanks and three 300-gallon above ground day tanks for the pump engines, and one 200-gallon tank for both generators, and miscellaneous insignificant activities. It is classified as a synthetic-minor source under the Prevention of Significant Deterioration (PSD) program and a natural minor source under the Hazardous Air Pollutant program.  Potential emissions of criteria pollutants from the source are limited below the 250 ton per year -- major source threshold of the PSD program -- by a federally enforceable construction permit (099-0620-001-AC).

Subsection B.  Summary of Emissions Units.

| EU ID No. | Status | Brief Description |
| --- | --- | --- |
| 002 | Regulated | One 1,210 brake horse-power (BHP) pump engine (RICE) This emissions unit is an eight cylinder Fairbanks-Morse Model 38D8-1/8 diesel engine/pump combination. (Serial No. 38D800005DS8) |
| 003 | Regulated | One 1,210-BHP pump engine (RICE) This emissions unit is an eight cylinder Fairbanks-Morse Model 38D8-1/8 diesel engine/pump combination. (Serial No. 38D800006DS8) |
| 004 | Regulated | One 2,005-BHP pump engine (RICE) This emissions unit is a twelve cylinder Fairbanks-Morse Model 38D8-1/8 diesel engine/pump combination. (Serial No. 38D800001DS12) |
| 005 | Regulated | One 2,005-BHP pump engine (RICE) This emissions unit is a twelve cylinder Fairbanks-Morse Model 38D8-1/8 diesel engine/pump combination. (Serial No. 38D800004DS12) |
| 006 | Regulated | One 2,005-BHP pump engine (RICE) This emissions unit is a twelve cylinder Fairbanks-Morse Model 38D8-1/8 diesel engine/pump combination. (Serial No. 38D800002DS12) |
| 007 | Regulated | - Two 685-BHP Cummins Onan emergency power generators (Serial No. 37205673 and 37205672) |
| 008 | Insignificant | Volatile Organic Liquid Storage Tanks: - Four 20,000 gallon above ground storage tanks. - Two 200 gallon above ground day tanks for 1,210 bhp diesel engines. - Three 300 gallon above ground day tanks for 2,005 bhp diesel engines. - One 200 gallon above ground day tank for both emergency generators. |

Also included in this permit are miscellaneous insignificant emissions units and/or activities (see Appendix I, List of Insignificant Emissions Units and/or Activities).

Subsection C.  Applicable Regulations.

Based on the Title V air operation permit renewal application received June 29, 2016, this facility is not a major source of hazardous air pollutants (HAP).  The existing facility is a prevention of significant deterioration (PSD) major source of air pollutants in accordance with Rule 62-212.400, F.A.C.  A summary of applicable regulations is shown in the following table.

| Regulation | ## EU No(s). |
| --- | --- |
| Federal Rule Citations |  |
| 40 CFR 63, Subpart _ZZZZ “National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines (RICE)” | EU002, EU003, EU004, EU005, EU006 & EU 007 |
| State Rule Citations |  |
| 62-4 - Permits | Facility Wide |
| 62-204 - Air Pollution Control - General Provisions | Facility Wide |
| 62-210 - Stationary Sources - General Requirements | Facility Wide |
| 62-213 - The facility is a Title V major source of air pollution | Facility Wide |
| 62-212 - Stationary Sources - Preconstruction Review Title V major source of air pollution (PSD) | Facility Wide |
| 62-257 - Asbestos Program | Facility Wide |
| 62-296 - Stationary Sources - Emission Standards | Facility Wide |
| 62-297 - Stationary Sources - Emissions Monitoring | Facility Wide |

Subsection D.  Relevant Documents

The following documents are on file with the permitting authority:

###### Title V Operating Permit renewal application (0990620-008-AV) received on June 29, 2016.

Please reference the Permit No., Facility ID No., and appropriate Emissions Unit(s) ID No(s), on all correspondence, test report submittals, applications, etc.

The following conditions apply facility-wide to all emission units and activities:

- Appendices.  The permittee shall comply with all documents identified in Section IV, Appendices, listed in the Table of Contents.  Each document is an enforceable part of this permit unless otherwise indicated.  [Rule 62-213.440, F.A.C.]

Emissions and Controls

- Objectionable Odor Prohibited.  No person shall cause, suffer, allow or permit the discharge of air pollutants, which cause or contribute to an objectionable odor.  An “objectionable odor” means any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance.  [Rule 62-296.320(2) and 62-210.200(Definitions), F.A.C.]

- General Volatile Organic Compounds (VOC) Emissions or Organic Solvents (OS) Emissions.  The permittee shall allow no person to store, pump, handle, process, load, unload or use in any process or installation, volatile organic compounds or organic solvents without applying known and existing vapor emission control devices or systems deemed necessary and ordered by the Department.  .  [Rule 62-296.320(1), F.A.C.]

{Permitting Note:  Nothing is deemed necessary and ordered at this time.}

- General Visible Emissions.  No person shall cause, let, permit, suffer or allow to be discharged into the atmosphere the emissions of air pollutants from any activity equal to or greater than 20% opacity.  This regulation does not impose a specific testing requirement.  [Rule 62-296.320(4)(b), F.A.C.]

- Unconfined Particulate Matter.  No person shall cause, let, permit, suffer or allow the emissions of unconfined particulate matter from any activity, including vehicular movement; transportation of materials; construction; alteration; demolition or wrecking; or industrially related activities such as loading, unloading, storing or handling; without taking reasonable precautions to prevent such emissions.  Reasonable precautions to prevent emissions of unconfined particulate matter at this facility include:

  - Surface Coating Areas:  When practical, use of partial or total enclosures and limiting outdoor activities to the times of favorable weather conditions to avoid off site impacts.

  - Lawn & Ground Maintenance: Application of water to non-vegetative areas as needed, landscaping and grass in other areas as necessary.

  - Parking areas:  Application of water as needed.

  - Paved and Unpaved Roads:  As needed, application of water, the removal of particulate matter from paved roads, limited site access to vehicles, and vehicle speed limitations.

[Rule 62-296.320(4)(c), F.A.C.; and, proposed by applicant in Title V air operation permit renewal application received June 29, 2016.]

Annual Reports and Fees

See Appendix RR, Facility-wide Reporting Requirements for additional details.

- Electronic Annual Operating Report and Title V Annual Emissions Fees.  The information required by the Annual Operating Report for Air Pollutant Emitting Facility [Including Title V Source Emissions Fee Calculation] (DEP Form No. 62-210.900(5)) shall be submitted by April 1 of each year, for the previous calendar year, to the Department of Environmental Protection’s (DEP) Division of Air Resource Management.  Each Title V source shall submit the annual operating report using the DEP’s Electronic Annual Operating Report (EAOR) software, unless the Title V source claims a technical or financial hardship by submitting DEP Form No. 62-210.900(5) to the DEP Division of Air Resource Management instead of using the reporting software.  Emissions shall be computed in accordance with the provisions of subsection 62-210.370(2), F.A.C.  Each Title V source must pay between January 15 and April 1 of each year an annual emissions fee in an amount determined as set forth in subsection 62-213.205(1), F.A.C.  The annual fee shall only apply to those regulated pollutants, except carbon monoxide and greenhouse gases, for which an allowable numeric emission-limiting standard is specified in the source’s most recent construction permit or operation permit.  Upon completing the required EAOR entries, the EAOR Title V Fee Invoice can be printed by the source showing which of the reported emissions are subject to the fee and the total Title V Annual Emissions Fee that is due.  The submission of the annual Title V emissions fee payment is also due (postmarked) by April 1st of each year.  A copy of the system-generated EAOR Title V Annual Emissions Fee Invoice and the indicated total fee shall be submitted to:  Major Air Pollution Source Annual Emissions Fee, Post Office Box 3070, Tallahassee, Florida 32315-3070.  Additional information is available by accessing the Title V Annual Emissions Fee On-line Information Center at the following Internet web site:  http://www.dep.state.fl.us/air/emission/tvfee.htm.  [Rules 62-210.370(3), 62-210.900 & 62-213.205, F.A.C.; and, §403.0872(11), Florida Statutes (2013)]

{Permitting Note:  Resources to help you complete your AOR are available on the electronic AOR (EAOR) website at:  http://www.dep.state.fl.us/air/emission/eaor.  If you have questions or need assistance after reviewing the information posted on the EAOR website, please contact the Department by phone at (850) 717-9000 or email at eaor@dep.state.fl.us.}

{Permitting Note:  The Title V Annual Emissions Fee form (DEP Form No. 62-213.900(1)) has been repealed.  A separate Annual Emissions Fee form is no longer required to be submitted by March 1st each year.}

- Annual Statement of Compliance.  The permittee shall submit an annual statement of compliance to the compliance authority at the address shown on the cover of this permit within 60 days after the end of each calendar year during which the Title V permit was effective.  [Rules 62-213.440(3)(a)2. & 3. and (b), F.A.C.]

FW8.	Prevention of Accidental Releases (Section 112(r) of CAA).  If, and when, the facility becomes subject to 112(r), the permittee shall:

- Submit its Risk Management Plan (RMP) to the Chemical Emergency Preparedness and Prevention Office (CEPPO) RMP Reporting Center.  Any Risk Management Plans, original submittals, revisions or updates to submittals, should be sent electronically through EPA’s Central Data Exchange system at the following address:  https://cdx.epa.gov.  Information on electronically submitting risk management plans using the Central Data Exchange system is available at:  http://www2.epa.gov/rmp.  The RMP Reporting Center can be contacted at:  RMP Reporting Center, Post Office Box 10162, Fairfax, VA  22038, Telephone:  (703) 227-7650.

- Submit to the permitting authority Title V certification forms or a compliance schedule in accordance with Rule 62-213.440(2), F.A.C.

[40 CFR 68]

FW9	Notifications and Reports:  The permittee shall submit all compliance-related notifications and reports required by this permit to the Palm Beach County Health Department and the Florida Department of Environmental Protection’s (FDEP) Southeast District Office at:

Palm Beach County Health Department

Air & Waste Section

Post Office Box 29

800 Clematis Street, 4th Floor

West Palm Beach, Florida  33402-0029

Telephone:  (561) 837-5900

Fax:   (561) 837-5295

Florida Department of Environmental Protection

Air Program, Southeast District Office

400 N. Congress Avenue Suite 200

West Palm Beach, Florida, 33401

Telephone: (561) 681-6600

Fax: (561) 681 – 6790

FW10.  U.S. Environmental Protection Agency, Report & Notifications:  Any reports, data, notification, certifications, and requests required to be sent to the U. S. EPA should be sent to:

United States Environmental Protection Agency

Region 4

Air and EPCRA Enforcement Branch, Air Enforcement Section

61 Forsyth Street

Atlanta, GA  30303

Telephone: (404) 562-9155

Fax: (404) 562-9163 or (404) 562-9164

FW11. 	Permitted Capacity: The permittee shall not allow, cause, suffer or permit the operation of the unit in excess of the following without prior authorization from the Permitting Authority:

Annual Fuel Consumption: Annual fuel consumption for the pump station including all support equipment shall not exceed 1,136,264 gallons of diesel in any consecutive 12 months, rolling total.

[Air Construction Permit 0990620-006-AC]

The specific conditions in this section apply to the following emissions unit(s):

| ##### EU ID No | ##### Status | ##### Brief Description |
| --- | --- | --- |
| 002 | Regulated | One 1,210 brake horse-power (BHP) pump engine (RICE) This emissions unit is an eight cylinder Fairbanks-Morse Model 38D8-1/10 diesel engine/pump combination. (Serial No. 38D8000005DS8) |
| 003 | Regulated | One 1,210-BHP pump engine (RICE) This emissions unit is an eight cylinder Fairbanks-Morse Model 38D8-1/10 diesel engine/pump combination. (Serial No. 38D8000006DS8) |
| 004 | Regulated | One 2,005-BHP pump engine (RICE) This emissions unit is a twelve cylinder Fairbanks-Morse Model 38D8-1/8 diesel engine/pump combination. (Serial No. 38D800001DS12) |
| 005 | Regulated | One 2,005-BHP pump engine (RICE) This emissions unit is a twelve cylinder Fairbanks-Morse Model 38D8-1/8 diesel engine/pump combination. (Serial No. 38D800004DS12) |
| 006 | Regulated | One 2,005-BHP pump engine (RICE) This emissions unit is a twelve cylinder Fairbanks-Morse Model 38D8-1/8 diesel engine/pump combination. (Serial No. 38D800002DS12) |

All the above engines were installed at the facility in 2003.

Two (2) rebuilt Fairbanks-Morse 38D8-1/10 engines each coupled to a flood control pump. They are eight-cylinder opposed piston engines firing distillate oil up to 66.23 gallons per hour (~9.08 mmBtu/hr).  They have the capability to fire distillate oil with a maximum sulfur content of 0.5 percent by weight.  The nameplate rating is 1,210 brake horsepower (BHP) each.

Three (3) Fairbanks-Morse 38D8-1/8 engine coupled to a flood control pump.  They are twelve-cylinder opposed piston engine firing distillate oil at up to 109.74 gallons per hour (~15.04 mmBtu/hr).  They have the capability to fire distillate oil with a maximum sulfur content of 0.5 percent by weight.  The nameplate rating is 2,005 BHP each.

The following specific conditions apply to the emissions unit(s) listed above:

Note: The emissions units listed above are subject to 40 CFR 63 Subpart ZZZZ, “National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines (RICE).” These emission units are not subject to 40 CFR 60 Subpart IIII, “Standards of Performance for Stationary Compression Ignition Internal Combustion Engines” based on the installation date.

Operating Restrictions

III.A.1.	Permitted Capacity:  The permittee shall not allow, cause, suffer or permit the operation of the unit in excess of the following without prior authorization from the Permitting Authority:

- Annual Fuel Consumption:  The permittee shall comply with the annual fuel consumption requirement specified in the Section II. Facility-Wide General Condition No. FW11 of this permit.

III.A.2.	Methods of Operation:  The permittee shall not allow, cause, suffer or permit any change in the method(s) of operation resulting in increased short-term or long-term emissions, without prior authorization from the Permitting Authority.  The authorized methods of operation include the following:

Fuels: The permittee is authorized to use only diesel fuel that meets the following requirements of 40 CFR 80.510(b).  [40 CFR 63.6604]

(1) Maximum Sulfur content of 15 ppm.

(2) Cetane index or aromatic content, as follows:

(i) A minimum cetane index of 40; or

(ii) A maximum aromatic content of 35 volume percent.

III.A.3.	Compliance Date:  The permittee shall comply with the applicable regulations, emission limitations and operating limitations of 40 CFR Part 63 Subpart ZZZZ. [40 CFR 63.6585, 40 CFR 63.6590(1) & 40 CFR 63.6595(a)(1)]

III.A.4.	Hours of Operation:  The permittee is authorized to operate the emissions units continuously without exceeding the fuel limitations specified in the Specific Condition III.A.1 of this permit

III.A.5.	Operating Limitation:  The permittee shall meet the following operating limitations:

- Maintain the catalyst so that the pressure drop across the catalyst does not change by more than 2 inches of water at 100 percent load plus or minus 10 percent from the pressure drop across the catalyst that was measured during the initial performance test; and

- Maintain the temperature of the engine’s exhaust so that the catalyst inlet temperature is greater than or equal to 450°F and less than or equal to 1350°F.

[40 CFR 63.6603 (a)]

Emissions Limitations and Standards

III.A.6.	Emission Limitations:  The permittee shall meet the following requirements, except during periods of startup: [40 CFR 63.6603(a)]

- Limit concentration of Carbon Monoxide (CO) in the exhaust to 23 ppmvd at 15% Oxygen (O2); 	or

- Reduce CO emissions by 70% percent or more.

Test Methods and Procedures

III.A.7.	Initial Performance Test:

- The permittee shall conduct the initial performance test as specified in the table below within 180 days after the compliance date as specified in the Specific Condition III.A.3 of this permit.

[40 CFR 63.6612 (a)]

‘Requirements for the Performance Test’ (Table 4 of Subpart ZZZZ of Part 63)

| For each . . . | Complying with the requirement to . . . | Permittee must . . . | Using . . . | According to the following requirements . . . |
| --- | --- | --- | --- | --- |
| CI stationary RICE | Reduce CO emissions | i. Measure the O2 at the inlet and outlet of the control device; and | (1) Portable CO and O2 analyzer | (a) Using ASTM D6522–00 (2005)a (incorporated by reference, see §63.14). Measurements to determine O2 must be made at the same time as the measurements for CO concentration. |
|  |  | ii. Measure the CO at the inlet and the outlet of the control device | (1) Portable CO and O2 analyzer | (a) Using ASTM D6522–00 (2005)ab (incorporated by reference, see §63.14) or Method 10 of 40 CFR appendix A. The CO concentration must be at 15 percent O2, dry basis. |

a The Permittee may also use Methods 3A and 10 as options to ASTM–D6522–00 (2005). The Permittee may obtain a copy of ASTM–D6522–00 (2005) from at least one of the following addresses: American Society for Testing and Materials, 100 Barr Harbor Drive, West Conshohocken, PA 19428–2959, or University Microfilms International, 300 North Zeeb Road, Ann Arbor, MI 48106. ASTM–D6522–00 (2005) may be used to test both CI and SI stationary RICE.

b The Permittee may also use Method 320 of 40 CFR part 63, appendix A, or ASTM D6348–03.

- The Permittee is not required to conduct an initial performance test on a unit for which a performance test has been previously conducted, but the test must meet all of the conditions described in paragraphs (1) through (4) of this section.

- The test must have been conducted using the same methods specified in 40 CFR 63 Subpart ZZZZ and these methods must have been followed correctly.

- The test must not be older than 2 years.

- The test must be reviewed and accepted by the Department.

- Either no process or equipment changes must have been made since the test was performed, or the owner or operator must be able to demonstrate that the results of the performance test, with or without adjustments, reliably demonstrate compliance despite process or equipment changes.

[40 CFR 63.6612 (b)]

{Permitting Note:  Initial performance test was conducted at this facility in August 2013.}

III.A.8.	Subsequent Performance Test: The permittee shall conduct subsequent performance tests as specified in Specific Condition III.A.7 (a) every 8,760 hours or 3 years, whichever comes first. [40 CFR 63.6615]

III.A.9.	Performance Test Procedure: The permittee shall use the following performance test procedure:

- Each performance test must be conducted according to the requirements specified in Specific Conditions III.A.7 and III.A.8. If the permittee operates a non-operational stationary RICE that is subject to performance testing, the permittee does not need to start up the engine solely to conduct the performance test.  The permittee can conduct the performance test when the engine is started up again. [40 CFR 63.220(a) & (b)]

- The permittee must conduct three separate test runs for each performance test required in this permit. Each test run must last at least 1 hour. [40 CFR 63.6620(d)]

(c)	(1) 	The Permittee must use Equation 1 (below) to determine compliance with the percent reduction requirement [40 CFR 63.6620(e)](1) & (2)]

Where:

Ci= 	concentration of carbon monoxide (CO) at the control device inlet,

Co=	 concentration of CO at the control device outlet, and

R = 	percent reduction of CO emissions

(2) 	The Permittee must normalize the carbon monoxide (CO) concentrations at the inlet and outlet of the control device to a dry basis and to 15 percent oxygen, or an equivalent percent carbon dioxide (CO2). If pollutant concentrations are to be corrected to 15 percent oxygen and CO2 concentration is measured in lieu of oxygen concentration measurement, a CO2 correction factor is needed. Calculate the CO2 correction factor as described below [40 CFR 63.6620 (e)(2)(i) through (iii)].

(i) Calculate the fuel-specific Fovalue for the fuel burned during the test using values obtained from Method 19, section 5.2, and the following equation:

Where:

Fo= 	Fuel factor based on the ratio of oxygen volume to the ultimate CO2 volume produced by the fuel at zero percent excess air.

0.209 = 	Fraction of air that is oxygen, percent/100.

Fd= 	Ratio of the volume of dry effluent gas to the gross calorific value of the fuel from Method 19, dsm3 /J (dscf/106 Btu).

Fc= 	Ratio of the volume of CO2 produced to the gross calorific value of the fuel from Method 19, dsm3 /J (dscf/106 Btu).

(ii) Calculate the CO2 correction factor for correcting measurement data to 15 percent oxygen, as follows:

Where:

Xco2= 		CO2correction factor, percent.

5.9 = 		20.9 percent O2−15 percent O2, the defined O2 correction value, percent.

(iii) Calculate the NOX and SO2 gas concentrations adjusted to 15 percent O2 using CO2 as follows:

Where:

%CO2= 	Measured CO2concentration measured, dry basis, percent.

(d)	The engine percent load during a performance test must be determined by documenting the calculations, assumptions, and measurement devices used to measure or estimate the percent load in a specific application. A written report of the average percent load determination must be included in the notification of compliance status. The following information must be included in the written report:

- the engine model number,

- the engine manufacturer,

- the year of purchase,

- the manufacturer's site-rated brake horsepower,

- the ambient temperature, pressure, and humidity during the performance test, and

- All assumptions that were made to estimate or calculate percent load during the performance test must be clearly explained.

- If measurement devices such as flow meters, kilowatt meters, beta analyzers, stain gauges, etc. are used, the model number of the measurement device, and an estimate of its accurate in percentage of true value must be provided.

[40 CFR 63.6620]

Monitoring, Installation, Collection, Operation and Maintenance Requirements

III.A.10.		Installation of Control Technology: The permittee shall install and maintain diesel oxidation catalyst (DOC) at each of the 1,210-BHP and 2,005-BHP engines to reduce the CO emissions to 23 ppmv @ 15% O2 or by 70% or more as required by 40 CFR 63 Subpart ZZZZ.  The DOC units are Quick-Lid Catalytic Converter, manufactured by DCL International, Inc. [Permit No. 0990620-006-AC]

III.A.11.    	Installation Requirements:   The permittee that owns or operates an existing non-emergency, non-black start CI engine greater than or equal to 300 HP that is not equipped with a closed crankcase ventilation system, must comply with either paragraph (a) or paragraph (b) of this specific condition. The permittee shall follow the manufacturer's specified maintenance requirements for operating and maintaining the open or closed crankcase ventilation systems and replacing the crankcase filters, or can request the Administrator to approve different maintenance requirements that are as protective as manufacturer requirements.  [40 CFR 63.6625 (g)]

- Install a closed crankcase ventilation system that prevents crankcase emissions from being emitted to the atmosphere, or

- Install an open crankcase filtration emission control system that reduces emissions from the crankcase by filtering the exhaust stream to remove oil mist, particulates, and metals.

III.A.12.		Operation Requirements:   The permittee shall minimize the engine's time spent at idle during startup and minimize the engine's startup time to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes, after which time the emission standards are applicable, as specified in Specific Condition III.A.6.  [40 CFR 63.6625(h)]

III.A.13.	    Special Compliance Tests:  When the Health Department, after investigation, has good reason (such as complaints, increased visible emissions or questionable maintenance of control equipment) to believe that any applicable emission standard contained in Rule 62-210, 62-212, 62-296, or 62-297, F.A.C. or in a permit issued pursuant to those rules is being violated, it may require the owner or operator of the facility to conduct compliance tests which identify the nature and quantity of pollutant emissions from the emissions units and to provide a report on the results of said tests to the Health Department.  [Rule 62-297.310(7)(b), F.A.C.]

{Permitting Note: The emissions units have been exempted from the NOx-RACT requirements of Rule 62-296.570(4)(b)7., F.A.C. by the Florida Department of Environmental Protection in a letter dated December 13, 1996 from FDEP.  In addition, the emissions units have avoided the requirements of BACT of Rule 62-212.300(5)(c), F.A.C. by accepting a federally enforceable cap on annual fuel oil usage. The Health Department reserves the right to request a special compliance test for emissions of nitrogen oxides in the event new data indicates that potential emissions would exceed 250 tons per year. The facility’s current potential NOx emissions are 249.12 tons per year, based on the NOx emission factor of 3.2 lb/MMBtu}

III.A.14.		 Annual Fuel Consumption:  The permittee shall monitor compliance with the annual fuel consumption limit on a monthly basis.  If the rolling 12-month total does not exceed 909,000 gallons (80% of the fuel oil consumption cap), the permittee shall continue to monitor fuel consumption on a monthly basis (rolling 12-month total).  If the rolling 12-month total exceeds 909,000 gallons, the permittee shall monitor fuel consumption on a daily basis (rolling 365-day total).  When the rolling 365-day total does not exceed 909,000 gallons for 30 consecutive days, monthly monitoring can be resumed. [Permit No. 0990620-006-AC]

III.A.15.		Emissions Factor Verification:  When the Health Department has reason to believe that the emission factor used to establish the fuel usage caps has changed, it may require the owner or operator of the emission unit to conduct compliance tests which identify the nature and quantity of pollutant emission from the emission unit and to provide a report on the results of said tests to the Department.  [Permit No. 0990620-006-AC]

Initial Compliance

III.A.16.    Initial Compliance Requirement:  The permittee complying with the requirement to reduce CO emissions and using oxidation catalyst shall have demonstrated the initial compliance if:

- The average reduction of emissions of CO determined from the initial performance test achieves the required CO percent reduction; and

- The permittee has recorded the catalyst pressure drop and catalyst inlet temperature during the initial performance test.

[40 CFR 63.6630(a)]

{Permitting Note:  Initial performance test was conducted at this facility in August 2013.}

III.A.17.    During the initial performance test, the permittee shall establish each operating limitation as specified in the Specific Condition III.A.5 of this permit.  [40 CFR 63.6630(b)]

III.A.18.    Notification of Initial Compliance Status: The permittee shall submit the Notification of Compliance Status containing the results of the initial compliance demonstration according to the requirements in Specific Condition III.A.24 of this permit.  [40 CFR 63.6630(c)]

Continuous Compliance

III.A.19.    The permittee shall be in compliance with the emissions limitation as required in the Specific Condition III.A.6 and operating limitation as required in the Specific Condition III.A.5 at all times. [40 CFR 63.6605 (a)]

III.A.20.   At all times the permittee shall operate and maintain any affected source, including associated air pollution control equipment and monitoring equipment, in a manner consistent with safety and good air pollution control practices for minimizing emissions. The general duty to minimize emissions does not require the permittee to make any further efforts to reduce emissions if levels required by this standard have been achieved. Determination of whether such operation and maintenance procedures are being used will be based on information available to the Administrator which may include, but is not limited to, monitoring results, review of operation and maintenance procedures, review of operation and maintenance records, and inspection of the source.  [40 CFR 63.6605 (b)]

III.A.21.	The permittee shall report each instance in which the emissions unit did not meet each emission limitation or operating limitation specified in the permit. These instances are deviations from the emission and operating limitations specified in the permit. These deviations must be reported according to the requirements in the Specific Condition III.A.27. If the permittee changes the catalyst, the permittee shall reestablish the values of the operating parameters measured during the initial performance test. When reestablishing the values of the operating parameters, the permittee shall also conduct a performance test to demonstrate that the emissions unit is meeting the required emission limitation.  [40 CFR 63.6640 (b)]

The permittee must also report each instance in which the emissions unit did not meet the requirements in Table 8 of Subpart ZZZZ of 40 CFR Part 63 (Appendix  ZZZZ).  [40 CFR 63.6640(e)]

Notification Requirements

III.A.22.	Notification of Performance Tests: The permittee shall notify the PBCHD in writing of the intent to conduct a performance test at least 60 calendar days before the performance test is initially scheduled to begin to allow the PBCHD, upon request, to review and approve the site-specific test plan and to have an observer present during the test. [40 CFR 63.6645 (a) & 40 CFR 63.7 (b)(1)]

III.A.23.	In the event the permittee is unable to conduct the performance test on the date specified in the notification requirement specified in Specific Condition III.A.22 due to unforeseeable circumstances beyond his or her control, the permittee must notify the PBCHD as soon as practicable and without delay prior to the scheduled performance test date and specify the date when the performance test is rescheduled. This notification of delay in conducting the performance test shall not relieve the permittee of legal responsibility for compliance with any other applicable provisions of this part or with any other applicable Federal, State, or local requirement, nor will it prevent the PBCHD from implementing or enforcing this part or taking any other action under the Act.

[40 CFR 63.6645 (a) & 40 CFR 63.7 (b)(2)]

III.A.24.	Notification of Compliance Status: The Notification of Compliance Status, including the performance test results, shall be mailed before the close of business on the 60th day following the completion of the relevant compliance demonstration activities (such as initial performance test or any subsequent required performance test). Notifications may be combined as long as the due date requirement for each notification is met.

[40 CFR 63.6645 (h)]

Reporting And Recordkeeping Requirements

III.A.25.     Record Keeping Requirements:

- For monthly fuel consumption monitoring (the rolling 12-month total does not exceed 909,000 gallons): Within the first 15 days of each month, the permittee shall record in a written log the following information [Permit No. 0990620-006-AC]:

- Gallons of diesel fuel consumed for the previous month of operation;

- Gallons of diesel fuel consumed for the previous consecutive 12 months of operation (including the previous month consumption discussed as above; and

- Hours of operation for each pump engine for the previous month of operation.

- For daily fuel consumption monitoring (the rolling 12-month total does exceed 909,000 gallons): Once per day, the permittee shall record in a written log the following information:

- Gallons of diesel fuel consumed for the that day of operation;

- Gallons of diesel fuel consumed for the previous consecutive 365 days of operation; and

- Hours of operation for each pump engine for that day of operation.

III.A.26.	The permittee shall maintain the recordkeeping for the following items listed below. The recordkeeping shall be maintained in a form suitable and readily available for expeditious inspection and review for the followings. The files shall be retained for at least 5 years following the date of each occurrence, measurement, maintenance, corrective action, report of record. At a minimum, the most recent 2 years of data shall be retained on site. The remaining 3 years of data may be retained off site.  Such files may be maintained on microfilm, on a computer, on computer floppy disks, on magnetic tape disks, or on microfiche. [40 CFR 63.6655(a) & (d)]

- A copy of each notification and report submitted to comply with the emission and operating limitations, including all documentation supporting any Initial Notification or Notification of Compliance Status.

- Records of the occurrence and duration of each malfunction of operation (i.e., process equipment) or the air pollution control and monitoring equipment.

- Records of performance tests and performance evaluations.

- Records of all required maintenance performed on the air pollution control and monitoring equipment.

- Records of actions taken during periods of malfunction to minimize emissions in accordance with Specific Condition III.A.20, including corrective actions to restore malfunctioning process and air pollution control and monitoring equipment to its normal or usual manner of operation.

- The permittee must keep records required in Table 6 of the Subpart ZZZZ (see Appendix ZZZZ) to show continuous compliance with each emission or operating limitations that applies.

III.A.27.	Reporting Requirements:  The Permittee shall submit Semiannual Compliance Report, as required in Table 7 of  Appendix ZZZZ, containing the following information:

- If there are no deviations from any emission limitations or operating limitations that apply to the emissions units, a statement that there were no deviations from the emission limitations or operating limitations during the reporting period.

- If the emissions units had a deviation from any emission limitation or operating limitation during the reporting period, the report shall contain following  information:

  - Company name and address.

  - Statement by a responsible official, with that official's name, title, and signature, certifying the accuracy of the content of the report.

  - Date of report and beginning and ending dates of the reporting period.

  - The total operating time of the stationary RICE at which the deviation occurred during the reporting period.

  - Information on the number, duration, and cause of deviations (including unknown cause, if applicable), as applicable, and the corrective action taken.

- If the emissions unit had a malfunction during the reporting period, the compliance report must include the number, duration, and a brief description for each type of malfunction which occurred during the reporting period and which caused or may have caused any applicable emission limitation to be exceeded. The report must also include a description of actions taken by the permittee during a malfunction of an affected source to minimize emissions in accordance with 40 CFR 63.6605(b), including actions taken to correct a malfunction.

[40 CFR 63.6650(a), (c), (d)]

III.A.28.	The permittee shall submit each report required in Specific condition III.A.27, by the date as specified below:

  - For semiannual compliance reports, the first compliance report must cover the period beginning on the compliance date as specified in Specific Condition III.A.3  and ending on June 30 or December 31, whichever date is the first date following the end of the first calendar half after the compliance date.

  - For semiannual compliance reports, the first compliance report must be postmarked or delivered no later than July 31 or January 31, whichever date follows the end of the first calendar half after the compliance date as specified in Specific Condition III.A.3.

  - For semiannual compliance reports, each subsequent compliance report must cover the semiannual reporting period from January 1 through June 30 or the semiannual reporting period from July 1 through December 31.

  - For semiannual compliance reports, each subsequent compliance report must be postmarked or delivered no later than July 31 or January 31, whichever date is the first date following the end of the semiannual reporting period.

[40 CFR 63.6650(b)]

III.A.29	The permittee must report all deviations as defined in the Subpart ZZZZ in the semiannual monitoring report required by 40 CFR 70.6 (a)(3)(iii)(A) or 40 CFR 71.6(a)(3)(iii)(A). If the permittee submits a Compliance report pursuant to Table 7 of the subpart ZZZZ along with, or as part of, the semiannual monitoring report required by 40 CFR 70.6(a)(3)(iii)(A) or 40 CFR 71.6(a)(3)(iii)(A), and the Compliance report includes all required information concerning deviations from any emission or operating limitation in this subpart, submission of the Compliance report shall be deemed to satisfy any obligation to report the same deviations in the semiannual monitoring report. However, submission of a Compliance report shall not otherwise affect any obligation permittee may have to report deviations from permit requirements to the Department. [40 CFR 63.6650(f)]

III.A. 30	Performance Tests Results: The performance test results shall be mailed as a part of Notification of Compliance Status, as specified in Specific Condition III.A.24 of this permit, before the close of business on the 60th day following the completion of the relevant performance tests. [40 CFR 63.6645(h)]

III.A.31 Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

III.A.32 Compliance Tests Prior To Renewal.  Except as provided in subparagraph 62-297.310(8)(b)3., F.A.C. (see condition TR7.b.(3) in Appendix TR – Facility-wide Testing Requirements), in addition to the compliance tests specified above, compliance tests shall also be performed prior to obtaining a renewed operation permit to demonstrate compliance with the emission limits in Specific Condition III.A.6.  [Rules 62-210.300(2)(a) and 62-297.310(8)(b), F.A.C.]

Recordkeeping and Reporting Requirements

III.A.33 Reporting Schedule.  The following reports and notifications shall be submitted to the Compliance Authority:

| Report | Reporting Deadline | Related Condition(s) |
| --- | --- | --- |
| Pump Engines/Generators (Permit Deviations) | Immediately upon occurrence (See RR2.d.) | RR2, RR3 |
| Semi-annual Title V Monitoring report | Every 6 months | RR4 |
| Semi-annual Title V NESHAP Compliance Report | Every 6 months | III.A.27 |
| Annual Operating Report | April 1 | RR5 |
| Annual Emissions Fee Form and Fee | April 1 | RR6 |
| Annual Statement of Compliance | Within 60 days after the end of each calendar year. | RR7 |

[Rule 62-213.440(1)(b), F.A.C.]

III.A.34 Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440(1)(b), F.A.C.]

Subsection B.  This portion of the permit addresses the following group of emissions units:

| EU ID No. | Status | Emissions Unit Description |  |
| --- | --- | --- | --- |
| 007 | Regulated | Two 685-BHP Cummins emergency power generators (Serial No. 37205673 and 37205672) |

Each generator is powered by a 685-BHP Cummins engine firing low sulfur distillate oil.  These generators were manufactured in 2002, and hence are not subject to 40 CFR part 60 Subpart IIII “Standards of Performance for Stationary Compression Ignition Internal Combustion Engines.”

The following specific conditions apply to the emissions unit(s) listed above:

Operating Restrictions

{Permitting note(s): Those operating restrictions which are identified as “Not Federally Enforceable” have been included for the purposes of local regulations, compliance testing, establishing appropriate emission limitations and to aid in determining future rule applicability.}

III.B.1.	Compliance Date:  The permittee shall comply with the applicable emission limitations and operating limitations of 40 CFR Part 63 Subpart ZZZZ. [40 CFR 63.6595(a)(1)]

Emissions Limitations and Standards

III.B.2.	Emission Limitations:  The permittee shall meet the following requirement, except during periods of startup:

- Change oil and filter every 500 hours of operation or annually, whichever comes first;

- Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first; and

- Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary.

{Permitting note(s): If an emergency engine is operating during an emergency and it is not possible to shut down the engine in order to perform the management practice shown above, or if performing the management practice on the required schedule would otherwise pose an unacceptable risk under Federal, State, or local law, the management practice can be delayed until the emergency is over or the unacceptable risk under Federal, State, or local law has abated. The management practice should be performed as soon as practicable after the emergency has ended or the unacceptable risk under Federal, State, or local law has abated. Sources must report any failure to perform the management practice on the schedule required and the Federal, State or local law under which the risk was deemed unacceptable.}

[40 CFR 63.6603(a), Table 2d to Subpart ZZZZ of Part 63]

III.B.3.	The permittee has the option to utilize an oil analysis program as described herein in order to extend the specified oil change requirement in the Specific Condition III.B.2.(a) of this permit. The oil analysis must be performed at the same frequency specified for changing the oil in this permit. The analysis program must at a minimum analyze the following three parameters: Total Base Number, viscosity, and percent water content. The condemning limits for these parameters are as follows: Total Base Number is less than 30 percent of the Total Base Number of the oil when new; viscosity of the oil has changed by more than 20 percent from the viscosity of the oil when new; or percent water content (by volume) is greater than 0.5. If all of these condemning limits are not exceeded, the permittee is not required to change the oil. If any of the limits are exceeded, the permittee must change the oil within 2 days of receiving the results of the analysis; if the engine is not in operation when the results of the analysis are received, the permittee must change the oil within 2 days or before commencing operation, whichever is later. The permittee must keep records of the parameters that are analyzed as part of the program, the results of the analysis, and the oil changes for the engine. The analysis program must be part of the maintenance plan for the engine.  [40 CFR 63.6625(i)]

Monitoring, Installation, Collection, Operation and Maintenance Requirements

III.B.4.	The permittee shall develop a maintenance plan which shall provide to the extent practicable for the maintenance and operation of the engine in a manner consistent with good air pollution control practice for minimizing emissions. [40 CFR 63.6625(e)]

III.B.5. 	The permittee shall install a non-resettable hour meter if one is not already installed. [40 CFR 63.6625(f)]

III.B.6.	 The permittee shall minimize the engine's time spent at idle during startup and minimize the engine's startup time to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes, after which time the emission standards applicable to all times other than startup as specified in the Specific Condition III.B.2 of this permit. [40 CFR 63.6625(h)]

Continuous Compliance

III.B.7. 	The permittee shall be in compliance with the emissions limitation as required in the Specific Condition III.B.2 at all times. [40 CFR 63.6605 (a)]

III.B.8. 	At all times the permittee shall operate and maintain any affected source, including associated air pollution control equipment and monitoring equipment, in a manner consistent with safety and good air pollution control practices for minimizing emissions. The general duty to minimize emissions does not require the permittee to make any further efforts to reduce emissions if levels required by this standard have been achieved. Determination of whether such operation and maintenance procedures are being used will be based on information available to the Administrator which may include, but is not limited to, monitoring results, review of operation and maintenance procedures, review of operation and maintenance records, and inspection of the source.  [40 CFR 63.6605 (b)]

III.B.9.	The Permittee shall operate the emergency stationary Reciprocating Internal Combustion Engine (RICE) according to the requirements in paragraphs (a) through (c) of this specific condition. Any operation other than emergency operation, maintenance and testing, and operation in non-emergency situations for 50 hours per year, as described in paragraphs (a) through (c) of this specific condition, is prohibited. If the permittee does not operate the engine according to the requirements in paragraphs (a) through (c) of this specific condition, the engine will not be considered an emergency engine under this subpart and will need to meet all requirements for non-emergency engines.

(a)      There is no time limit on the use of emergency stationary RICE in emergency situations.

(b) 	The permittee may operate the emergency stationary RICE for the purpose of maintenance checks and readiness testing, provided that the tests are recommended by Federal, State or local government, the manufacturer, the vendor, or the insurance company associated with the engine. Maintenance checks and readiness testing of such units is limited to 100 hours per year. The permittee may petition the PBCHD for approval of additional hours to be used for maintenance checks and readiness testing, but a petition is not required if the permittee maintains records indicating that Federal, State, or local standards require maintenance and testing of emergency RICE beyond 100 hours per year.

(c) 	The permittee may operate the emergency stationary RICE up to 50 hours per year in non-emergency situations, but those 50 hours are counted towards the 100 hours per year provided for maintenance and testing. The 50 hours per year for non-emergency situations cannot be used for peak shaving or to generate income for a facility to supply power to an electric grid or otherwise supply power as part of a financial arrangement with another entity; except that the permittee may operate the emergency engine for a maximum of 15 hours per year as part of a demand response program if the regional transmission organization or equivalent balancing authority and transmission operator has determined there are emergency conditions that could lead to a potential electrical blackout, such as unusually low frequency, equipment overload, capacity or energy deficiency, or unacceptable voltage level. The engine may not be operated for more than 30 minutes prior to the time when the emergency condition is expected to occur, and the engine operation must be terminated immediately after the facility is notified that the emergency condition is no longer imminent. The 15 hours per year of demand response operation are counted as part of the 50 hours of operation per year provided for non-emergency situations. The supply of emergency power to another entity or entities pursuant to financial arrangement is not limited by this paragraph (c), as long as the power provided by the financial arrangement is limited to emergency power.[40 CFR 63.6640 (f)(1),(2)(i),(3) and (4)]

III.B.10.	The permittee shall report each instance in which the emissions unit did not meet each emission limitation or operating limitation specified in the permit. These instances are deviations from the emission and operating limitations specified in the permit. These deviations must be reported according to the requirements in the Specific Condition III.B.11. If the permittee changes the catalyst, the permittee shall reestablish the values of the operating parameters measured during the initial performance test. When reestablishing the values of the operating parameters, the permittee shall also conduct a performance test to demonstrate that the emissions unit is meeting the required emission limitation.  [40 CFR 63.6640 (b)]

Reporting And Recordkeeping Requirements

III.B.11.	The permittee shall maintain the recordkeeping for the following items listed below. The recordkeeping shall be maintained in a form suitable and readily available for expeditious inspection and review for the followings. The files shall be retained for at least 5 years following the date of each occurrence, measurement, maintenance, corrective action, report of record. At a minimum, the most recent 2 years of data shall be retained on site. The remaining 3 years of data may be retained off site.  Such files may be maintained on microfilm, on a computer, on computer floppy disks, on magnetic tape disks, or on microfiche.

- Records of the occurrence and duration of each malfunction of operation (i.e., process equipment) or the air pollution control and monitoring equipment. [40 CFR 63.6655(a)(2)]

- Records of all required maintenance performed on the air pollution control and monitoring equipment. [40 CFR 63.6655(a)(4)]

- Records of actions taken during periods of malfunction to minimize emissions in accordance with Specific Condition III.B.10, including corrective actions to restore malfunctioning process and air pollution control and monitoring equipment to its normal or usual manner of operation. . [40 CFR 63.6655(a)(5)]

III.B.12.	The permittee shall keep records of the maintenance conducted on the stationary RICE in order to demonstrate that the permittee operated and maintained the stationary RICE and after-treatment control device (if any) according to the maintenance plan. [40 CFR 63.6655(e)]

III. B.13.	The permittee shall keep records of the hours of operation of the engine that is recorded through the non-resettable hour meter. The permittee must document how many hours are spent for emergency operation, including what classified the operation as emergency and how many hours are spent for non-emergency operation. If the engines are used for demand response operation, the permittee must keep records of the notification of the emergency situation, and the time the engine was operated as part of demand response. [40 CFR 63.6655(f)]

III. B.14.	The permittee shall keep records of the amount of fuel consumed by the generators on a monthly basis. The permittee shall follow the frequency of maintaining the fuel consumption records as required in the specific condition III.A.25 of this permit. The permittee shall take the fuel consumed by the generators into account in demonstrating compliance with the facility wide condition FW11 of this permit. [Rule 62-4.070(3), F.A.C.]

Appendix A, ABBREVIATIONS, ACRONYMS, CITATIONS AND IDENTIFICATION NUMBERS.

Appendix I, List of Insignificant Emissions Units and/or Activities.

Appendix NESHAP, Subpart A – General Provisions. (Include for all units that are subject to a NESHAP)

Appendix ZZZZ, “National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines (RICE)” Appendix RR, Facility-wide Reporting Requirements.

Appendix TR, Facility-wide Testing Requirements.

Appendix RR, Facility-wide Reporting Requirements

Appendix TV, Title V General Conditions.