Permittee

| Duke Energy Florida, Inc. University of Florida Cogeneration Plant 1928 Mowery Road, Building 82 Gainesville, FL 32611-2295 Authorized Representative: Brian V. Powers, Station Manager | Air Permit No. 0010001-014-AC PSD-181C University of Florida Cogeneration Plant Facility ID No. 0010001 Boiler Replacement Project |
| --- | --- |

Project

This is the final permit authorizing the construction of a new steam boiler to replace the existing Boiler No. 4 (EU 002) at the UF Cogeneration (CoGen) Plant.  The new boiler will support the steam load requirements of the UF.  The UF CoGen Plant address is 1928 Mowry Road, Building 82, Gainesville, Florida 32611.  The UTM coordinates are Zone 17, 369.39 kilometers (km) East, and 3279.29 km North.  The facility is an electrical power generating plant with a Standard Industrial Classification Code (SIC) of No. 4911.

This final permit is organized into the following sections:  Section 1 (General Information); Section 2 (Administrative Requirements); Section 3 (Emissions Unit Specific Conditions); Section 4 (Appendices).  Because of the technical nature of the project, the permit contains numerous acronyms and abbreviations, which are defined in Appendix A of Section 4 of this permit.  As noted in the Final Determination provided with this final permit, only minor changes and clarifications were made to the draft permit.

Statement of Basis

This air pollution construction permit is issued under the provisions of:  Chapter 403 of the Florida Statutes (F.S.) and Chapters 62-4, 62-204, 62-210, 62-212, 62-296 and 62-297 of the Florida Administrative Code (F.A.C.).  The permittee is authorized to conduct the proposed work in accordance with the conditions of this permit.  This project is subject to the general preconstruction review requirements in Rule 62-212.300, F.A.C. and the preconstruction review requirements for major stationary sources in Rule 62-212.400, F.A.C. for the Prevention of Significant Deterioration (PSD) of Air Quality.

Upon issuance of this final permit, any party to this order has the right to seek judicial review of it under Section 120.68 of the Florida Statutes by filing a notice of appeal under Rule 9.110 of the Florida Rules of Appellate Procedure with the clerk of the Department of Environmental Protection in the Office of General Counsel (Mail Station #35, 3900 Commonwealth Boulevard, Tallahassee, Florida, 32399-3000) and by filing a copy of the notice of appeal accompanied by the applicable filing fees with the appropriate District Court of Appeal.  The notice must be filed within 30 days after this order is filed with the clerk of the Department.

Executed in Tallahassee, Florida

(DRAFT)

for:	Jeffery F. Koerner, Program Administrator

Office of Permitting and Compliance

Division of Air Resource Management

## CERTIFICATE OF SERVICE

The undersigned duly designated deputy agency clerk hereby certifies that this final air permit package (including the Final Determination and Final Permit with Appendices) was sent by electronic mail, or a link to these documents made available electronically on a publicly accessible server, with received receipt requested before the close of business on the date indicated below to the following persons.

# Mr. Brian V. Powers, Duke Energy Florida, Inc.: Brian.Powers@duke-energy.com

# Mr. Chris Bradley, Duke Energy Florida, Inc.:  Chris.Bradley@duke-energy.com

# Mr. Scott Osbourn, PE, Golder Associates:  scott_osbourn@golder.com

# Mr. Richard Rachal, Northeast District Office:  Richard.Rachal@dep.state.fl.us

# Ms. Kathleen Forney, EPA Region 4:  forney.kathleen@epa.gov

Ms. Lynn Scearce, DEP:  lynn.scearce@dep.state.fl.us

# Clerk Stamp

# FILING AND ACKNOWLEDGMENT FILED, on this date, pursuant to Section 120.52(7), Florida Statutes, with the designated agency clerk, receipt of which is hereby acknowledged.

(DRAFT)

Facility and Project Description

Existing Facility

The UF CoGen Plant consists of one nominal 48 megawatt General Electric LM6000-PC-ESPRINT Combustion Turbine (CT) with one Heat Recovery Steam Generator (HRSG) and Duct Burner (DB) system comprising a combined cycle unit.  In addition, there are two Backup Steam Boilers.  The CT uses spray inter-cooling to maximize power generation and reduce the need for supplemental firing of the DB system to meet steam and power requirements.  Emissions from the CT and DB system are vented through the HRSG stack.  Emissions of nitrogen oxides (NOX) are controlled with steam injection and compliance is demonstrated by data collected from a continuous emissions monitoring system (CEMS).  Each backup steam boiler has a separate exhaust stack and is used only as a backup source of steam when the combined cycle system is not available or to provide supplemental steam during periods of high steam demand.

A summary of the regulated existing emission units and corresponding emissions unit identification numbers (E.U. ID No.) within the Department’s Air Resource Management System (ARMS) at the UF CoGen Plant is given below.  The emission unit affected by this permitting action is highlighted in turquoise in the table.

| Facility ID No. 0010001 |  |
| --- | --- |
| EU ID No. | Emission Unit Description |  |
| 002 | No. 4 Backup Steam Boiler (to be replaced) |  |
| 003 | No. 5 Backup Steam Boiler |  |
| 005 | Heat Recovery Steam Generator with Duct Burner System |  |
| 007 | Combustion Turbine, General Electric Model No. LM6000-PC-ESPRINT |  |

Proposed Project

This project involves the construction of a new steam boiler to replace the existing Backup Steam Boiler No. 4 (EU 002) at the UF CoGen Plant.  The new boiler will support the steam load requirements of the UF when the combined cycle system in not available or to provide supplemental steam during periods of high steam demand.  UF is planning to replace Boiler No. 4, which is permitted at 69.6 million British thermal units per hour (MMBtu/hr) and 40,000 pounds per hour (lb/hr) of steam, with the new boiler with a heat input of 99.9 MMBtu/hr and capacity to produce approximately 78,500 lb/hr of steam.  UF will purchase and install the boiler, which is proposed to be a Cleaver Brooks Company model NB-300D-70, and Duke Energy Florida (DEF) will operate the boiler.

The new emission unit resulting from this project will be assigned the following E.U. ID No. within the Department’s ARMS:

| New EU ID No. | Description |
| --- | --- |
| 008 | New Backup Steam Boiler No. 6 - Heat Input: 99.9 MMBtu/hr - Steam Generation: 78,500 lb/hr |

Facility Regulatory Classification

- The facility is not a major source of hazardous air pollutants (HAP).

- The facility has units subject to the acid rain provisions of the Clean Air Act.

- The facility is a Title V major source of air pollution in accordance with Chapter 62-213, F.A.C.

- The facility is a major stationary source in accordance with Rule 62-212.400, F.A.C. for the Prevention of Significant Deterioration (PSD) of Air Quality.

- This project (as discussed below) does not trigger a PSD review and a requirement to conduct Best Available Control Technology (BACT) determinations pursuant to Department Rule 62-212.400, F.A.C.

- The proposed project includes units subject to Clean Air Interstate Rule (CAIR).

- The proposed project includes units subject to the New Source Performance Standards (NSPS) of Title 40 Code of Federal Regulations (CFR) Part 60.

- The proposed project includes units subject to the National Emission Standards for Hazardous Air Pollutants (NESHAP) of 40 CFR 63.

Changes are highlighted in yellow with additions denoted with double-underline and deletions denoted with strikethrough.

- Permitting Authority:  The Permitting Authority for this project is the Office of Permitting and Compliance (OPC) in the Division of Air Resource Management of the Department.  The mailing address for the OPC is 2600 Blair Stone Road, MS #5505, Tallahassee, Florida  32399-2400.  All documents related to applications for permits to operate an emissions unit shall be submitted to the OPC Section.

- Compliance Authority:  All documents related to compliance activities such as reports, tests and notifications shall be submitted to the Northeast District Office.  The mailing address and phone number of the Northeast District Office is:  8800 Baymeadows Way West, Suite 100, Jacksonville, Florida 32256-7590, (904) 256-1700.

- Appendices:  The following Appendices are attached as part of this permit:

- Appendix A.  Citation Formats and Glossary of Common Terms;

- Appendix B.  General Conditions;

- Appendix C.  Common Conditions;

- Appendix D.  Common Testing Requirements;

- Appendix Subpart A.  NSPS Subpart A and NESHAP Subpart A - Identification of General Provisions;

- Appendix Dc.  NSPS 40 CFR Part 60 - Subpart Dc - Standards of Performance for Small Industrial-Commercial-Institutional Steam Generating Units; and

- Appendix GG.  NSPS 40 CFR 60, Subpart GG - Standards of Performance for Industrial-Commercial-Institutional Steam Generating Units.

- Applicable Regulations, Forms and Application Procedures:  Unless otherwise specified in this permit, the construction and operation of the subject emissions units shall be in accordance with the capacities and specifications stated in the application.  The facility is subject to all applicable provisions of: Chapter 403, F.S.; and Chapters 62-4, 62-204, 62-210, 62-212, 62-213, 62-296 and 62-297, F.A.C.  Issuance of this permit does not relieve the permittee from compliance with any applicable federal, state, or local permitting or regulations.

- New or Additional Conditions:  For good cause shown and after notice and an administrative hearing, if requested, the Department may require the permittee to conform to new or additional conditions.  The Department shall allow the permittee a reasonable time to conform to the new or additional conditions, and on application of the permittee, the Department may grant additional time.  [Rule 62-4.080, F.A.C.]

- Modifications:  The permittee shall notify the Compliance Authority upon commencement of construction.  No new emissions unit shall be constructed and no existing emissions unit shall be modified without obtaining an air construction permit from the Department.  Such permit shall be obtained prior to beginning construction or modification.  
[Rules 62-210.300(1) and 62-212.300(1)(a), F.A.C.]

- Construction and Expiration:  The permit expiration date includes sufficient time to complete construction, perform required testing, submit test reports, and submit an application for a Title V operation permit to the Department.  For good cause, the permittee may request that this air construction permit be extended.  Such a request shall be submitted to the Office of Permitting and Compliance at least sixty (60) days prior to the expiration of this permit.  [Rules 62-4.070(4), 62-4.080, and 62-210.300(1), F.A.C.]

- Source Obligation:

a.	Authorization to construct shall expire if construction is not commenced within 18 months after receipt of the permit, if construction is discontinued for a period of 18 months or more, or if construction is not completed within a reasonable time.  This provision does not apply to the time period between construction of the approved phases of a phased construction project except that each phase must commence construction within 18 months of the commencement date established by the Department in the permit.

b.	At such time that a particular source or modification becomes a major stationary source or major modification (as these terms were defined at the time the source obtained the enforceable limitation) solely by virtue of a relaxation in any enforceable limitation which was established after August 7, 1980, on the capacity of the source or modification otherwise to emit a pollutant, such as a restriction on hours of operation, then the requirements of subsections 62-212.400(4) through (12), F.A.C., shall apply to the source or modification as though construction had not yet commenced on the source or modification.

c.	At such time that a particular source or modification becomes a major stationary source or major modification (as these terms were defined at the time the source obtained the enforceable limitation) solely by exceeding its projected actual emissions, then the requirements of subsections 62-212.400(4) through (12), F.A.C., shall apply to the source or modification as though construction had not yet commenced on the source or modification.

[Rule 62-212.400(12), F.A.C.]

- Title V Permit:  This permit authorizes specific modifications and/or new construction on the affected emissions units as well as initial operation to determine compliance with conditions of this permit.  A Title V operation permit is required for regular operation of the permitted emissions unit.  The permittee shall apply for a Title V operation permit at least 90 days prior to expiration of this permit, but no later than 180 days after completing the required work and commencing operation.  To apply for a Title V operation permit, the applicant shall submit the appropriate application form, compliance test results, and such additional information as the Department may by law require.  The application shall be submitted to the appropriate Permitting Authority with copies to each Compliance Authority.  
[Rules 62-4.030, 62-4.050, 62-4.220, and Chapter 62-213, F.A.C.]

- Annual Operating Report (AOR):  The owner or operator shall submit an AOR for the Air Pollutant Emitting Facility (DEP Form No. 62-210.900(5)) to the Department annually pursuant to subsection 62-210.370(3), F.A.C.

- Shutdown of Existing Backup Steam Boiler No. 4:  Upon commercial operation of the new Backup Steam Boiler No. 6 (EU 008), the existing Backup Steam Boiler No. 4 shall no longer be used to provide steam generation to the UF.   [Application 0010001-014; Rules 62-210.200 (Potential to emit) and 62-4.030, F.A.C.]

- Permitting Authority:  The permitting authority for this project is the Air Permitting and Compliance Section, Division of Air Resource Management, Florida Department of Environmental Protection (Department) at:  2600 Blair Stone Road (MS #5505), Tallahassee, Florida  32399-2400.  All documents related to applications for permits to operate an emissions unit shall be submitted to the Air Resource Section of the Northeast District (as applicable) at:  7825 Baymeadows Way, Suite 200B, Jacksonville, Florida  32256-7590.

- Compliance Authority:  All documents related to compliance activities such as reports, tests, and notifications shall be submitted to the Air Resource Section of the Northeast District (as applicable) at:  7825 Baymeadows Way, Suite 200B, Jacksonville, Florida  32256-7590.

- Appendices:  The following Appendices are attached as a part of this permit:  Appendix A (Citation Formats and Glossary of Common Terms); Appendix B (General Conditions); Appendix C (Common Conditions); Appendix D (Common Testing Requirements); Appendix E (Final BACT Determinations); and Appendix F (Heat Input Rate vs. Compressor Inlet Temperature).

- Applicable Regulations, Forms and Application Procedures:  Unless otherwise specified in this permit, the construction and operation of the subject emissions units shall be in accordance with the capacities and specifications stated in the application.  The facility is subject to all applicable provisions of: Chapter 403, F.S.; and Chapters 62-4, 62-204, 62-210, 62-212, 62-296 and 62-297, F.A.C.  Issuance of this permit does not relieve the permittee from compliance with any applicable federal, state, or local permitting or regulations.

- New or Additional Conditions:  For good cause shown and after notice and an administrative hearing, if requested, the Department may require the permittee to conform to new or additional conditions.  The Department shall allow the permittee a reasonable time to conform to the new or additional conditions, and on application of the permittee, the Department may grant additional time.  [Rule 62-4.080, F.A.C.]

- Modifications:  No emissions unit shall be constructed or modified without obtaining an air construction permit from the Department.  Such permit shall be obtained prior to beginning construction or modification.  [Rules 62-210.300(1) and 62-212.300(1)(a), F.A.C.]

- Source Obligation:

(a)	At such time that a particular source or modification becomes a major stationary source or major modification (as these terms were defined at the time the source obtained the enforceable limitation) solely by virtue of a relaxation in any enforceable limitation which was established after August 7, 1980, on the capacity of the source or modification otherwise to emit a pollutant, such as a restriction on hours of operation, then the requirements of subsections 62-212.400(4) through (12), F.A.C., shall apply to the source or modification as though construction had not yet commenced on the source or modification. [Rule 62-212.400(12)(b), F.A.C.]

(b)	At such time that a particular source or modification becomes a major stationary source or major modification (as these terms were defined at the time the source obtained the enforceable limitation) solely by exceeding its projected actual emissions, then the requirements of subsections 62-212.400(4) through (12), F.A.C., shall apply to the source or modification as though construction had not yet commenced on the source or modification.  [Rule 62-212.400(12)(c), F.A.C.]

- Title V Permit:  This permit authorizes specific modifications and/or new construction on the affected emissions units as well as initial operation to determine compliance with conditions of this permit.  A Title V operation permit is required for regular operation of the permitted emissions unit.  The permittee shall apply for a Title V operation permit within 180 days of issuance of this final air construction permit revision.  To apply for a Title V operation permit, the applicant shall submit the appropriate application form, compliance test results, and such additional information as the Department may by law require.  The application shall be submitted to the appropriate Permitting Authority with copies to each Compliance Authority.  [Rules 62-4.030, 62-4.050, 62-4.220, and Chapter 62-213, F.A.C.]

- Actual Emissions Reporting:  This permit is based on an analysis that compared baseline actual emissions with projected actual emissions and avoided the PSD preconstruction review requirements of Rule 62-212.400(4) through (12), F.A.C. for several pollutants.  Therefore, pursuant to Rule 62-212.300(1)(e), F.A.C., the permittee is subject to the following monitoring, reporting and recordkeeping provisions.

- The permittee shall monitor the emissions of any PSD pollutant that the Department identifies could increase as a result of the construction or modification and that is emitted by any emissions unit that could be affected; and, using the most reliable information available, calculate and maintain a record of the annual emissions, in tons per year on a calendar year basis, for a period of 10years following resumption of regular operations after the change.  Emissions shall be computed in accordance with the provisions in Rule 62-210.370, F.A.C., which are provided in Appendix C of this permit.

- The permittee shall report to the Department within 60 days after the end of each calendar year during the 10-year period setting out the unit’s annual emissions during the calendar year that preceded submission of the report.  The report shall contain the following:

  - The name, address and telephone number of the owner or operator of the major stationary source;

  - The annual emissions calculations pursuant to the provisions of 62-210.370, F.A.C., which are provided in Appendix C of this permit;

  - If the emissions differ from the preconstruction projection, an explanation as to why there is a difference; and

  - Any other information that the owner or operator wishes to include in the report.

- The information required to be documented and maintained pursuant to subparagraphs 62-212.300(1)(e)1 and 2, F.A.C., shall be submitted to the Department, which shall make it available for review to the general public.

For this project, the permit requires the annual reporting of actual 2011 NOx emissions from the combustion turbine and duct burner system.  {Permitting Note:  The baseline NOx emissions are 114.50 tons/year for the combustion turbine and duct burner combined, resulting is a PSD applicability trigger threshold of 154.50 tons/year (114.50+40=154.50). The two calendar years used to establish the 114.50 tons/year baseline were 2000 and 2001.  The permittee has already report nine years of this data.}

[Rules 62-212.300(1)(e) and 62-210.370, F.A.C.]

This section of the permit addresses the following emissions units.

| ID No. | Emission Unit Description |
| --- | --- |
| 002 | No. 4 Backup Steam Boiler |
| 003 | No. 5 Backup Steam Boiler |
| 005 | Heat Recovery Steam Generator with Duct Burner System |
| 007 | Combustion Turbine, General Electric Model No. LM6000-PC-ESPRINT |
| 008 | New Backup Steam Boiler No. 6 |

The steam boilers (EU-002 and 003 and 008) are to be used only as back-up sources of steam or to provide supplemental steam during periods of high steam demand.  Each boiler will/or has its own exhaust stack.  The maximum design heat input rate for the No. 4 steam boiler is 69.6 million British thermal units per hour (MMBtu/hour) based on firing 68,000 cubic feet of natural gas per hour and 444 gallons per hour of No. 2 fuel oil.  The maximum design heat input rate for the No. 5 steam boiler is 168 MMBtu/hour based on firing 164,000 cubic feet of natural gas per hour and 1,067 gallons per hour of No. 2 fuel oil.  The No. 4 steam boiler has a stack height of 82 feet, exit diameter of 5 feet, exit temperature of 350°F and an actual volumetric flow rate of 13,500 actual cubic feet per minute (acfm).  The No. 5 steam boiler has a stack height of 82 feet, exit diameter of 6 feet, exit temperature of 400 °F and actual volumetric flow rate of 56,250 acfm.  The backup steam boilers are regulated under this permit and Rule 62-296.406, F.A.C., Fossil Fuel Steam Generators with Less than 250 MMBtu per Hour Heat Input.  The steam boilers No. 5 began commercial service in January 1976.

The combined cycle system (EU-005 and 007) consists of a nominal 48 MW CT combustion turbine and a HRSG with a DB system. heat recovery steam generator with duct burner.  The CT combustion turbine is fired with natural gas and utilizes spray inter-cooling to maximize power output, which reduces the need for supplemental firing of the DB system in the duct burner to meet steam and power requirements.  Steam injection is used to control NOX emissions from the combustion turbine.  The DB system duct burner is equipped with low-NOX burners to control NOX emissions while firing natural gas.  Exhaust gas from the combined cycle system exits the HRSG heat recovery steam generator stack at a height of 93 feet, exit diameter of 9.8 feet, exit temperature of 257°F and actual volumetric flow rate of 365,700 acfm, (based on the CT combustion turbine only at a compressor inlet temperature of 59 °F, 60% relative humidity at inlet, maximum dry standard flow rate of 216,956 dscfm and exit velocity of 80.8 feet per second.  Originally, a 43 MW CT combustion turbine (GE LM6000-PA) began commercial service on January 31, 1994.  It was replaced with new 48 MW unit (GE LM6000-PC-ESPRINT) with spray inter-cooling, which began commercial service on September 24, 2002.

{Permitting Note:  This facility was permitted originally in 1992 to provide electrical power and steam for the University of Florida.  The original project (PSD-FL-181) authorized the construction of the cogeneration facility and required the permanent shutdown of Boilers Nos. 1, 2 and 3.  In accordance with Rule 62-212.400(PSD), F.A.C., the above emission units are subject to Best Available Control Technology (BACT) determinations for carbon monoxide (CO).  The final BACT determinations are presented in Appendix E of this permit.}

Other Permits

- New Permit:  This permit supersedes all previous air construction permits for the specified emissions units at the cogeneration plant.  The conditions of the new permit are based upon Application No. 0010001-0141-AC as well as previous applications for the original Permit No. PSD-FL-181 as well as subsequent modifications and amendments.  [Rule 62-4.070(3), F.A.C]

Shutdown Units

- Shutdown Units:  Boilers 1, 2 and 3 4 shall be permanently shut down as a part of this PSD project.  {Permitting Note:  This requirement of the original permit has been previously satisfied.}  [Rule 62-212.400(12), F.A.C.]

Applicable Standards and Regulations

- NSPS Requirements:  The new backup Steam Boiler No. 6 (EU 008) along with existing emission units shall comply with all applicable requirements in NSPS in 40 CFR 60, Subpart A (General Provisions).  In addition the new boiler shall comply with all applicable requirements of 40 CFR 60, Subpart Dc (Standards of Performance for Small Industrial-Commercial-Institutional Steam Generating Units).  The existing duct burner and HRSG (EU 005) shall comply with all applicable requirements in NSPS 40 CFR 60, Subpart Db (Standards of Performance for Industrial-Commercial-Institutional Steam Generating Units).  The existing CT (EU 007) shall comply with all applicable requirements in NSPS 40 CFR 60, Subpart GG (Standards of Performance for Stationary Gas Turbines).  See Appendices Subpart A, Db, Dc and GG of this permit.  [Rule 62-204.800(7)(b), F.A.C.; and NSPS 40 CFR 60, Subparts A, Db, Dc and GG]

- State Requirements:  The backup steam boilers are regulated under this permit and Rule 62-296.406, F.A.C., Fossil Fuel Steam Generators with Less than 250 MMBtu per Hour Heat Input.  [Rule 62-296.406, F.A.C.]

New Equipment

- New Backup Steam Boiler No. 6 (EU 008):  The permittee is authorized to install, tune, operate, and maintain one Cleaver Brooks Company model NB-300D-7 boiler or other vendor equivalent to provide backup steam to the UF.  The boiler will be designed for dual-fuel capability (natural gas and No. 2 fuel oil with a maximum sulfur content of 0.1%).  The boiler will have a nominal heat input of 99.9 MMBtu/hr based on firing 97,941 cubic feet of natural gas per hour and 723 gallons per hour of No. 2 fuel oil with nominal capacity to produce approximately 78,500 lb/hr of steam.  The new Backup Steam Boiler No. 6 will have a nominal stack height of 82 feet, exit diameter of 5 feet, exit temperature of 302 °F and an actual volumetric flow rate of 28,170 actual cubic feet per minute (acfm).  [Application 0010001-014-AC; Design]

- Boiler Pollution Control Equipment:  The new Backup Steam Boiler No. 6 shall utilize low NOX burners and flue gas recirculation to minimize emission of NOX.  [Application 0010001-014-AC; Design; Rule 62-210.200(PTE), F.A.C.]]

Existing Equipment

- 3  Combined Cycle Combustion Turbine System:  The permittee is authorized to construct, operate and maintain as combined cycle combustion turbine system consisting of a nominal 48 MW combustion turbine (GE LM6000-PC-ESPRINT) and a heat recovery steam generator with duct burner.  The combustion turbine system generally consists of the following components:  gas generator, accessory drive system, air inlet and filtration system, fuel delivery system, cooling system, lubrication system, control system, starting system and exhaust system with stack.  This aero-derivative gas turbine is designed with modular components to facilitate quick repairs.  Common “wear items” include compressor vanes, turbine nozzles, compressor blades, turbine blades, fuel nozzles, combustion chambers, seals, and shaft packing.  The concept of modular design extends to the complete replacement of major components of the gas turbine.  Replacements are authorized provided the following requirements are met.

- The “hot section” components (e.g., combustors and high-speed turbines including blades, nozzles and other components) shall be replaced with equivalent “like-kind” equipment.  Replacement components shall not increase the maximum heat input rate, capacity or emissions from the combustion turbine.  Replacement components shall be designed to achieve and shall achieve the emissions standards specified in this permit or better.

- Within 90 days of replacing a gas turbine, the permittee shall conduct emissions stack tests to demonstrate compliance with the emission standards for CO and visible emissions.  The permittee shall comply with the requirements for notification, test methods, test procedures, and reporting required by this permit.

- To up-rate the gas turbine or increase the maximum heat input rate or capacity, the permittee shall submit an application for an air construction permit.

[Application and Design]

- 4.  Combustion Turbine – Steam Injection:  A steam injection system shall be used installed to reduce NOX emissions from the combustion turbine exhaust.  In accordance with 40 CFR 60.334, the permittee shall install and operate a continuous monitoring system to monitor and record the ratio of steam to fuel being fired in the combustion turbine.  The permittee shall establish the steam-to-fuel ratio that demonstrates compliance with the emissions standards of this permit by correlating with data collected by the NOX CEMS.  When the NOX CEMS is down, the permittee shall operate at a steam-to-fuel injection rate that demonstrates compliance.  [Rule 62-4.070(3), F.A.C. and NSPS Subpart GG in 40 CFR 60]

- 5.  Existing Backup Steam Boilers No. 5:  The permittee is authorized to operate and maintain Backup Steam Boilers Nos. 4 and 5 to provide a source of steam in case the combustion turbine is unavailable or to provide supplemental steam during periods of high steam demand.  [Application and Design]

Performance Restrictions

- 6.  Permitted Capacities:

- Combustion Turbine:  The heat input to the combustion turbine shall not exceed the values defined by the manufacturer’s performance curve of heat input rate vs. compressor inlet temperature.  The maximum heat input limits are based on the lower heating value (LHV) of natural gas, 100% load and ambient conditions of 60% relative humidity and 14.7 psia.  The maximum heat input rates will vary depending upon ambient conditions, the combustion turbine characteristics and the demand.  {Permitting Note:  The maximum design heat input rate to the combustion turbine is 480 MMBtu/hour for a compressor inlet temperature of 59 °F.}

- Duct Burner:  The maximum design heat input to the duct burner system is 188 MMBtu/hour of natural gas.  The duct burner shall not fire more than 519.5 million ft3/year of natural gas based on the lower heating value (LHV) of 950 Btu/ft3.

- Backup Steam Boilers No. 5:  When either firing natural gas or No. 2 fuel oil, the maximum design heat input rate for the No. 4 steam boiler is 69.6 MMBtu/hour (equivalent to 68,000 cubic feet of natural gas per hour or 444 gallons per hour of No. 2 fuel oil).  When either firing natural gas or No. 2 fuel oil, the maximum design heat input rate for the No. 5 steam boiler is 168 MMBtu/hour (equivalent to 164,000 cubic feet of natural gas per hour or 1067 gallons per hour of No. 2 fuel oil).

[Application, Design and Rule 62-210.200(PTE), F.A.C.]

- 7. Authorized Fuels:  The combustion turbine, HRSG, duct burners and backup steam boilers are authorized to fire natural gas with a maximum sulfur content of 2 grains of sulfur per 100 scf of natural gas (annual average based on vendor data).  The backup steam boilers No. 5 is are authorized to fire No. 2 fuel oil with a maximum sulfur content of 0.5% by weight while backup steam boiler No. 6 is are authorized to fire No. 2 fuel oil with a maximum sulfur content of 0.1% by weight (annual average based on vendor data). [Rules 62-210.200(PTE), 62-212.400(12), 62-296.406, F.A.C., and 40 CFR 60.333(b)]

- 8.  Restricted Operation CT and Backup Steam Boiler No. 5:  The hours of operation for the CT and Backup Steam Boiler No. 5 equipment authorized by this permit are not limited (8,760 hours per year).  [Rules 62-4.070(3) and 62-210.200(PTE), F.A.C.]

- Restricted Operation New Backup Boiler No. 6:  The hours of operation while firing natural gas in Backup Steam Boiler No. 6 is not limited (8,760 hours per year).  When natural gas is available, backup boiler No. 6 is limited to firing fuel oil to no more than a combined total of 48 hours during any calendar year except during periods of natural gas supply curtailment or interruption.  [Rules 62-4.070(3) and 62-210.200(PTE), F.A.C; NESHAP 40 CFR 63, Subpart JJJJJJ.]

- Gas Curtailment:  During times of gas curtailment, the new backup boiler No. 6 may fire fuel oil for the number of operational hours determined by the below equations.  Because the UF CoGen site is supplied by a single natural gas pipeline examples of periods of gas interruptions include, pressure testing of the gas supply pipeline, maintenance and repair of gas valves and gas leak repair.  [Rules 62-4.070(3) and 62-210.200(PTE), F.A.C; NESHAP 40 CFR 63, Subpart JJJJJJ.]

##### Allowable Hoursoil firing=80,600-3.64 x Hours firing natural gas 12.6             EQ. 1*

8,760hoursyear≥Hours firing natural gas+Allowable Hoursoil firing    EQ. 2*

185.3 NOX tonsyear≥ CT**NOXtonsyear+Boiler No. 5NOXtonsyear+Boiler No. 6NOXtonsyear EQ. 3 *

*   Annual NOX emissions from the backup steam boilers shall be determined based on the annual fuel consumption rates and the appropriate NOx emissions factors (see Specific Condition 29 of this subsection).

**  CT emissions include emissions from the duct burner system and shall be determined by data collected from the NOX CEMS (see Specific Condition 29 of this subsection).

##### Emissions Standards

- 9.  Emissions Standards – Combined Cycle Combustion Turbine with Duct Burner:

### Carbon Monoxide (CO) Emissions:

(1)	As determined by EPA Method 10, CO emissions from the combustion turbine shall not exceed 36.0 ppmvd corrected to 15% oxygen.  {Permitting Note:  This is equivalent to 35.8 lb/hour at a compressor inlet temperature of 59 °F.}

(2)	As determined by EPA Method 10, CO emissions from the duct burner shall not exceed 0.15 lb/MMBtu and 28.1 lb/hour.

[Rule 62-212.400(BACT), F.A.C.]

### Nitrogen Oxides (NOX) Emissions:

- As determined by CEMS, NOX emissions from the combustion turbine shall not exceed 39.6 lb/hour with the duct burner “off” and 58.3 lb/hour with the duct burner “on”, based on 30-day rolling averages.  {Permitting Note:  The basis for the NOX limit on the combustion turbine is 25 ppmvd corrected to 15% oxygen as provided by the vendor.}  [PSD avoidance pursuant to Rule 62-212.400(12), F.A.C.]

- As determined by CEMS, NOX emissions from the combustion turbine shall not exceed the applicable NSPS emissions standard in 40 CFR 60.332:

(14.4)

STD = 75 ppmvd corrected to 15% oxygen ------------ = 123 ppmvd corrected to 15% oxygen

(8.8)

where:

STD = allowable NOX emissions standard corrected to ISO conditions based on a 4-hour rolling CEMS average [40 CFR 60.334]

Y = 8.8 kilojoules per watt hour (kJ/W-hr) based on 950 Btu/SCF (LHV) for natural gas, which is the manufacturer’s rated heat rate at manufacturer's rated load (kilojoules per watt-hour) or, actual measured heat rate based on lower heating value of fuel as measured at actual peak load for the facility.  The value of Y shall not exceed 14.4 kJ/W-hr.

There is no NOX emission allowance for fuel-bound nitrogen for natural gas.

[40 CFR 60.334]

- As determined by CEMS data pursuant to 40 CFR 60.46b, NOX emissions from the duct burner shall not exceed 0.1 lb/MMBtu and 18.7 lb/hour based on 30-day rolling average.  [40 CFR 60.44b and original Permit No. PSD-FL-181]

### Sulfur Dioxide (SO2) Emissions:  SO2 emissions from the combustion turbine shall be controlled by firing natural gas with a maximum sulfur content of 2 grains of sulfur per 100 standard cubic feet of natural gas.  This condition also ensures that the fuel contains less than 0.8% by weight pursuant to 40 CFR 60.333(b).  [Rules 62-212.400(12) and 40 CFR 60.333]

### Visible Emissions:  As determined by EPA Method 9, visible emissions shall not exceed 10% opacity from the combustion turbine with or without the duct burner in operation.  [Rule 62-4.070(3), F.A.C.]

- 10.  Emissions Standards – Backup Steam Boilers No. 5:  To control PM and SO2 emissions, the backup steam boilers No. 5 shall fire only natural gas or No. 2 fuel oil with a maximum sulfur content of 0.5%.  As determined by EPA Method 9, visible emissions when firing any authorized fuel shall not exceed 20% opacity except for one, 6-minute block average per hour not to exceed 27% opacity.
[Rule 62-296.406(BACT) and 62-296.406, F.A.C.]

- Emission Standards – Backup Steam Boiler No. 6:  Backup Steam Boiler No. 6 shall meet the following emission limits:

| Pollutant | Fuel 1 | lb/MMBtu 2 | lb/hr | Basis | Compliance Method |
| --- | --- | --- | --- | --- | --- |
| NOX | Natural Gas | N/A 3 | 3.64 | Rule 62-210.200(PTE), F.A.C. | Annual Stack Test |
|  | Fuel Oil |  | 12.6 |  |  |
| SO2 | Fuel Oil | 050 | N/A | NSPS Subpart Dc |  |
| PM |  | 0.03 |  | NSPS Subpart Dc and NESHAP Subpart JJJJJJ |  |
| Opacity 4 | Fuel Oil | 20/27 |  | NSPA Subpart Dc |  |
|  | Natural Gas |  |  | Rule 62-296.406, F.A.C. |  |
| - Fuel oil limits only apply when oil is fired in backup boiler No. 6 for more than 48 hours in a calendar year excluding periods of gas supply curtailment and interruptions. - Opacity limits are in percent (%) visible emissions (VE). - .N/A = not applicable. - VE when firing any authorized fuel shall not exceed 20% opacity except for one, 6-minute block average per hour not to exceed 27% opacity |  |  |  |  |  |

[Rules 62-4.070(3); 62-210.200(PTE) and 62-296.406, F.A.C; NSPS Subpart Dc and NESHAP 40 CFR 63, Subpart JJJJJJ.]

- 11.  Facility-Wide Annual NOX Emission Cap:  NOX emissions shall not exceed 185.3 tons per year for any calendar year for all emissions units regulated by this air construction permit (EU 002, 003, 005, and 007 and 008).  The backup steam boilers may operate individually or in combination with one another or in combination with the CT/HRSG for supplemental steam during periods of high steam demand provided NOX emissions from all emissions units regulated by this permit comply with this facility-wide NOX emissions cap.  [PSD avoidance pursuant to 62-212.400(12), F.A.C.]

##### Excess Emissions

- 12.  Excess Emissions Prohibited:  Excess emissions caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure that may reasonably be prevented during startup, shutdown or malfunction are prohibited.  These emissions shall be included in the compliance averages for NOX emissions.  [Rule 62-210.700(4), F.A.C.]

- 13. Excess Emissions Allowed:  Best operational practices shall be used to minimize hourly emissions that may occur during episodes of startup, shutdown and malfunction.  Excess emissions resulting from startup, shutdown, and malfunction shall be permitted providing:  (1) best operational practices to minimize emissions are adhered to, and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24-hour period unless specifically authorized by the Department for longer duration.  For the combined cycle combustion turbine with a 30-day NOX averaging period, this requirement shall mean the following.  The 24-hour period shall be defined as the 24-hour block based on data collected from the NOX CEMS.  If the NOX CEMS reports emissions in excess of the 30-day rolling average, the permittee may exclude up to two hours of excess emissions data caused by each startup, shutdown and malfunction during the 30-day period to determine compliance.  No NOX emission data shall be excluded from the annual NOX emission caps.  This requirement is not intended to limit the duration of a startup – only the amount of data that may be excluded from the 30-day compliance averaging period.  If the 30-day rolling NOX emissions rate exceeds the standard, the permittee shall notify the Compliance Authority within one working day with a preliminary report of: the nature, extent, and duration of the excess emissions; the cause of the excess emissions; and the actions taken to correct the problem.  In addition, the Department may request a written summary report of the incident.  [Rule 62-210.700(1), F.A.C.]

##### Stack Testing Requirements

- 14.  Test Requirements:  The permittee shall notify the Compliance Authority in writing at least 15 days prior to any required tests.  Tests shall be conducted in accordance with the applicable requirements specified in Appendix D (Common Testing Requirements) of this permit.  [Rule 62-297.310(7), F.A.C.]

- 15.  Initial Compliance Stack Tests:  Backup Steam Boiler No. 6 The emissions units shall be tested to demonstrate initial compliance with the emissions standards within 60 days after achieving permitted capacity on natural gas but not later than 180 days after initial operation of the unit.  The boiler shall be tested to demonstrate compliance with the fuel oil emissions standards within 180 days of exceeding 48 hours of fuel oil in a calendar year excluding periods of natural gas supply curtailment or interruption.

- Combustion Turbine:  Initial compliance tests for CO and visible emissions shall be conducted at 90% to 100% of the maximum heat input rate for the actual compressor inlet temperature conditions during the test.  Compliance with the NOx limits shall be demonstrated by data collected from the CEMS.  {Permitting Note:  The requirements in the original permit to conduct initial compliance tests have previously been satisfied.}

- Duct Burner:  Initial compliance tests for CO emissions shall be conducted at 90% to 100% of the maximum heat input rate.  Compliance with the NOx limits shall be demonstrated by data collected from the CEMS.  {Permitting Note:  The requirements in the original permit to conduct initial compliance tests have previously been satisfied.  Safety considerations prevent subsequent periodic testing of the duct burner, which would likely require dumping excess steam during the test.}

- c.  Backup Steam Boilers No. 6:  Initial informational stack tests on the backup boilers No. 6 shall be conducted to establish the NOX emissions rate for purposes of reporting the NOX emission rate and complying with the facility-wide NOX emission cap and other applicable NOX emission limits. {Permitting Note:  The requirements in the original permit to conduct initial compliance tests on backup boiler No. 5 have previously been satisfied.}

[Rules 62-4.070(3) and 62-297.310(7), F.A.C.]

- 16.  Annual Compliance Tests:

  - Combined Cycle Combustion Turbine System:  During each federal fiscal year (October 1st to September 30th), the combined cycle combustion turbine system shall be tested to demonstrate compliance with the CO and visible emissions standards.  Due to safety considerations, stack testing while firing the duct burner when there is no demand for steam would require dumping excess steam, which presents a safety issue given the existing configuration.  Therefore, subsequent periodic testing for CO emissions may be with the duct burner on or off, as dictated by the system demand.  Visible emissions for each backup steam boiler shall be conducted only if No. 2 fuel oil is fired for more than 400 hours during the federal fiscal year.  {Permitting Note:  A safety evaluation of the steam vent system indicated that it did not meet code and was deemed unsafe; therefore, it was dismantled.}  [Rules 62-4.070(3) and 62-297.310(7), F.A.C.]

  - New Backup Boiler No. 6:  During each federal fiscal year (October 1st to September 30th), the backup boiler No. 6 shall be tested to demonstrate compliance with the NOX and visible emissions standards while firing natural gas.  The boiler shall be tested to demonstrate compliance with the fuel oil emissions limits for SO2, PM, NOX and visible emissions during each calendar year when fuel oil firing exceeds 48 hours excluding periods of natural gas supply curtailment and interruptions.  For determining compliance with the SO2 emission limit, the use of 40 CFR Part 75 Appendix D is authorized.  [Rules 62-4.070(3) and 62-210.200(PTE), F.A.C;NSPA Subpart Dc and NESHAP 40 CFR 63, Subpart JJJJJJ.]

- 17.  Special Compliance Tests:  When the Department, after investigation, has good reason (such as complaints, increased visible emissions or questionable maintenance of control equipment) to believe that any applicable emission standard contained in a Department rule or in a permit issued pursuant to those rules is being violated, it shall require the owner or operator of the emissions unit to conduct compliance tests which identify the nature and quantity of pollutant emissions from the emissions unit and to provide a report on the results of said tests to the Department.  [Rules 62-297.310(7), F.A.C.]

- 18.  Test Methods:  Any tests required by this permit shall be performed in accordance with the following reference methods.

| Method | Description of Method and Comments |
| --- | --- |
| 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| 5 | Method for Determining Particulate Matter Emissions |
| 7E | Determination of Nitrogen Oxide Emissions from Stationary Sources |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |
| 10 | Determination of Carbon Monoxide Emissions from Stationary Sources {Note: The method shall be based on a continuous sampling train.} |
| 19 | Determination of Sulfur Dioxide Removal Efficiency and Particulate Matter, Sulfur Dioxide, and Nitrogen Oxides Emission Rates (Optional F-factor method may be used to determine flow rate and gas analysis to calculate mass emissions in lieu of Methods 1-4.) |
| Part 75 Appendix D | Fuel Sulfur Analysis to determine SO2 Emissions. |

The above methods are described in Appendix A of 40 CFR 60 and are adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Rules 62-204.800 and 62-297.100, F.A.C.; and Appendix A of 40 CFR 60]

Monitoring Requirements

- 19.  Continuous Emission Monitoring System:  The permittee shall install, calibrate, maintain and operate a CEMS in the stack to measure and record the emissions of NOX from the combined cycle combustion turbine and duct burner system in a manner sufficient to demonstrate compliance with the NOX emission limits and caps specified in this permit.  The oxygen content or the carbon dioxide content of the flue gas shall also be monitored at the location where NOX is monitored to correct the measured NOX emissions rates to 15% oxygen and also reported as lb/hour.  The NOX CEMS shall be maintained in accordance with the monitoring equipment requirements in 40 CFR 75 for acid rain units.  [Rule 62-4.070(3), F.A.C., NSPS Subpart GG in 40 CFR 60 and 40 CFR 75]

- 20.  Fuel Flow Monitoring:  The permittee shall install/maintain equipment to monitor the fuel flow rates of the combustion turbine, duct burner and backup steam boilers.  [Rules 62-4.070(3) and 62-212.400(12), F.A.C. and NSPS Subpart GG in 40 CFR 60]

Records and Reports

- 21.  Fuel Consumption Rates Monthly Monitoring:  By the 15th calendar day of each month, the permittee shall record the monthly fuel consumption rates of the duct burner and backup steam boilers.  The written log shall summarize the fuel consumption for the previous month of operation and the previous 12 months of operation.  Information may be recorded and stored as an electronic file.  Records shall be available for inspection and printing within at least three days of a request by the Department or Compliance Authority.  [Rule 62-4.070(3), F.A.C.]

- 22.  Annual Facility-Wide NOX Emissions Report:  To demonstrate compliance with the facility-wide annual NOX emissions cap, the permittee shall calculate and record annual emissions as follows:

- Annual NOX emissions from the combined cycle combustion turbine and duct burner system shall be determined by data collected from the NOX CEMS.

- By April 1st of each year, the permittee shall report the facility-wide annual NOX emissions along with the Annual Operating Report.  Annual NOX emissions from the backup steam boilers Backup Steam Boiler No. 5 shall be determined based on the annual fuel consumption rate and either the following NOX emissions factors or more recent stack test data (at the option of the permittee).

No. 4 Steam Boiler:  0.0745 lb NOX/MMBtu (gas) and 0.0815 lb NOX/MMBtu (oil), and

No. 5 Steam Boiler:  0.110 lb NOX/MMBtu (gas) and 0.1070 lb NOX/MMBtu (oil).

Annual NOX emissions from the Backup Steam Boiler No. 6 shall be determined based on the annual fuel consumption rate and the annual stack test data.

If the facility-wide annual NOX emissions exceed the NOX emissions cap, the permittee shall notify the Compliance Authority within three working days of discovery.

- Before March 1st of 2012, the permittee shall submit a report to the Compliance Authority comparing the 2011 annual NOX emissions from the combustion turbine and duct burner to the estimated baseline actual emissions of 114.5 tons/year and the PSD applicability trigger threshold of 154.50 tons/year (114.5 + 40.0 = 154.50 tons/year).  This condition becomes obsolete after this reporting requirement is met.

[Rules 62-4.070(3) and PSD avoidance pursuant to 62-212.400(12), F.A.C.]

- 23.  Fuel Sulfur Records:  The permittee shall maintain records of the fuel sulfur content of natural gas and No. 2 fuel oil fired.  Such information may be provided by the natural gas pipeline vendor or the fuel oil vendor.  The following methods shall be used to determine the sulfur content of natural gas:  ASTM methods D4084-82, D3246-81, D5504, more recent versions of these methods, methods prescribed in Appendix D of 40 CFR 75, or other methods approved by the Department.  The following methods shall be used to determine the sulfur content of fuel oil:  ASTM D1552, ASTM D5453, ASTM D129-91, D2622-94 or D4294-90, more recent versions of these methods, methods prescribed in NSPS Subpart GG of 40 CFR 60 or other methods approved by the Department.  The permittee may also have a sample of fuel analyzed to determine the actual sulfur content.  Vendor certification acceptable in lieu of testing for fuel sulfur content.  [NSPS Subparts Db and GG in 40 CFR 60, 40 CFR 75 and Rule 62-4.070(3), F.A.C.]

- 24.  Stack Test Reports:  The permittee shall prepare and submit reports for all required tests in accordance with the requirements specified in Appendix D (Common Testing Requirements) of this permit.  For each test run, the report shall also indicate the heat input rate of the emissions unit.  [Rule 62-297.310(8), F.A.C.]

- 25.  Semi-Annual NSPS Excess Emissions Reports:  The permittee shall submit semi-annual excess emission reports in accordance with 40 CFR 60.7(d) to the Compliance Authority.  [40 CFR 60.7]

NSPS PROVISIONS

- NSPS Requirements:  The combustion turbine shall comply with the applicable provisions of NSPS Subpart GG in 40 CFR 60, Standards of Performance for Stationary Gas Turbines, adopted by reference in Rule 62-204.800, F.A.C.  The duct burner shall comply with the applicable provisions of NSPS Subpart Db in 40 CFR 60, Standards of Performance for Industrial-Commercial-Institutional Steam Generating Units, adopted by reference in Rule 62-204.800, F.A.C.  The emissions units shall also comply with the applicable requirements of 40 CFR 60, Subpart A, General Provisions, including:

- 40CFR60.7	Notification and Record Keeping

- 40CFR60.8	Performance Tests

- 40CFR60.11	Compliance with Standards and Maintenance Requirements

- 40CFR60.12	Circumvention

- 40CFR60.13	Monitoring Requirements

- 40CFR60.19	General Notification and Reporting requirements

[40 CFR 60, NSPS Subparts A, Db and GG]