### TECHNICAL EVALUATION

&

PRELIMINARY DETERMINATION

#### APPLICANT

University of Florida

Animal Resource Department

Post Office Box 100006

Gainesville, Florida 32610

Progress Park Facility

Facility ID No. 0010072

#### PROJECT

# Project No. 0010072-005-AC

Application for Air Construction Permit

#### Simonds Biological Waste Incinerator

#### COUNTY

Alachua, Florida

PERMITTING AUTHORITY

Florida Department of Environmental Protection

Northeast District Office

Waste and Air Resource Management

8800 Baymeadows Way West, Suite 100

Jacksonville, Florida  32256

COMPLIANCE AUTHORITY

Florida Department of Environmental Protection

Northeast District Office

Compliance Assurance

8800 Baymeadows Way West, Suite 100

Jacksonville, Florida  32256

December 20, 2013

1.  General Project INFORMATION

Air Pollution Regulations

Projects at stationary sources with the potential to emit air pollution are subject to the applicable environmental laws specified in Section 403 of the Florida Statutes (FS).  The statutes authorize the Department of Environmental Protection (Department) to establish regulations regarding air quality as part of the Florida Administrative Code (F.A.C.), which includes the following applicable chapters:  62-4 (Permits); 62-204 (Air Pollution Control – General Provisions); 62-210 (Stationary Sources – General Requirements); 62-212 (Stationary Sources – Preconstruction Review); 62-213 (Operation Permits for Major Sources of Air Pollution); 62-296 (Stationary Sources - Emission Standards); and 62-297 (Stationary Sources – Emissions Monitoring).  Specifically, air construction permits are required pursuant to Rules 62-4, 62-210 and 62-212, F.A.C.

In addition, the U. S. Environmental Protection Agency (EPA) establishes air quality regulations in Title 40 of the Code of Federal Regulations (CFR).  Part 60 specifies New Source Performance Standards (NSPS) for numerous industrial categories.  Part 61 specifies National Emission Standards for Hazardous Air Pollutants (NESHAP) based on specific pollutants.  Part 63 specifies NESHAP based on the Maximum Achievable Control Technology (MACT) for numerous industrial categories. The Department adopts these federal regulations on a quarterly basis in Rule 62-204.800, FAC.

Glossary of Common Terms

Because of the technical nature of the project, the permit contains numerous acronyms and abbreviations, which are defined in Appendix A of this permit.

Facility Description and Location

The University of Florida Progress Park Facility operates a Simonds, dual chambered natural gas-fired biological waste incinerator (Model 604L) which is designed to burn pathological, animal waste.  The maximum design capacity of this emissions unit is 600 pounds per hour. (Certification of Completion of Construction dated June 26, 1991)  The incinerator consists of primary and secondary (afterburner) chambers, each fired on natural gas.

The incinerator utilizes four primary Eclipse 936SIB-G chamber burners (1 MMBtu/hr each), and one ThermAir TA200 second stage burner (2.071 MMBtu/hr). Emissions are controlled by the afterburner, which maintains a minimum secondary chamber combustion zone temperature of 1800 degrees Fahrenheit prior to and during combustion of material in the primary chamber.  The secondary chamber is designed to insure one-second residence time at a gas temperature of 1800 degrees Fahrenheit (F), and is equipped with a continuous temperature monitor.

Only 100% pathological wastes and, if applicable, the bedding and the remains associated with the animals placed in leak-proof containers, are incinerated. Chlorinated materials shall not be incinerated.

The existing facility Standard Industrial Classification Code (SIC) (8733) is classified as a synthetic non-titlve V source of air pollution because the potential emissions of regulated air pollutants are less than 100 tons per year, and individual and total hazardous air pollutants are less than 10 and 25 tons per year, respectively in accordance with Chapter 62-210, FAC.  The facility has restricted hours of operation so that potential HCl emissions are below the major source threshold.  The facility is located at Research Drive and S.E. 12th Street, in Alachua County.  UTM Coordinates:  Zone 17, 355.3 km East and 3295.5 km North.

Facility Regulatory Categories

Based on the application received November 21, 2013,

- The facility is not a major source of hazardous air pollutants (HAP).

- The facility has no units subject to the acid rain provisions of the Clean Air Act.

- The facility is not a Title V major source of air pollution in accordance with Chapter 213, F.A.C.

- The facility is not a major stationary source in accordance with Rule 62-212.400, F.A.C. for the Prevention of Significant Deterioration (PSD) of Air Quality.

State Requirements

The existing facility will continue to be subject to the requirements of Rule 62-296.401(4) F.A.C. for Biological Waste Incinerators.

Project Description

The purpose of this project is to:

1).	Authorize the installation of a Program Logic Controller (PLC) to the existing Simonds 604L Biological Waste Incinerator.  Modification includes the installation of a Siemens S7-1200CPU (1215C) with a SM1231 thermocouple module and a KTP600 mono touch screen.  The Siemens S7-1200 CPU will accept the weight scale’s analog output which will monitor the charge weight (495lbs/hr).  Each load will be weighed and logged into the PLC controller.  If the total of the weight exceeds 495lbs/hr the machines PLC will not allow load to charge enabling CPU controlled mechanical lock out of the loading process.

2). Establish a restriction of 495lbs/hr. maximum incinerator operating rate (applicant request).

3). Authorize a change to the PM emissions limiting standards  from 0.030 grains per dry standard cubic feet of flue gas corrected to 7% O2  (Rule  62-296.401(4) (b) 3a. F.A.C.), to 0.100 grains per dry standard cubic feet of flue gas corrected to 7% O2 (Rule 62-296.401(4) (b) 2a. F.A.C).

- Proposed Work

Biological Waste Incinerator (EU 001):  The permittee is authorized to, modify, and operate (for purposes of testing and unit shakedown) the existing Simonds 604L Biological Waste Incinerator. Upon final issuance of this construction permit the maximum incinerator operating rate shall be physicallylimited by the installation of the PLC to no more than 495 lbs/hr of pathological animal waste (Application No. 0010072-005-AC, Applicant Request).

Processing Schedule

November 21, 2013	Application for Air Construction Permit Modification

December 13, 2013	Supplemental information received

2.  PSD Applicability

General PSD Applicability

For areas currently in attainment with the state and federal AAQS or areas otherwise designated as unclassifiable, the Department regulates major stationary sources of air pollution in accordance with Florida’s PSD preconstruction review program as defined in Rule 62-212.400, FAC.  Under preconstruction review, it must first be determined if a project is subject to the PSD requirements (“PSD applicability review”) and, if so, a PSD preconstruction review must be conducted.  A PSD applicability review is required for projects at new and existing major stationary sources.  In addition, proposed projects at existing minor sources are subject to a PSD applicability review to determine whether potential emissions from the proposed project itself will exceed the PSD major stationary source thresholds.  A facility is considered a major stationary source with respect to PSD if it emits or has the potential to emit:

- 5 tons per year or more of lead;

- 250 tons per year or more of any regulated air pollutant; or

- 100 tons per year or more of any regulated air pollutant and the facility belongs to one of the following 28

PSD-major facility categories:  fossil fuel-fired steam electric plants of more than 250 million British thermal units per hour heat input, coal cleaning plants (with thermal dryers), Kraft pulp mills, portland cement plants, primary zinc smelters, iron and steel mill plants, primary aluminum ore reduction plants, primary copper smelters, municipal incinerators capable of charging more than 250 tons of refuse per day, hydrofluoric, sulfuric, and nitric acid plants, petroleum refineries, lime plants, phosphate rock processing plants, coke oven batteries, sulfur recovery plants, carbon black plants (furnace process), primary lead smelters, fuel conversion plants, sintering plants, secondary metal production plants, chemical process plants, fossil fuel boilers (or combinations thereof) totaling more than 250 million British thermal units per hour heat input, petroleum storage and transfer units with a total storage capacity exceeding 300,000 barrels, taconite ore processing plants, glass fiber processing plants and charcoal production plants.

Once it is determined that a project is subject to PSD preconstruction review, the project emissions are compared to the “significant emission rates” defined in Rule 62-210.200, F.A.C. for the following pollutants:  carbon monoxide (CO); nitrogen oxides (NOX); sulfur dioxide (SO2); particulate matter (PM); particulate matter with a mean particle diameter of 10 microns or less (PM10); volatile organic compounds (VOC); lead (Pb); fluorides (Fl); sulfuric acid mist (SAM); hydrogen sulfide (H2S); total reduced sulfur (TRS), including H2S; reduced sulfur compounds, including H2S; municipal waste combustor organics measured as total tetra- through octa-chlorinated dibenzo-p-dioxins and dibenzofurans; municipal waste combustor metals measured as particulate matter; municipal waste combustor acid gases measured as SO2 and hydrogen chloride (HCl); municipal solid waste landfills emissions measured as non-methane organic compounds (NMOC); and mercury (Hg).  In addition, significant emissions rate also means any emissions rate or any net emissions increase associated with a major stationary source or major modification which would construct within 10 kilometers of a Class I area and have an impact on such area equal to or greater than 1 μg/m3, 24-hour average.

If the potential emission exceeds the defined significant emissions rate of a PSD pollutant, the project is considered “significant” for the pollutant and the applicant must employ the Best Available Control Technology (BACT) to minimize the emissions and evaluate the air quality impacts.  Although a facility or project may be major with respect to PSD for only one regulated pollutant, it may be required to install BACT controls for several “significant” regulated pollutants.

PSD Applicability for Project

This facility is not major for purposes of Prevention of Significant Deterioration.  This project is not subject to PSD preconstruction review requirements since the proposed project itself has potential emissions of PSD air pollutants that are less than 250 tons per year pursuant to Rule 62-210.200(194), F.A.C., and Rule 2.301, JEPB. Therefore, additional Prevention of Significant Deterioration analysis is not required.

3.  Department of Environmental Protection Application Review

APPLICABILITY OF PREVIOUS PERMITS

Existing Permits and Regulations:  The conditions of this permit supplements all other previously issued air construction and operation permits for this emission unit. These conditions are in addition to all other applicable permit conditions and regulatory requirements. The Permittee shall continue to comply with the conditions of

those permits, which include restrictions and standards regarding capacities, production, operation, fuels, emissions, monitoring, recordkeeping, reporting and the like.

4.  Preliminary Determination

The Department makes a preliminary determination that the proposed project will comply with all applicable local, state and federal air pollution regulations as conditioned by the draft permit. This determination is based on a technical review of the complete application, reasonable assurances provided by the applicant, and the conditions specified in the draft permit. No air quality modeling analysis is required because the project does not result in a significant increase in emissions. Yasmin K. Enriquez is the project specialist responsible for reviewing the application and drafting the permit.  Additional details of this analysis may be obtained by contacting the project specialist at the Florida Department of Environmental Protection, Northeast District Office, Waste and Air Resource Management Program, 8800 Baymeadows Way West, Suite 100, Jacksonville, FL 32256, Phone: 904-256-1700.