### TECHNICAL EVALUATION

&

PRELIMINARY DETERMINATION

#### APPLICANT

Gulf Power Company

One Energy Place

Pensacola, Florida  32520-0100

Lansing Smith Electric Generating Plant

Facility ID No. 0050014

#### PROJECT

# Project No. 0050014-024-AC

Test Burn of Emissions Control Sorbent Additives

#### COUNTY

Bay County, Florida

PERMITTING AUTHORITY

Florida Department of Environmental Protection

Division of Air Resource Management

Office of Permitting and Compliance

2600 Blair Stone Road, MS#5505

Tallahassee, Florida  32399-2400

November 1, 2013

- General Project INFORMATION

  - Air Pollution Regulations

Projects at stationary sources with the potential to emit air pollution are subject to the applicable environmental laws specified in Section 403 of the Florida Statutes (F.S.).  The statutes authorize the Department of Environmental Protection (Department) to establish regulations regarding air quality as part of the Florida Administrative Code (F.A.C.), which includes the following applicable chapters:  62-4 (Permits); 62-204 (Air Pollution Control – General Provisions); 62-210 (Stationary Sources – General Requirements); 62-212 (Stationary Sources – Preconstruction Review); 62-213 (Operation Permits for Major Sources of Air Pollution); 62-296 (Stationary Sources - Emission Standards); and 62-297 (Stationary Sources – Emissions Monitoring).  Specifically, air construction permits are required pursuant to Chapters 62-4, 62-210 and 62-212, F.A.C.

In addition, the U. S. Environmental Protection Agency (EPA) establishes air quality regulations in Title 40 of the Code of Federal Regulations (CFR).  Part 60 specifies New Source Performance Standards (NSPS) for numerous industrial categories.  Part 61 specifies National Emission Standards for Hazardous Air Pollutants (NESHAP) based on specific pollutants.  Part 63 specifies NESHAP based on the Maximum Achievable Control Technology (MACT) for numerous industrial categories.  The Department adopts these federal regulations in Rule 62-204.800, F.A.C.

  - Facility Description and Location

The Gulf Power Company Lansing Smith Generating Plant is categorized under Standard Industrial Classification Code No. 4911.  Refer to Figure 1 and Figure 2.  The Lansing Smith Generating Plant is located in Bay County at 4300 County Road 2300, Southport, Florida.

Lansing Smith

Bay County

Figure 1.  Bay County, Florida.	Figure 2.  Location of Lansing Smith Plant.

The UTM coordinates are Zone 16; 623.74 Kilometer (km) East and 3349.11 km North.  This site is in an area that is in attainment (or designated as unclassifiable) for all air pollutants subject to Ambient Air Quality Standards (AAQS).

Table 1 is a summary of Emissions Units (E.U.) from the Facility Title V Air Operation Permit 
0050014-018-AV.  Units 1 and 2 are the subject of the present permit application.  Units 1 and 2 are tangentially fired, dry bottom coal-fueled boilers that began commercial operation in 1965 and 1967, respectively.

Table 1.  Summary of Emissions Units (E.U.).

| E.U. No. | ## Brief Description |
| --- | --- |
| Regulated Emissions Units |  |
| 001 | Boiler Number 1 - 1,944.8 MMBtu/hour |
| 002 | Boiler Number 2 - 2,246.2 MMBtu/hour |
| 003 | Combustion Turbine - 542 MMBtu/hour Peaking Unit |
| 004 | 170 MW Gas Combustion Turbine with HRSG and Duct Burner |
| 005 | 170 MW Gas Combustion Turbine with HRSG and Duct Burner |
| 006 | Cooling Tower |
| 010 | Portable Welding Machine |
| 011 | Diesel Emergency Sump Pump |
| 012 | Diesel Emergency Generator for units -001 and -002 |
| Unregulated Emissions Units and Activities |  |
| 007 | Material Handling of Coal and Ash |
| 008 | Fugitive PM Sources - On-site Vehicles |
| 009 | General Purpose Internal Combustion Engines |

Units 1 and 2 have a common 199-foot stack and are equipped with the air pollution control and measurement equipment listed below:

- Hot and cold side electrostatic precipitators to control particulate matter (PM);

- Low nitrogen oxide (NOX) burners and non-selective catalytic reduction (SNCR) systems to control NOX; and

- Continuous emissions monitoring systems (CEMS) to measure and record NOX and sulfur dioxide (SO2) emissions and a continuous opacity monitoring system (COMS) to measure and record the opacity of the exhaust gas.

  - Facility Regulatory Categories

- The facility is a major source of hazardous air pollutants (HAP).

- The facility operates units subject to the acid rain provisions of the Clean Air Act.

- The facility is a Title V major source of air pollution in accordance with Chapter 62-213, F.A.C.

- The facility is a major stationary source in accordance with Rule 62-212.400, F.A.C. for the Prevention of Significant Deterioration (PSD) of Air Quality.

- The facility is subject to the Clean Air Interstate Rule (CAIR) set forth in Rule 62-296.470, Florida Administrative Code (F.A.C.)

- The facility operates units subject to the Standards of Performance for New Stationary Sources (NSPS) pursuant to 40 CFR Part 60.

  - Application

On October 18, 2013, Gulf Power Corporation submitted an air construction permit application for Lansing Smith Generating Plant Units 1 and 2.  The application may be accessed by entering permit No. 0050014-024-AC on the following web site:  http://www.dep.state.fl.us/air/emission/apds/default.asp.

  - Project Description

- The project conducted on units 1 and 2 is considered an engineering and design improvement assessment project.  The objective of this project is to finalize Gulf Power’s compliance plan to meet the Best Available Retrofit Technology (BART) and Mercury and Air Toxic Standards (MATS) air quality reduction goals.  For this test series, several emissions control sorbent additives called Hydrated Lime, Trona, and Activated Carbon will be injected at various points to reduce combustion emissions of sulfur dioxide (SO2), hydrogen chloride (HCl), and mercury (Hg).  The additives will be injected into the boiler, EPSs, or ductwork during the test burn program to decipher the optimal injection zone for the sorbents in order to meet emissions reduction goals.  In conjunction with the design assessment the facility will be conducting a sorbent study to determine if there are long term impacts on the Air-preheater and ESP’s from the use of the additives.

The additional mass loading increases the volume of ash to be handled.  With the addition of Trona, hydrated lime, and activated carbon there is at least the possibility of some minor changes in the coal, ash handling systems, and pollution control equipment to facilitate the overall emissions reduction objective.

For the Gulf Power Lansing Smith tests, the following temporary operations and equipment are required:

- A silo filled by hydrated lime tanker truck, a blower truck, small heat exchanger, and injection lances for the boiler, ESPs, or ductwork.

- A silo filled by Trona tanker truck, in-line pin mill, blower truck, small heat exchanger, and injection lances for the boiler, ESPs, or ductwork.

- A trailer mounted blower conveying powder activated carbon through injection lances into the boiler, ESPs, or ductwork.

  - Processing Schedule

10/18/2013	Received the application for a test burn program

11/01/2013	Distributed Intent to Issue Air Permit package.

- PSD Applicability

  - General PSD Applicability

The Department regulates major stationary sources in accordance with Florida’s PSD program pursuant to Rule 62-212.400(PSD), F.A.C.  PSD preconstruction review is required in areas that are currently in attainment with the state and federal ambient air quality standards (AAQS) or areas designated as “unclassifiable” for these regulated pollutants.

Commonly addressed PSD pollutants in the power industry include: carbon monoxide (CO), SO2, NOX, PM, PM smaller than 10 micrometers (µm) (PM10), PM smaller than 2.5 µm (PM2.5), volatile organic compounds (VOC), sulfuric acid mist (SAM), lead (Pb), fluorides (F), and Hg.

Additional PSD pollutants that are more common to certain other industries include: hydrogen sulfide (H2S), TRS including H2S, reduced sulfur compounds (RSC) including H2S, municipal waste combustor (MWC) organics measured as total tetra- through octa-chlorinated dibenzo-p-dioxins and dibenzofurans (dioxin/furan), MWC metals measured as PM; MWC acid gases measured as SO2 and HCl, and municipal solid waste (MSW) landfill emissions as non-methane organic compounds (NMOC).

As defined in Rule 62-210.200(Definitions), F.A.C., a stationary source is a “major stationary source” (major PSD source) if it emits or has the potential to emit (PTE):

- 250 tons per year (tons/year) or more of any PSD pollutant; or

- 100 tons/year or more of any PSD pollutant and the facility belongs to one of the 28 listed PSD major facility categories.

The list given in the citation includes the category of “fossil fuel-fired steam electric plants of more than 250 million British thermal units per hour heat input”.  The given category applies to the Lansing Smith Generating Plant.  Lansing Smith Generating Plant is a major stationary source based on actual emissions of and potential to emit 100 tons/year or more of several individual PSD pollutants.

For major stationary sources such as the Lansing Smith Plant, PSD applicability for modification projects is based on thresholds known as the significant emission rates (SER) as defined in Rule 62-210.200 (Definitions), F.A.C.  Any “net emissions increase” as defined in Rule 62-210.200 (Definitions), F.A.C. of a PSD pollutant from the project that equals or exceeds the respective SER is considered “significant”.

SER also means any emissions rate or any net emissions increase of a PSD pollutant associated with a major stationary source or major modification which would construct within 10 km of a Class I area and have an impact on such area equal to or greater than 1 gram per cubic meter, 24-hour average.

Although a facility may be “major” (i.e. emits or has the potential to emit 100 or 250 tons/year as applicable) for only one PSD pollutant, a project must include Best Available Control Technology (BACT) for any PSD pollutant increase in that equals or exceeds the corresponding significant emission rate (SER) given in Table 2.

Table 2.  List of SER by PSD-Pollutant Relevant to the Facility. 2

| Pollutant | SER (tons/year) | Pollutant | SER (tons/year) |
| --- | --- | --- | --- |
| PM | 25 | PM10 | 15 |
| PM2.5 | 10 | PM2.5 (NOX) 1 | 40 |
| PM2.5 (SO2) 1 | 40 | CO | 100 |
| SO2 |  | NOX | 40 |
| Ozone (NOX) 1 | 40 | Ozone (VOC) 1 | 40 |
| Sulfuric acid mist (SAM) | 7 | fluoride | 3 |
| mercury | 0.1 | lead | 0.6 |
| - PM2.5 is also regulated through precursors (NOX and SO2); Ozone (O3) is regulated through precursors (VOC and NOX). - There is federal SER of 75,000 tons/year for Greenhouse Gases (GHG) as carbon dioxide equivalent (CO2e) that has not been incorporated into Department rules. |  |  |  |

According to 40 CFR 52.21, six greenhouse gases (GHG), are also subject to regulation at new stationary sources According to 40 CFR 52.21, six greenhouse gases (GHG), are also subject to regulation at new stationary sources that will emit or have the potential to emit 100,000 tons/year (SER equal to 75,000 tons/year) expressed as the carbon dioxide equivalent emissions (CO2e).  This requirement has not been incorporated into Department rules but is a separate requirement of the EPA.

Methodology for Calculations of Baseline Actual Emissions and Projected Actual Emissions

To determine whether the project causes net emissions increases equal to or greater than the respective SER (triggering PSD) requires a comparison of recent “baseline actual emissions” with future “projected actual emissions”.  According to Rule 62-210.200(Definitions), F.A.C., for any existing electric utility steam generating unit:

“Baseline actual emissions" means the average rate, in tons per year, at which the unit actually emitted the pollutant during any consecutive 24-month period selected by the owner or operator within the 5-year period immediately preceding the date a complete permit application is received by the Department.  The Department shall allow the use of a different time period upon a determination that it is more representative of normal source operation”.

- The average rate shall include fugitive emissions to the extent quantifiable, and emissions associated with startups and shutdowns.

- The average rate shall be adjusted downward to exclude any non-compliant emissions that occurred while the source was operating above any emission limitation that was legally enforceable during the consecutive 24-month period.

- For a PSD pollutant, when a project involves multiple emissions units, only one consecutive 24-month period must be used to determine the baseline actual emissions for the emissions units being changed.  A different consecutive 24-month period can be used for each PSD pollutant.

- The average rate shall not be based on any consecutive 24-month period for which there is inadequate information for determining annual emissions, in tons per year, and for adjusting this amount if required by subparagraph 2, above.

According to Rule 62-210.200(Definitions), F.A.C., for an existing unit (other than an electric steam generating unit):

“Projected Actual Emissions” means the maximum annual rate, in tons/year, at which an existing emissions unit is projected to emit a PSD pollutant in any one of the 5 years following the date the unit resumes regular operation after the project, or in any one of the 10 years following that date, if the project involves increasing the emissions unit's design capacity or its potential to emit that PSD pollutant and full utilization of the unit would result in a significant emissions increase or a significant net emissions increase at the major stationary source.  One year is one 12-month period.   In determining the projected actual emissions, the Department:

- Shall consider all relevant information, including historical operational data, the company’s own representations, the company’s expected business activity and the company’s highest projections of business activity, the company’s filings with the State or Federal regulatory authorities, and compliance plans or orders, including consent orders; and

- Shall include fugitive emissions to the extent quantifiable and emissions associated with startups and shutdowns; and

- Shall exclude that portion of the unit's emissions following the project that an existing unit could have accommodated during the consecutive 24-month period used to establish the baseline actual emissions and that are also unrelated to the particular project including any increased utilization due to product demand growth; or

- In lieu of using the method set out in paragraphs (a) through (c) above, may be directed by the owner or operator to use the emissions unit’s potential to emit, in tons per year.

  - PSD Applicability for Project

The project is located in Bay County, which is in an area that is currently in attainment with the state and federal AAQS or otherwise designated as unclassifiable.

According to the applicant and stack test data from multiple, short duration test runs allowed in air construction permit No. 0050014-023-AC, the project is expected to increase PM emissions (and thus PM10 and filterable PM2.5) by far less than 6 tons/year.  The test burn program Gulf Power previously conducted on units 1 and 2 (permit No. 0050014-023-AC) using the same emission control sorbents saw a slight increase of PM emissions of 1.5 tons.  Emission reductions of mercury were up to sixty percent during the initial round of testing conducted in August at the hot side of the ESP with no opacity or particulate issues.  The hydrated lime sorbent met the hydrogen chloride reduction objective with an observed emission rate lower than MATS at approximately 0.0012 to 0.0024 lbs/MMBtu with no observed opacity or particulate issues.  The Trona sorbent met the SO2 (50%) and HCl (90%) reduction goals on all loads with no observed opacity or particulate issues.

The activated carbon injection before the cold-side ESP performed as expected during the initial testing.  Opacity and PM emission measurements indicated that most of the carbon sorbent did not react and was not collected by the cold-side precipitator.  A second test was conducted using ADA Fast Pac carbon with success by adjusting the cold-side ESP rapper program.  This information along with a longer term impact study on process and control equipment will be used to develop the mercury control strategy.

After analyzing the stack test data provide from the initial test project, the applicant demonstrated: Hg emissions can be significantly reduced; SO2 and HCl emissions can be significantly reduced; and all other pollutants remained comparable to baseline levels when injecting a single sorbent or a combination of sorbents.

- Preliminary Determination

The requested test program will allow units 1 and 2 to inject hydrated lime, Trona, and activated carbon sorbents to evaluate engineering and design improvements in order to determine long term operational impacts and feasibility.  No air quality modeling analysis was required because the project does not result in a significant increase in emissions.  After reviewing the test data submitted as required by permit No. 0050014-023-AC, it has been demonstrated these units have sufficient control equipment to ensure that PSD could not possibly be triggered.  The Department has reasonable assurance that the engineering and design improvement study to determine a final compliance strategy to meet the BART and MATS air quality reduction goals will not discharge, emit, or cause pollution in contravention of Department standards or rules.

The Department makes a preliminary determination that the proposed engineering and design improvement project to reduce SO2, acid gases, and mercury emissions will comply with presently applicable state and federal air pollution regulations as conditioned by the draft permit.  This determination is based on a technical review of the application, reasonable assurances provided by the applicant, test data, and the conditions specified in the draft permit.  Leigh-Ann Pell is the project engineer responsible for reviewing the application and drafting the permit.  Additional details of this analysis may be obtained by contacting the project engineer at leigh.pell@dep.state.fl.us , 850/717-9033, or the Department’s Office of Permitting and Compliance, Mail Station #5505, 2600 Blair Stone Road, Tallahassee, Florida  32399-2400.