### TECHNICAL EVALUATION

&

PRELIMINARY DETERMINATION

#### APPLICANT

Orlando Utilities Commission

US 1 and Kings Highway

Titusville, Florida  32780

Indian River Power Plant

Facility ID No. 0090008

#### PROJECT

# Project No. 0090008-008-AC

Application for Minor Source Air Construction Permit

Removal of Oil Firing Capability from Units 1, 2 & 3

#### COUNTY

Brevard County, Florida

PERMITTING AUTHORITY

Florida Department of Environmental Protection

Division of Air Resource Management

Office of Permitting and Compliance

Power Plant Permitting Group

2600 Blair Stone Road, MS#5505

Tallahassee, Florida  32399-2400

July 27, 2012

1.  General Project INFORMATION

Air Pollution Regulations

Projects at stationary sources with the potential to emit air pollution are subject to the applicable environmental laws specified in Section 403 of the Florida Statutes (F.S.).  The statutes authorize the Department of Environmental Protection (Department) to establish regulations regarding air quality as part of the Florida Administrative Code (F.A.C.), which includes the following applicable chapters:  62-4 (Permits); 62-204 (Air Pollution Control – General Provisions); 62-210 (Stationary Sources – General Requirements); 62-212 (Stationary Sources – Preconstruction Review); 62-213 (Operation Permits for Major Sources of Air Pollution); 62-296 (Stationary Sources - Emission Standards); and 62-297 (Stationary Sources – Emissions Monitoring).  Specifically, air construction permits are required pursuant to Chapters 62-4, 62-210 and 62-212, F.A.C.

In addition, the U. S. Environmental Protection Agency (EPA) establishes air quality regulations in Title 40 of the Code of Federal Regulations (CFR).  Part 60 specifies New Source Performance Standards (NSPS) for numerous industrial categories.  Part 61 specifies National Emission Standards for Hazardous Air Pollutants (NESHAP) based on specific pollutants.  Part 63 specifies NESHAP based on the Maximum Achievable Control Technology (MACT) for numerous industrial categories.  The Department adopts these federal regulations in Rule 62-204.800, F.A.C.

Facility Description and Location

The Indian River Power Plant is an existing electrical generating power plant, which is categorized under Standard Industrial Classification Code No. 4911.  The existing facility primarily consists of four combustion turbines and three steam generating boilers.  The three boilers were recently purchased from the adjacent GenOn facility.  The Indian River Power Plant is located in Brevard County at US 1 and Kings Highway in Titusville, Florida.  The UTM coordinates of the existing facility are Zone 17, 521.3 East and 3,151.7 North.  Latitude is:  28° 29′ 36" North; and, Longitude is:  80° 46′ 57" West.  This site is in an area that is in attainment (or designated as unclassifiable) for all air pollutants subject to Ambient Air Quality Standards (AAQS).

Facility Regulatory Categories

- The facility is a major source of hazardous air pollutants (HAP).

- The facility operates units subject to the acid rain provisions of the Clean Air Act.

- The facility is a Title V major source of air pollution in accordance with Chapter 62-213, F.A.C.

- The facility is a major stationary source in accordance with Rule 62-212.400, F.A.C. for the Prevention of Significant Deterioration (PSD) of Air Quality.

- Project Description

With the inclusion of the three boilers that were recently purchased from the adjacent facility (formerly owned by GenOn), the combined facility is a major source of hazardous air pollutants (HAP).  Emissions units 001, 002 and 003 are Combustion Engineering steam generators (boilers).  The boilers may currently burn a variable combination of natural gas, propane, No. 6 and No. 2 fuel oils, and on-specification used oil from facility operations.  While preparing the Title V air operation permit revision application to incorporate Units 1, 2 and 3 from the GenOn facility into the Title V air operation permit for the Indian River Plant, OUC decided that they did not wish to retain the option of firing fuel oil in these units.  Therefore, they have requested that an air construction permit be issued concurrently with Title V air operation permit to remove oil firing as an allowable method of operation and to limit the sulfur content of the gas to 2 grains per 100 standard cubic feet.

Processing Schedule

6/4/12	Received the application for a minor source air pollution construction permit, application deemed complete upon receipt.

2.  PSD Applicability

The requested revision is to reduce the potential sulfur dioxide (SO2) emissions from Units 1, 2 & 3 by removing the authority to fire fuel oil.  There are no other changes requested, nor are there any increases in emissions or operating capacity authorized.  As such, a PSD review is not applicable.

3.  Department review

During the time when Units 1, 2 & 3 were owned by GenOn, permit No. 0090196-010-AC was issued to establish federally enforceable heat input rates for firing gas and oil.  With the transfer of ownership of these units to OUC, the authorizations established by this permit also transfer.  Based on OUC’s request to remove fuel oil firing as an allowable method of operation, the Department will issue an air construction permit which supersedes the authority established by permit No. 0090196-010-AC by limiting operation of Units 1, 2 & 3 to only firing natural and propane gas containing a maximum of 2 grains of sulfur per 100 standard cubic feet.  The visible emissions limitation of 40% originally allowed under the authority of Rule 62-296.405(1)(a), F.A.C., for pre-NSPS oil and coal-fired boilers electing to test for particulate emissions quarterly is not appropriate for gas-fired boilers.  Therefore, the visible emissions limitation will be changed to 20%, pursuant to Rule 62-296.320(4)(b)1., F.A.C.

4.  Preliminary Determination

The Department makes a preliminary determination that the proposed project will comply with all applicable state and federal air pollution regulations as conditioned by draft permit No. 0090008-008-AC.  This determination is based on a technical review of the complete application, reasonable assurances provided by the applicant, and the conditions specified in the draft permit.  No air quality modeling analysis is required because the project does not result in an increase in any emissions.  Jon Holtom, P.E., is the project engineer responsible for reviewing the application and drafting the permit.  Additional details of this analysis may be obtained by contacting the project engineer at the Department’s Office of Permitting and Compliance at Mail Station #5505, 2600 Blair Stone Road, Tallahassee, Florida  32399-2400.