Operation & Maintenance Plan

for the Baghouses and Ovens

(Attachment A)

BI-WEEKLY OPERATION & MAINTENANCE PLAN

Blasting Booth Baghouse

Pangborn Type CM, Model C40 #222KO76-662 Baghouse

- Process Parameters: To inspect on a bi-weekly basis and record any abnormal or unusual conditions on Log Form.

- The following observation checks apply to this source:

- Observe stack for emissions (visually)

- Note any unusual occurrences in the process

- Observe operation of baghouse when shakers operates

- Check shaker mechanism

- Visually inspect lubrication of mechanism

- Visually inspect shaker motor

- Visually inspect drums

- Visually inspect seals

- Visually inspect ducts for corrosion

- Visually inspect gasket on inspection door

- Visually inspect and record manometer gauge readings

- Inspect the ground areas underneath and around the collection drums

- Annual Maintenance:

- Replace bags and drums on an as needed basis

- Inspect all ductwork for cracks, holes or openings

- Reporting Requirements:

- Report any discrepancies to the Training & Risk Manager, and Facility Plant Manager

- Document and initial Maintenance Log and turn in to Training & Risk Manager

BI-WEEKLY OPERATION & MAINTENANCE PLAN

Grinding Room Baghouse

Torit, Model #84-55 Baghouse

- Process Parameters: To inspect on a bi-weekly basis and record any abnormal or unusual conditions on Log Form.

- The following observation checks apply to this source:

- Observe stack for emissions (visually)

- Note any unusual occurrences in the process

- Observe operation of baghouse when shakers operates

- Check shaker mechanism

- Visually inspect lubrication of mechanism

- Visually inspect shaker motor

- Visually inspect drums

- Visually inspect seals

- Visually inspect ducts for corrosion

- Visually inspect gasket on inspection door

- Visually inspect and record manometer gauge readings

- Inspect the ground areas underneath and around the collection drums

- Annual Maintenance:

- Replace bags and drums on an annual basis or as needed

- Inspect all ductwork for cracks, holes or openings

- Reporting Requirements:

- Report any discrepancies to the Training & Risk Manager, and Facility Plant Manager

- Document and initial Maintenance Log and turn in to Training & Risk Manager

BI-WEEKLY OPERATION & MAINTENANCE PLAN

Teardown Room Baghouse

DustKop, Model #FH58-3D Baghouse

- Process Parameters: To inspect on a bi-weekly basis and record any abnormal or unusual conditions on Log Form.

- The following observation checks apply to this source:

- Observe stack for emissions (visually)

- Note any unusual occurrences in the process

- Observe operation of baghouse when shakers operates

- Check shaker mechanism

- Visually inspect lubrication of mechanism

- Visually inspect shaker motor

- Visually inspect drums

- Visually inspect seals

- Visually inspect ducts for corrosion

- Visually inspect gasket on inspection door

- Visually inspect and record manometer gauge readings

- Inspect the ground areas underneath and around the collection drums

- Annual Maintenance:

- Replace bags and drums on an annual basis or as needed

- Inspect all ductwork for cracks, holes or openings

- Reporting Requirements:

- Report any discrepancies to the Training & Risk Manager, and Facility Plant Manager

- Document and initial Maintenance Log and turn in to Training & Risk Manager

OPERATION & MAINTENANCE PLAN

Steelman Industrial Oven

1.	Daily – check temperature chart to insure afterburner temperature of 1400OF is reached and maintained for each run.

2.	Weekly – Blow out the burner air inlet with compressed air with oven not in operation.

3.	Semi-annually – Inspect for damage to the burner controls.

4.	Annually – Have thermocouple calibrated.  If any periods of low temperature occur, have it recalibrated.

Reporting Requirements:

- Report any discrepancies to the Training & Risk Manager, and Facility Plant Manager

- Document and initial Maintenance Log and turn in to Training & Risk Manager

OPERATION & MAINTENANCE PLAN

Bayco BB-536

1.	Daily – check temperature chart to insure afterburner temperature of 1200OF is reached and maintained for each run.

2.	Weekly – Blow out the burner air inlet with compressed air with oven not in operation.

3.	Semi-annually – Inspect for damage to the burner controls.

4.	Annually – Have thermocouple calibrated.  If any periods of low temperature occur, have it recalibrated.

Reporting Requirements:

- Report any discrepancies to the Training & Risk Manager, and Facility Plant Manager

- Document and initial Maintenance Log and turn in to Training & Risk Manager

OPERATION & MAINTENANCE PLAN

Bayco BB-42

1.	Daily – check temperature chart to insure afterburner temperature of 1200OF is reached and maintained for each run.

2.	Weekly – Blow out the burner air inlet with compressed air with oven not in operation.

3.	Semi-annually – Inspect for damage to the burner controls.

4.	Annually – Have thermocouple calibrated.  If any periods of low temperature occur, have it recalibrated.

Reporting Requirements:

- Report any discrepancies to the Training & Risk Manager, and Facility Plant Manager

- Document and initial Maintenance Log and turn in to Training & Risk Manager