ENVIRONMENTAL PROTECTION COMMISSION OF

HILLSBOROUGH COUNTY, as Delegated by

STATE OF FLORIDA

DEPARTMENT OF ENVIRONMENTAL PROTECTION

NOTICE OF PERMIT ISSUANCE

CERTIFIED MAIL

Tim Garris						File No.:  0570163-003-AO

District Manager					County:  Hillsborough

Griffin Industries, Inc.

1001 Orient Road

Tampa, FL 33619

______________________________/

Enclosed is Permit No. 0570163-003-AO to operate a rendering facility, issued pursuant to Section 403.087, Florida Statutes.  Please read this new permit thoroughly as there are changes from the previous permit.

The EPC will issue the final permit with the attached conditions unless a timely petition for an administrative hearing is filed pursuant to Section 120.569 and 120.57 F.S. before the deadline for filing a petition.  The procedures for petitioning for a hearing are set forth below.

A person whose substantial interests are affected by the proposed permitting decision may petition for an administrative proceeding (hearing) under Sections 120.569 and 120.57, F.S.  The petition must contain the information set forth below and must be filed (received) in the Legal Department of the EPC at 3629 Queen Palm Drive, Tampa, Florida 33619, Phone 813-627-2600, Fax 813-627-2602.  Petitions filed by the permit applicant or any of the parties listed below must be filed within 14 (fourteen) days of receipt of this notice of intent. Petitions filed by any persons other than those entitled to written notice under Section 120.60(3), F.S. must be filed within 14 (fourteen) days of receipt of this permit.  Under Section 120.60(3), however, any person who asked the EPC for notice of agency action may file a petition within 14 (fourteen) days of receipt of that notice, regardless of the date of publication.

Griffin Industries, Inc.							                                       Page Two

Tampa, FL  33619

A petitioner shall mail a copy of the petition to the applicant at the address indicated above, at the time of filing.  The failure of any person to file a petition within the appropriate time period shall constitute a waiver of that person's right to request an administrative determination (hearing) under Sections 120.569 and 120.57, F.S., or to intervene in this proceeding and participate as a party to it.  Any subsequent intervention will be only at the approval of the presiding officer upon the filing of a motion in compliance with Rule 28-106.205 of the F.A.C.

A petition that disputes the material facts on which the EPC’s action is based must contain the following information:

- The name and address of each agency affected and each agency’s file or identification number if known;

- The name, address, and telephone number of the petitioner and the name, address, and telephone number of each petitioner’s representative, if any, which shall be the address for service purposes during the course of the proceedings; and an explanation of how the petitioner’s substantial interests will be affected by the EPC’s determination;

- A statement of how and when the petitioner received notice of the EPC action;

(d) A statement of all disputed issues of material fact. If there are none, the petition must so indicate;

- A concise statement of the ultimate facts alleged, including the specific facts the petitioner contends warrant reversal or modification of the EPC’s proposed action;

- A statement of specific rules or statutes the petitioner contends requires reversal or modification of the EPC’s proposed action; and

- A statement of the relief sought by the petitioner, stating precisely the action petitioner wishes the EPC to take with respect to the EPC’s proposed action.

A petition that does not dispute the material facts upon which the EPC’s action is based shall state that no such facts are in dispute and otherwise shall contain the same information as set forth above as required by Rule 28-106.301.

Because the administrative hearing process is designed to formulate final agency action, the filing of a petition means that the EPC's final action may be different from the position taken by it in this notice. Persons whose substantial interests will be affected by any such final decision of the EPC on the application have the right to petition to become a party to the proceeding, in accordance with the requirements set forth above.

Mediation under section 120.573, F.S. is not available in this proceeding.

This action is final and effective on the date filed with the Clerk of the EPC unless a petition is filed in accordance with above.  Upon the timely filing of a petition, this order will not be effective until further order of the EPC.

Griffin Industries, Inc.							                                       Page Three

Tampa, FL  33619

Any person listed below may request to obtain additional information, a copy of the application (except for information entitled to confidential treatment pursuant to Section 403.111, F.S.), all relevant supporting materials, and all other materials available to the EPC that are relevant to the permit decision.  Interested persons may contact Diana M. Lee, P.E., at the above address or call (813) 627-2600, for additional information.

Any party to this order has the right to seek judicial review of it under Section 120.68 of the Florida Statues, by filing a notice of appeal under rule 9.110 of the Florida rules of Appellate Procedure with the EPC’s Legal Office at 3629 Queen Palm Drive, Tampa, Florida 33619 and with the clerk of the Department of Environmental Protection in the Office of General Counsel, Mail Station 35, 3900 Commonwealth Boulevard, Tallahassee, Florida 32399-3000, and by filing a copy of the notice of appeal accompanied by the applicable filing fees with the appropriate district court of appeal.  The notice must be filed within thirty days after this order is filed with the clerk of the Department.

Executed in Tampa, Florida

ENVIRONMENTAL PROTECTION COMMISSION

OF HILLSBOROUGH COUNTY

__________________________________

Richard D. Garrity, Ph.D.

Executive Director

RDG/KRZ/krz

Griffin Industries, Inc.							                                       Page Four

Tampa, FL  33619

CERTIFICATE OF SERVICE

This is to certify that this NOTICE OF PERMIT and all copies were mailed before the close of business on _________________________ to the listed persons.

FILING AND ACKNOWLEDGEMENT FILED, on this

date, pursuant to Section 120.52(7),

Florida Statutes, with the clerk, receipt 										of which is hereby acknowledged.

_____________________________ ___________

Clerk				           Date

PERMITTEE:							PERMIT/CERTIFICATION

Griffin Industries, Inc.						Permit No:  0570163-003-AO

1001 Orient Road						County:  Hillsborough

Tampa, FL  33619						Expiration Date:  August 22, 2013

Project:  Rendering Operation

This permit is issued under the provisions of Chapter 403, Florida Statutes, and Florida Administrative Code Rules 62-204, 62-210, 62-212, 62-296, 62-297, and 62-4.  The above named permittee is hereby authorized to perform the work or operate the facility shown on the application and approved drawing(s), plans and other documents, attached hereto or on file with the EPC and made a part of hereof and specifically described as follows:

For the operation of a rendering facility having two (2) high pressure steam heated cookers that are used to separate fat from meat or animal remains by slow heating and processing fat, bone, offal, and used restaurant grease.  Each cooker has a maximum input rate of 34,000 pounds per hour to produce tallow yellow grease and bone meal.

Each cooker has a water-cooled shell and a tube condenser to control condensable odor emissions generated from the cooking operation.  The two water-cooled shell and tube condensers operating in parallel are followed by two scrubbers in series, a Venturi Scrubber and a High Intensity Packed Bed Scrubber, to control non-condensable odor emissions from the tube condensers.  In both scrubbers, chlorine dioxide is injected as a scrubber agent for odor control.

There is a third scrubber used as a secondary odor control system to treat the process vapors from the dual scrubber system and the air drawn from the interior of the rendering plant.  This scrubber is a 50,000 cfm Room Air Scrubber.  It treats about 40,000 cfm of in-plant air and 10,000 cfm of pretreated process vapors from the existing 2-stage scrubber system.

In addition, there is a tertiary odor control system, which sprays a mist of Whoof compound around the opening gate at the truck unloading/receiving pit area for the purpose of masking odors in the immediate raw material unloading area.

Two steam boilers, one rated at 62.76 MMBtu/hr and the other one rated at 31.38 MMBtu/hr, supply process steam for use in the two cookers.  Both boilers are fired primarily on natural gas with backup of virgin No. 2 fuel oil with less than 0.05% sulphur content by weight.  Both the boilers are exempted from permitting based on Rule 62-210.300(3)(a), F.A.C. and the EPC permit determination letter dated March 6, 2000.

The maker and model numbers for the control equipment are provided as below:

| Equipment | Manufacturer | Model No. | Serial No.* |
| --- | --- | --- | --- |
| Cooker | Dupps Company | 1500 Equacooker | N/A |
| Cooker | Dupps Company | 1500 Equacooker | N/A |
| Shell and tube condenser | Dupps Company | 12 SS | N/A |
| Shell and tube condenser | Dupps Company | 12 SS | N/A |
| Venturi Scrubber | 10,000 ACFM SCP Control Inc. | 8” x 20” | N/A |
| Packed Bed Scrubber | 10,000 ACFM GPI Corporation | #4468 60” x 258” | PO # 1444 |
| Room Air Scrubber | 50,000 ACFM American Fan Co. | BI-490 | N/A |

N/A - Serial number was not available at the time inquired by the EPC during this permit renewal.

Location:  1001 Orient Road, Tampa, FL 33619

UTM:  17-364.0 E 3096.4 N

NEDS NO:  0570163

EU 003 – Rendering Operation

Reference Permit No.:	0570163-002-AO

1.	A part of this permit is the attached General Conditions. [Rule 62-4.160, F.A.C.]

2.	All applicable rules of the Environmental Protection Commission of Hillsborough County including design discharge limitations specified in the application shall be adhered to.  The permit holder may also need to comply with county, municipal, federal, or other state regulations prior to construction.

[Rule 62-4.070(7), F.A.C.]

3.	Issuance of this permit does not relieve the permittee from complying with applicable emission limiting standards or other requirements of Chapters 62-204, 62-210, 62-212, 62-296 and 62-297, F.A.C., or any other requirements under federal, state, or local law. [Rule 62-210.300, F.A.C.]

4.	The permittee shall not cause, suffer, allow or permit the discharge of air pollutants which cause or contribute to an objectionable odor. [Rule 62-296.320, F.A.C.]

5.	The input rate at each Cooker shall not exceed 34,000 lb/hr of processing fat, bones, offal, and restaurant grease. [Rule 62-4.070(1), F.A.C. and Construction Permit No. AC29-106753]

6.	In order to ensure compliance with Specific Condition No. 4, the following shall apply to this rendering operation: [Rule 62-4.070(3), F.A.C.]

A)	The odor control systems, which include water-cooled shells and tube condensers, and scrubbers, must be properly maintained, and operated whenever there is material being processed in the cookers.

B)	Raw materials shall be restricted to animal by-products and grease.

C)	Raw materials shall be processed as soon as reasonably practicable upon delivery to the facility.  If raw materials are not processed within 24 hours after delivery to the facility due to an operational breakdown or plant upset, the permittee shall notify the EPC regarding the operational breakdown or plant upset and the estimated time frame for completing processing of raw materials.

D)	The water in the line returning from either of the two condensers following the cookers shall not exceed 140o F.

7.	The following Operation and Maintenance Plan for the odor control systems shall be strictly adhered to: [Rule 62-4.070(1), F.A.C.]

A)	The following performance parameters of the sources and the odor control/monitoring system shall be maintained within the specified operating ranges below:

1)	High Intensity Packed Bed Scrubber pressure drop:  2-8 inches H2O

2)	Room Air Scrubber pressure drop:  1-5 inches H2O

3)	Scrubbing liquid flow rate to the High Intensity Packed Bed Scrubber spray nozzles:

minimum of 100 gpm

4)	Scrubbing liquid flow rate to the Room Air Scrubber nozzles: normal, 450 gpm

5)	Total liquid flow rate (make up and recirculating) to Venturi Scrubber:  Minimum of 40

gpm

6)	pH of scrubbing liquid to the High Intensity Packed Bed and Room Air Scrubbers:  not to \

exceed 9

- Oxidation-Reduction Potential (ORP) of scrubber liquid to the High Intensity Packed Bed

and Room Air Scrubber as measured at the line leading to/supplying spray nozzles:  minimum 500 mV (10 ppm)*

8)	Cookers Temperature Range:  not to exceed 300o F*

*  The ORP may be operated at a higher mV value, as necessary, in order to minimize objectionable odors.  The cooker temperature upper limit may be exceeded up to 320 oF for no longer than 15 minutes in any single hour.  Operating under either or both of these conditions does not exempt the permittee from complying with Specific Condition No. 4 of this permit.

B)	The following observations, checks, and operations apply to this source and shall be conducted and recorded on the schedule specified:

Daily (While Operating)

1)	Check the pressure drop across the High Intensity Packed Bed and Room Air Scrubbers

(hourly).

- Check the scrubbing liquid flow rate to the Venturi, High Intensity Packed Bed and Room

Air Scrubbers (hourly).

3)	Check the pH of the High Intensity Packed Bed and Room Air Scrubbers scrubbing liquid

reservoir (hourly).

4)	Check the amp meter for the fan serving the Room Air Scrubber.

5)	Continuously monitor and record the ORP of the scrubbing liquid in the High Intensity

Packed Bed and Room Air Scrubbers.

6)	Continuously monitor and record process temperature of each cooker.

7)	Good housekeeping practices shall be adhered to.

Every Other Month:

- Cleaning procedure for High Intensity Packed Bed Scrubber:

- Check the packed tower for grease build-up.

- Caustic wash the tower with 20-gallons for 2 hours.

- Caustic wash the Venturi scrubber with 15-gallons for 2 hours.

- Drain both systems - fill with fresh water rinse for 1 hour.

- Drain both systems - fill with fresh water add 25 gallons 20% muriatic acid and wash for 3 hours.

- Drain both systems - fill with fresh water.

- Check ORP and pH probes.  Make sure they are clean and verify calibration.

- Turn on fan. Make sure pressure drop is reading as permit requires.

- Set valves to make sure the circulating pumps read what 	the permit requires for both systems.

- Before leaving system, make sure ORP and pH probes are reading what the permit requires.

- Cleaning Procedure for Room Air Scrubber:

- Check packed tower for grease build-up.

- Caustic wash tower with 55-gallons for 2 hours.

- Drain system fill with fresh water - rinse 1 hour.

- Drain system fill with fresh water.  Add 55 gallon 20% muriatic acid wash for 3 hours.

- Drain system - fill with fresh water.

- Check ORP and pH probes.  Make sure they are clean and verify calibration.

- Turn on fan.  Make sure pressure drop is reading as permit requires.

- Set valves to make sure the bleed is 10 gpm to outside scrubber.

- Before leaving system, make sure ORP and pH probes are reading what the permit requires.

- The following maintenance and operation shall apply to this source and shall be conducted on the schedule specified.

Weekly

1) Check all the fan bearings and lubricate if needed.

Monthly

1)	Check all drive belts and chains for wear and tension.

2)	Check the High Intensity Packed Bed and Room Air Scrubbers spray nozzles to ensure that there is a proper spray pattern.  Repair if necessary.

3)	Check all hoses and clamps.

4)	Calibrate all indicating equipment.

5)	Inspect housing for corrosion.

Quarterly

1)	Inspect paint on odor control systems.

Annually

- Check all bolts.

- Check welds.

- Calibrate ORP and pH controllers.

D)	Records:

Records of inspections, maintenance, and performance parameters required by the specific condition of this permit shall be retained for a minimum of two years and shall be made available to the Environmental Protection Commission of Hillsborough County upon request. [Rule 62-4.070(3), F.A.C.]

8.	All reasonable precautions shall be taken to prevent and control generation of unconfined emissions of particulate matter in accordance with the provision in Rule 62-296.320, F.A.C.  These provisions are applicable to any source, including, but not limited to, vehicular movement, transportation of materials, construction, alterations, demolition or wrecking, or industrial related activities such as loading, unloading, storing and handling. Reasonable precautions shall include, but not be limited to, the following:

A)	Maintenance of parking areas and yards.

B)	Removal of particulate matter from paved areas, buildings and work areas under control of the owner/operator.

9.	Excess emissions resulting from start-up, shutdown or malfunction of any emissions unit shall be permitted provided that (1) best operational practices to minimize emissions are adhered to and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24-hour period.

[Rule 62-210.700(1), F.A.C.]

10.	If the permittee is not able to comply with any of the provisions of this permit, in particular, maintenance of the operating parameters of the main and the secondary odor control systems, then the permittee shall report the problem to the Environmental Protection Commission of Hillsborough County by telephone or in writing no later than the next business day. [Rule 62-4.070(1), F.A.C.]

11.	The use of property, facilities, equipment, processes, products, or compounds, or the commission of paint overspraying or any other act, that causes or materially contributes to a public nuisance is prohibited, pursuant to the Hillsborough County Environmental Protection Act, Section 16, Chapter 84-446, Laws of Florida, as Amended.

12.	The permittee shall provide timely notification to the Environmental Protection Commission of Hillsborough County prior to implementing any changes that may result in a modification to this permit pursuant to Rule 62-210.200, F.A.C.  The changes do not include normal maintenance, but may include, and are not limited to, the following, and may also require prior authorization before implementation: [Rules 62-4.070(1) and 62-210.300, F.A.C.]

A)	Alteration or replacement of any equipment or major component of such equipment.

B)	Installation or addition of any equipment which is a source of air pollution.

13.	If the permittee wishes to transfer this permit to another owner, an "Application for Transfer of Air Permit" (DEP Form 62-210.900(7)) shall be submitted, in duplicate, to the Environmental Protection Commission of Hillsborough County within 30 days after the sale or legal transfer of the permitted facility. [Rule 62-4.120, F.A.C.]

14.	Prior to sixty days before the expiration of this operating permit, the permittee shall apply for a renewal of the permit using the current version of the permit renewal application form.  A renewal application shall be timely and sufficient.  If the application is submitted prior to sixty days before the expiration of the permit, it will be considered timely and sufficient.  If the renewal application is submitted at a later date, it will not be considered timely and sufficient unless it is submitted and made complete prior to the expiration of the operation permit.  When the application for renewal is timely and sufficient, the existing permit shall remain in effect until the renewal application has been finally acted upon by the EPC or, if there is court review of the final agency action, until a later date is required by Section 120.60, Florida Statutes. [Rule 62-4.090, F.A.C.]

ENVIRONMENTAL PROTECTION COMMISSION

OF HILLSBOROUGH COUNTY

_________________________________

Richard D. Garrity, Ph.D.

Page 6 of 6

Executive Director