FINAL DETERMINATION

FOR

University of South Florida

Hillsborough County

Construction Permit

Application Number

0570480-012-AC

Environmental Protection Commission of

Hillsborough County

Tampa, FL

May 2, 2012

FINAL DETERMINATION

The Environmental Protection Commission of Hillsborough County an Air Construction (AC) Permit No. 0570480-012-AC for the construction of a new 54 MMBtu/hr Natural Gas-fired English Boiler and Tube, Inc. Model No. 45-Os-250 Boiler (Boiler No. 7) as a replacement for Boiler No. 3 at the University of South Florida located at 4202 East Fowler Avenue, Tampa, FL  33620.

The initial Draft AC Permit was issued on March 14, 2012.  Comments from the facility were received on April 3rd and 6th, 2012, in which they requested that the type and model of the boiler be changed from a 55 MMBtu/hr Natural Gas/No. 2 Fuel Oil Cleaver Brooks to a 54 MMBtu/hr Natural Gas English Boiler and Tube Inc.   Also, the new replacement boiler will be fired on natural gas, exclusively.  The Revised Draft AC Permit was issued on April 17, 2012, and it reflected the requested changes as well as the fact that this new boiler will not be subject to the Area Source Boiler MACT of 40 CFR 63, Subpart JJJJJJ, since gas-fired boilers are exempt from this regulation pursuant to 40 CFR 63.11195(e), and can only burn solid or liquid fuels during periods of gas curtailment, gas supply emergencies, or periodic testing on liquid fuels for less than 48 hours during any calendar year.    The revised AC permit was uploaded into the FDEP’s website for the public to review.

Also, on April 17, 2012, the EPC received the proof of the Public Notice of Intent to Issue Permit (NOI), which was published in the La Gaceta on March 23, 2012.  EPC staff was not made aware that the applicant had done the publication the Draft AC permit, especially since EPC was in discussions with the applicant and also in the process of reviewing their comments.  The most significant change is that the new boiler is not subject to the NESHAP as originally reflected in the Draft AC permit. During subsequent discussions with the Jerry Kissel, PE consultant for USF, it was agreed that the facility will not be required to publish the revised draft AC permit, since the project is minor in nature and also no comments were received from the public during the processing of the permit or issuance of the draft AC permit.  In addition, it was agreed that the Final permit would be issued 14 days from receipt of the proof of publication to allow additional time for the public to provide comments.

No comments have been received from the public since the intent was published.

The final action of the Environmental Protection Commission of Hillsborough County is to issue the final permit.

ENVIRONMENTAL PROTECTION COMMISSION OF

HILLSBOROUGH COUNTY, as Delegated by

STATE OF FLORIDA

DEPARTMENT OF ENVIRONMENTAL PROTECTION

NOTICE OF PERMIT

Otis Singfield

Utilities Coordinator

University of South Florida

4202 East Fowler Avenue

Tampa, Fl 33620

Dear Mr. Singfield: 							Re:  Hillsborough County - AP

Enclosed is Permit No. 0570480-012-AC to construct Natural Gas-fired English Boiler and Tube, Inc. Model No. 45-Os-250 Boiler (Boiler No. 7) as a replacement for Boiler No. 3 at the University of South Florida located at 4202 East Fowler Avenue, Tampa, FL  33620.  This permit is issued pursuant to Section 403.087, Florida Statutes.

Any party to this order (permit) has the right to seek judicial review of the permit pursuant to Section 120.68, Florida Statutes, by the filing of a Notice of Appeal pursuant to Rule 9.110, Florida Rules of Appellate Procedure, with the Clerk of the EPC in the Legal Department at 3629 Queen Palm Dr, Tampa, FL  33619; and by filing a copy of the Notice of Appeal accompanied by the applicable filing fees with the appropriate District Court of Appeal.  The Notice of Appeal must be filed within 30 days from the date this Notice is filed with the clerk of the EPC.

Executed in Tampa, Florida.

Sincerely,

_______________________________

Richard D. Garrity, Ph.D.

Executive Director

RDG/KRZ/krz

cc:  Gerald Kissel, P.E. (via email)

CERTIFICATE OF SERVICE

This is to certify that this NOTICE OF PERMIT and all copies were mailed before the close of business on _________________________ to the listed persons.

Clerk Stamp

FILED, on this date, pursuant to Section 120.52(7), Florida Statutes, with the designated clerk, receipt of which is hereby acknowledged.

___________________________   _____________

Clerk			                     Date

PERMITTEE:                    	   		            PERMIT/CERTIFICATION

University of South Florida			 	 Permit No.:  0570480-012-AC

4202 East Fowler Avenue				  County:  Hillsborough

Tampa, FL  33620          				 Expiration Date:  March 14, 2013

Project: Construction of a New 54 MMBtu/hr English Boiler and Tube Inc. Boiler No. 7

This permit is issued under the provisions of Chapter 403, Florida Statutes, and Florida Administrative Code Rules 62-204, 62-210, 62-212, 62-296, 62-297, and 62-4.  The above named permittee is hereby authorized to perform the work or operate the facility shown on the application and approved drawing(s), plans, and other documents, attached hereto or on file with the EPC and made a part hereof and specifically described as follows:

This project authorizes the construction of a new 54 MMBtu/hr Natural Gas-fired English Boiler and Tube, Inc. Model No. 45-Os-250 Boiler (Boiler No. 7) as a replacement for Boiler No. 3 at the University of South Florida located at 4202 East Fowler Avenue, Tampa, FL  33620.  The facility’s operations are currently permitted under Operating Permit 0570480-011-AO, which includes the operation of two (2) English Boilers rated at 54 MMBtu/hr (Boiler No. 6 - EU No. 007) and 57 MMBtu/hr (Boiler No. 5 - EU No. 001), and a 56 MMBtu/hr Union Iron Boiler (Boiler No. 3 – EU No. 003).

The new Boiler No. 7 is subject to the 20% opacity standard Rule 62-296.406(1), F.A.C.  Although it is subject to NSPS 40 CFR, Subpart Dc, it is only subject to the recordkeeping requirements of 60.48c(a) and (c) because it only burns natural gas.  On the other hand, pursuant to Rule 62-296.406(2) and (3), F.A.C., the facility is required to control PM and SO2 emissions through the application of Best Available Control Technology (BACT), which is the firing of natural gas..  The combined maximum heat input for all three (3) boilers will be 165 MMBtu/hr.  Based upon the maximum heat input rate, the maximum natural gas usage for all three boilers is 1,445 106 ft3/yr, while the maximum No. 2 Fuel Oil usage is around 7,097,518 gal/yr. However, the facility has requested that the maximum permitted natural gas and fuel oil usage has been remains unchanged and is limited to 600 x 106 ft3/yr for all three boilers, and 804,600 gal/yr. for Boiler Nos. 5 and 6. This establishes a combined NOx, CO, SO2, PM, and VOC PTE of 30 tpy, 25.2 tpy, 2.9 tpy, and 2.3 tpy, 1.7 tpy.  Total HAP emissions are less than 10 tpy.

The new boiler is not subject to the Area Source Boiler MACT of 40 CFR 63, Subpart JJJJJJ, since the new boiler only burns natural gas and gas-fired boilers are exempt pursuant to 40 CFR 63.11195(e), and can only burn solid or liquid fuels during periods of gas curtailment, gas supply emergencies, or periodic testing on liquid fuels for less than 48 hours during any calendar year.

Location:  4202 East Fowler Avenue, Tampa, FL  33620

UTM:  17-360.8 	E 3104.8 N		Facility ID No.: 0570480

Point IDs:

| EU No. ID | Boiler ID | Description | Capacity (MMBtu/hr) |
| --- | --- | --- | --- |
| 001 | No. 5 | Steam Boiler- (East Most Stack) | 57 |
| 007 | No. 6 | Steam Boiler- (West Most Stack) | 54 |
| 003 (To be Replaced) | No. 3* | Steam Boiler- (East Most Stack) | 56 |
| 009 (New Replacement Boiler) | No. 7* | Steam Boiler- (East Most Stack) | 54 |

*Boiler No. 3 will vent to the East Most Stack until start-up of Boiler No. 7

when it will be shutdown.

References Permit No.:  0570480-011-AO

1.  	A part of this permit is the attached 15 General Conditions. [Rule 62-4.160, F.A.C.]

2.	All applicable rules of the Environmental Protection Commission of Hillsborough County including design discharge limitations specified in the application shall be adhered to.  The permit holder may also need to comply with county, municipal, federal, or other state regulations prior to construction.

[Rule 62-4.070(7), F.A.C.]

3.	Issuance of this permit does not relieve the permittee from complying with applicable emission limiting standards or other requirements of Chapters 62-204, 62-210, 62-212, 62-296 and 62-297, F.A.C., or any other requirements under federal, state, or local law. [Rule 62-210.300, F.A.C.]

4.	The amount of particulate matter and sulfur dioxide emissions from the boilers shall be limited by the firing of natural gas or No. 2 Fuel Oil as a back-up.  The No. 2 Fuel Oil shall have a maximum sulfur content not to exceed 0.05 percent by weight. [Rule 62-296.406, F.A.C., 40 CFR 60.42c(d), Construction Permit Application dated March 2, 2012, and BACT Determination dated March 13, 2012]

5.	Visible emissions from the boilers shall not exceed a density of 20% opacity except for one six-minute period per hour which opacity shall not exceed 27%. [Rule 62-296.406(1), F.A.C.]

6.	As requested by the permittee, in order to establish the facility as a Synthetic Minor for both criteria and Hazardous Air Pollutants (HAP), the HAP, as defined in Rule 62-210.200, F.A.C., emissions shall be less than 10 tons in any 12 consecutive month period for any individual HAP, and less than 25 tons in any 12 consecutive month period for any combination of HAPs.  [Rule 62-4.070(3), F.A.C.]

7.	The permittee shall not cause, suffer, allow or permit the discharge of air pollutants which cause or contribute to an objectionable odor. [Rule 62-296.320(2), F.A.C.]

8.	To ensure compliance with Specific Condition Nos. 4 and 5, the following restrictions and limitations shall apply for any consecutive twelve month period:

[Rule 62-4.070(3), F.A.C. and Permit Nos. 0570480-009-AC and 0570480-010-AO]

A)	Boilers (EU Nos. 001, 007, and 009) shall have the following maximum annual usage rates:

| Natural Gas | 165 MMBtu/hr | 600 MMCF |
| --- | --- | --- |
| No. 2 Fuel Oil | 165 MMBtu/hr | 802,460 gallons |

The annual usage rate means the total fuel utilized by Emission Unit Nos. 001, 007, and 009 during the past twelve months.

B)	Hours of operation are not restricted.

- All products of combustion must be vented through the stack

9.	Test Boiler No. 5 and Boiler No. 6 for visible emissions annually between October 1 and September 30 (once per federal fiscal year) with a target date of March 15 of each year.  After Boiler No. 3 has been shutdown, test Boiler No. 7 for visible emissions within 30 days after startup and annually thereafter.  Since Boiler No. 5 and Boiler No. 7 both utilize the East Most Stack, the visible emissions test may be performed simultaneously provided Specific Condition No. 11 is met for EU No. 001 and EU No. 009.  Submit two (2) copies of test data to the Air Compliance Section of the Environmental Protection Commission of Hillsborough County within 45 days of such testing.  Testing procedures shall be consistent with the requirements of 40 CFR 60 and Rule 62-297, F.A.C.

10.	Compliance with Specific Condition No. 4 shall be demonstrated by either of the following:

A)	A Certificate of Fuel Oil Analysis* from a fuel oil vendor or a vendor shipment receipt (bill of lading) showing delivery or low sulfur oil containing a maximum of 0.05% sulfur by weight or equivalent.

B)	Certificate of Fuel Oil Analysis* for a fuel oil sample taken during the visible emission compliance test shall be submitted in conjunction with the test results.

*According to ASTM Method D 975 [Rule 62-297.440, F.A.C.]

11.  	Compliance testing of each boiler must be accomplished during a period when it is cycling up to a normal high firing rate, or is continuously operated at capacity.  Capacity is defined as 90-100% of rated capacity.  If it is impracticable to test at capacity, then the boiler may be tested at less than capacity; in this case subsequent operation is limited to 110% of the test load until a new test is conducted.  Once the unit is so limited, then operation at higher capacities is allowed for no more than fifteen days for purposes of additional compliance testing to regain the rated capacity in the permit, with prior notification to the EPC.  The permittee shall submit a statement of the operating mode as part of the compliance test.  Failure to submit an operation mode statement or operating at conditions which do not reflect the normal operating conditions may invalidate the data. [Rules 62-4.070(3) and 62-297.310(2)(b), F.A.C.]

12. 	The annual visible emissions test shall be conducted while the boiler is running on No. 2 Fuel Oil, if the specific boiler has burned diesel oil for more than 400 hours in the previous 12 months, otherwise it shall be conducted while burning natural gas.  EPA Method 9 contained in 40 CFR 60, Appendix A and adopted by reference in Rule 62-297, F.A.C. shall be used to test for compliance.  Test results must include the sulfur content of the fuel if No. 2 Fuel Oil is burned.  The EPA Method 9 test shall be at least 60 minutes in duration.  The minimum requirements for stack sampling facilities, source sampling and reporting, shall be in accordance with Rule 62-297, F.A.C. and 40 CFR 60, Appendix A. [Rules 62-4.070(3) and 62-297.310(7)(a)3, F.A.C.]

13.	In order to demonstrate compliance with Specific Condition Nos. 8.A) and 12, the permittee shall:

[Rule 62-4.070(3), F.A.C. and Permit No. 0570480-009-AC]

A)	Maintain the existing fuel flow meters in good operating condition.

B)	Maintain No. 2 Fuel Oil usage records on-site for the most recent 24 months.  At a minimum the records shall contain the following:

a. 	The date and duration of all periods where No. 2 Fuel Oil is combusted by EU Nos. 001, 007, or 009.

b.	Based upon Specific Condition No. 13.B).a. above, maintain a monthly summary and rolling twelve month totals for the hours of operation in which No. 2 Fuel Oil is burned.

14.	The permittee shall comply with the following requirements for Boiler Nos. 5, 6, and 7:

[Rule 62-204.800, F.A.C.]

- University of South Florida shall furnish the EPC written notification of any physical or operational change to an existing facility which may increase the emission rate of any air pollutant to which a standard applies, unless that change is specifically exempted under an applicable subpart or in §60.14(e).  This notice shall be postmarked 60 days or as soon as practicable before the change is commenced and shall include information describing the precise nature of the change, present and proposed emission control systems, productive capacity of the facility before and after the change, and the expected completion date of the change.  The EPC may request additional relevant information subsequent to this notice. [40 CFR 60.7(a)(4)]

B)		The permittee shall maintain records of the occurrence and duration of any startup, shutdown, or malfunction in the operation of an affected facility; any malfunction of the air pollution control equipment; or any periods during which a continuous monitoring system or monitoring device is inoperative. [40 CFR 60.7(b)]

C)		The permittee shall maintain a file of all measurements, including performance testing measurements and all other information required by this part recorded in a permanent form suitable for inspection.  The file shall be retained for at least two years following the date of such measurements, maintenance, reports, and records. [40 CFR 60.7(f)]

D)		At all times, including periods of startup, shutdown, and malfunction, owners and operators shall, to the extent practicable, maintain and operate any affected facility including associated air pollution control equipment in a manner consistent with good air pollution control practice for minimizing emissions.  Determination of whether acceptable operating and maintenance procedures are being used will be based on information available to the EPC which may include, but is not limited to, monitoring results, opacity observations, review of operating and maintenance procedures, and inspection of the source. [40 CFR 60.11(d)]

E)		The opacity standards set forth in this permit shall apply at all times except during periods of startup, shutdown, malfunction, and as otherwise provided in the applicable standard. [40 CFR 60.11(c)]

F)		No owner or operator subject to the provisions of this part shall build, erect, install, or use any article, machine, equipment or process, the use of which conceals an emission which would otherwise constitute a violation of an applicable standard.  Such concealment includes, but is not limited to, the use of gaseous diluents to achieve compliance with an opacity standard or with a standard which is based on the concentration of a pollutant in the gases discharged to the atmosphere. [40 CFR 60.12]

15.	The permittee shall notify the Air Compliance Section of the Environmental Protection Commission of Hillsborough County at least 15 days prior to the date on which each formal compliance test is to begin of the date, time, and place of each such test, and the contact person who will be responsible for coordinating and having such test conducted.  [Rule 62-4.070(3) and 62-297.310(7)(a)9., F.A.C]

16.	Compliance with the emission limitations of Specific Condition No. 5 shall be determined using EPA Method 9 contained in 40 CFR 60, Appendix A and adopted by reference in Rule 62-297, F.A.C.  The minimum requirements for stack sampling facilities, source sampling and reporting, shall be in accordance with Rule 62-297, F.A.C. and 40 CFR 60, Appendix A.

17.  	In order to demonstrate compliance with Specific Condition Nos. 8 and 10, the permittee shall maintain fuel usage records for the emission units specified in Specific Condition 8A) and copies of certificates of fuel oil analysis.  The records shall be maintained on-site for the most recent 24 months.  The records shall be made available to the Environmental Protection Commission of Hillsborough County, state, or federal air pollution agency upon request.  The records shall include, but are not limited to, the following:

A)  Month & Year

B)  Monthly summary of the natural gas* and fuel oil usage

C)  Rolling (12) month total of the natural gas and fuel oil usage

*The Permittee must describe the necessary assumptions made to estimate the natural gas usage.  [Rule 62-4.070(3), F.A.C.]

18.	Submit to the Environmental Protection Commission of Hillsborough County each calendar year on or before April 1 for EU Nos. 001, 007, and 009, completed DEP Form 62-210.900(5), "Annual Operating Report for Air Pollutant Emitting Facility", for the preceding calendar year. [Rule 62-210.370(3), F.A.C.]

19.	When the Environmental Protection Commission of Hillsborough County (EPC) after investigation, has good reason (such as complaints, increased visible emissions or questionable maintenance of control equipment) to believe that any applicable emission standard contained in Rules 62-204, 62-210, 62-212, 62-296, or 62-297, F.A.C., or in a permit issued pursuant to those rules is being violated, it may require the owner or operator of the source to conduct compliance tests which identify the nature and quantity of pollutant emissions from the source and to provide a report on the results of said tests to the EPC. [Rule 62-297.310(7)(b), F.A.C.]

20.	The permittee shall provide timely notification to the Environmental Protection Commission of Hillsborough County prior to implementing any changes that may result in a modification to this permit pursuant to Rule 62-210.200, F.A.C., Modification.  The changes do not include normal maintenance, but may include, and are not limited to, the following, and may also require prior authorization before implementation: [Rules 62-210.300 and 62-4.070(3), F.A.C.]

A)	Alteration or replacement of any equipment or major component of such equipment.*

B)	Installation or addition of any equipment* which is a source of air pollution.

C)	The use of materials and fuels other than those authorized in this permit.

*Not applicable to routine maintenance, repair, or replacement of component parts of an emission unit.  The cost of replacement of component parts in an emission unit such as a boiler shall count toward the fixed capital cost for reconstruction. [Rule 40 CFR 60.15 and Rule 62-210.200, F.A.C.]

21.	All reasonable precautions shall be taken to prevent and control generation of unconfined emissions of particulate matter in accordance with the provision in Rule 62-296.320, F.A.C.  These provisions are applicable to any source, including, but not limited to, vehicular movement, transportation of materials, construction, alterations, demolition or wrecking, or industrial related activities such as loading, unloading, storing and handling.

22.	Appendix A is part of this permit.  It lists miscellaneous emission points such as small steam generators, hot water heaters, burners used in laboratories and other places.  All of these emission points are fired on natural gas, and considered insignificant emission units and exempt from permitting.  These points are not required to have individual gas meters or monthly recordkeeping.

23.	If the permittee wishes to transfer this permit to another owner, an "Application for Transfer of Permit" (DEP Form 62-210.900(7)) shall be submitted, in duplicate, to the Environmental Protection Commission of Hillsborough County within 30 days after the sale or legal transfer of the permitted facility. [Rule 62-4.120, F.A.C.]

24.	A minimum of two copies of an application for an Air Permit – Non-Title V Source, DEP Form No. 62-210.900(3), to incorporate this construction permit into Operating Permit No. 0570480-011-AO, along with completion of compliance testing shall be submitted to the Environmental Protection Commission of Hillsborough County after completion of the construction, or at least 60 days prior to the expiration date of this permit, whichever occurs first. [Rules 62-4.050(2) and 62-4.220, F.A.C.]

ENVIRONMENTAL PROTECTION COMMISSION

OF HILLSBOROUGH COUNTY

_________________________________

Richard D. Garrity, Ph.D.

Executive Director

P.E. Certification Statement

Permittee:

University of South Florida					DRAFT Permit No.:  0570480-012-AC

Project Type:  Air Construction				Facility ID No.:  0570480

I HEREBY CERTIFY that the engineering features described in the above referenced application and subject to the proposed permit conditions provide reasonable assurance of compliance with applicable provisions of Chapter 403, Florida Statutes, and Florida Administrative Code Chapters 62-4 and 62-204 through 62-297.  However, I have not evaluated and I do not certify aspects of the proposal outside of my area of expertise (including but not limited to the electrical, mechanical, structural, hydrological, and geological features).

(Seal)

__________________________  _______________

Sterlin K. Woodard,  P.E.                       	Date

Registration No.: 52809

Permitting Authority:

Environmental Protection Commission

of Hillsborough County

Air Management Division

3629 Queen Palm Dr

Tampa, FL  33619

Telephone:  (813) 627-2600

Fax:  (813) 627-2660