### TECHNICAL EVALUATION

&

PRELIMINARY DETERMINATION

#### APPLICANT

Florida Municipal Power Agency (FMPA)

P.O. Box 6100

Key West, Florida  33041-6100

Stock Island Power Plant

Facility ID No. 0870003

#### PROJECT

# Project No. 0870003-013-AC

Application for Minor Source Air Construction Permit

Diesel Engine Hours of Operation

#### COUNTY

Monroe County, Florida

PERMITTING AUTHORITY

Florida Department of Environmental Protection

Division of Air Resource Management

Office of Air Permitting and Compliance

Power Plant Group

April 9, 2012

1.  General Project INFORMATION

Air Pollution Regulations

Projects at stationary sources with the potential to emit air pollution are subject to the applicable environmental laws specified in Section 403 of the Florida Statutes (F.S.).  The statutes authorize the Department of Environmental Protection (Department) to establish regulations regarding air quality as part of the Florida Administrative Code (F.A.C.), which includes the following applicable chapters:  62-4 (Permits); 62-204 (Air Pollution Control – General Provisions); 62-210 (Stationary Sources – General Requirements); 62-212 (Stationary Sources – Preconstruction Review); 62-213 (Operation Permits for Major Sources of Air Pollution); 62-296 (Stationary Sources - Emission Standards); and 62-297 (Stationary Sources – Emissions Monitoring).  Specifically, air construction permits are required pursuant to Rules 62-4, 62-210 and 62-212, F.A.C.

In addition, the U. S. Environmental Protection Agency (EPA) establishes air quality regulations in Title 40 of the Code of Federal Regulations (CFR).  Part 60 specifies New Source Performance Standards (NSPS) for numerous industrial categories.  Part 61 specifies National Emission Standards for Hazardous Air Pollutants (NESHAP) based on specific pollutants.  Part 63 specifies NESHAP based on the Maximum Achievable Control Technology (MACT) for numerous industrial categories.  The Department adopts these federal regulations on a quarterly basis in Rule 62-204.800, F.A.C.

Facility Description and Location

The Florida Municipal Power Agency (FMPA) Stock Island Plant is an existing electrical generation power plant, which is categorized under Standard Industrial Classification Code No. 4911.  The facility is located in Monroe County, at 6900 Front Street, in Stock Island, Florida.  The Universal Transverse Mercator (UTM) coordinates of the existing facility are Zone 17, 425.65 kilometer (km) East, and 2716.67 km North.  This site is in an area that is in attainment (or designated as unclassifiable) for all air pollutants subject to state and federal Ambient Air Quality Standards (AAQS).

Facility Regulatory Categories

- The facility is not a major source of hazardous air pollutants (HAP).

- The facility has units subject to the acid rain provisions of the Clean Air Act.

- The facility is a Title V major source of air pollution in accordance with Chapter 213, F.A.C.

- The facility is a major stationary source in accordance with Rule 62-212.400, F.A.C., for the Prevention of Significant Deterioration (PSD) of Air Quality.

- Project Description

- The existing facility previously contained three high-speed peaking generators powered by diesel fuel-fired engines.  Two of the three units were taken out of service as of December 28, 2009.  The third engine, designated as the EP2 engine (Emissions Unit 003 in the Air Resource Management System (ARMS) data base), was refurbished in 2010.  It is currently treated as an emissions unit that is exempt from permitting since FMPA accepted a fuel usage limit of 32,000 gallons of diesel fuel oil per year for this engine.  Because the engine has the potential to burn approximately 159 gallons of oil per hour, the self-imposed fuel usage limit will currently only allow operation for up to approximately 200 hours per year.  FMPA is requesting the authority to more fully utilize this generator to provide electrical energy to the local grid during periods of peak demand.  Providing this peak energy generation capability will allow FMPA to better meet near-term demand increases and to delay the need to invest capital in new power production units.  FMPA has provided information to show that this engine can be operated up to a maximum of 2,500 hours per year without triggering a net significant increase in actual emissions pursuant to the prevention of significant deterioration (PSD) rules.  However, any increase in actual emissions is considered to be a modification that requires an air construction permit to implement.

Processing Schedule

January 11, 2012.	Received application for a Title V air operation permit revision.

January 13, 2012.	Received a resubmitted application to include a signed request for a concurrent minor source air pollution construction permit; application deemed complete.

2.  PSD Applicability

General PSD Applicability

For areas currently in attainment with the state and federal AAQS or areas otherwise designated as unclassifiable, the Department regulates major stationary sources of air pollution in accordance with Florida’s PSD preconstruction review program as defined in Rule 62-212.400, F.A.C.  Under preconstruction review, the Department first must determine if a project is subject to the PSD requirements (“PSD applicability review”) and, if so, must conduct a PSD preconstruction review.  A PSD applicability review is required for projects at new and existing major stationary sources.  In addition, proposed projects at existing minor sources are subject to a PSD applicability review to determine whether potential emissions from the proposed project itself will exceed the PSD major stationary source thresholds.  A facility is considered a major stationary source with respect to PSD if it emits or has the potential to emit:

- 250 tons per year or more of any regulated air pollutant; or

- 100 tons per year or more of any regulated air pollutant and the facility belongs to one of the following 28 PSD-major facility categories:  fossil fuel-fired steam electric plants of more than 250 million British thermal units per hour heat input, coal cleaning plants (with thermal dryers), Kraft pulp mills, portland cement plants, primary zinc smelters, iron and steel mill plants, primary aluminum ore reduction plants, primary copper smelters, municipal incinerators capable of charging more than 250 tons of refuse per day, hydrofluoric, sulfuric, and nitric acid plants, petroleum refineries, lime plants, phosphate rock processing plants, coke oven batteries, sulfur recovery plants, carbon black plants (furnace process), primary lead smelters, fuel conversion plants, sintering plants, secondary metal production plants, chemical process plants, fossil fuel boilers (or combinations thereof) totaling more than 250 million British thermal units per hour heat input, petroleum storage and transfer units with a total storage capacity exceeding 300,000 barrels, taconite ore processing plants, glass fiber processing plants and charcoal production plants.

Once it is determined that a project is subject to PSD preconstruction review, the project emissions are compared to the “significant emission rates” defined in Rule 62-210.200, F.A.C. for the following pollutants:  carbon monoxide (CO); nitrogen oxides (NOX); sulfur dioxide (SO2); particulate matter (PM); particulate matter with a mean particle diameter of 10 microns or less (PM10); volatile organic compounds (VOC); lead (Pb); fluorides (Fl); sulfuric acid mist (SAM); hydrogen sulfide (H2S); total reduced sulfur (TRS), including H2S; reduced sulfur compounds, including H2S; municipal waste combustor organics measured as total tetra- through octa-chlorinated dibenzo-p-dioxins and dibenzofurans; municipal waste combustor metals measured as particulate matter; municipal waste combustor acid gases measured as SO2 and hydrogen chloride (HCl); municipal solid waste landfills emissions measured as non-methane organic compounds (NMOC); and mercury (Hg).  In addition, significant emissions rate also means any emissions rate or any net emissions increase associated with a major stationary source or major modification which would construct within 10 kilometers of a Class I area and have an impact on such area equal to or greater than 1 μg/m3, 24-hour average.

If the potential emission exceeds the defined significant emissions rate of a PSD pollutant, the project is considered “significant” for the pollutant and the applicant must employ the Best Available Control Technology (BACT) to minimize the emissions and evaluate the air quality impacts.  Although a facility or project may be major with respect to PSD for only one regulated pollutant, it may be required to install BACT controls for several “significant” regulated pollutants.

PSD Applicability for Project

Although EP2 is currently exempt from permitting with the fuel usage limit, the refurbished engine is subject to the requirements of 40 CFR 60 Subpart IIII.  Per 40 CFR 60.4201(d), this engine must meet the emission standards for new marine compression ignition engines in 40 CFR 94.8, since the engine displacement is 10.6 liters per cylinder.  Per 40 CFR 94.8, Table A-1, these standards are as follows:  7.8 grams per kilowatt (kW)-hour (hr) of combined NOX and total hydrocarbons (THC), 5.0 grams per kW-hr of CO and 0.27 grams per kW-hr of PM.  It has been determined, and will be confirmed below, that the critical pollutant for triggering PSD is NOX.  For NOX, the PSD significant emission rate is 40 tons per year.  Based on the NOX standard in 40 CFR 94.8, this 2,250 kilowatt engine has the potential to emit 17,550 grams per hour of combined NOX and THC.  The 0.0015% sulfur limit is required from 40 CFR 80.510(b).

Prior to the renewal in 2009, the last permitting exercise at this facility was the addition of Emissions Unit 011, combustion turbine 4, in October 2005.  This is more than 5 years ago; so the emissions increase associated with that permitting action is not considered contemporaneous with this current action.  As mentioned above, the facility operated 3 high speed diesel engines until December 28, 2009, when they were taken out of service, one being refurbished (EP2).  The reduction in NOX emissions associated with the removal of these engines can be considered contemporaneous with this current action.  During their last two years of operation, their NOX annual emissions were 6.85 tons in 2008 and 11.21 tons in 2009, averaging 9.03 tons.  This can be added to the 40 ton significant emission rate for NOX to estimate the maximum number of hours that the EP2 engine can be operated without triggering PSD:

(49.03 tons/year)(2,000 pounds/ton)(453.6 grams/pound)(hour/17,550 grams) = 2,534 hours/year

Note:  (7.8 grams/kW-hour)(2,250 kilowatts) = 17,550 grams/hour

With this permit revision application, FMPA is requesting 2,500 hours of operational time for the EP2 engine.  Since there are no contemporaneous emissions increases associated with this action, and there are 9.03 tons of contemporaneous NOX emissions decreases, the net emissions change can be estimated as follows:

(7.8 grams/kW-hour)(pounds/453.6 grams)(ton/2,000 pounds)(2,500 hours/year)(2,250 kW) – 9.03 tons = 39.3 tons/year

Since the emission limit of 7.8 grams per kW-hr includes THC emissions and since FMPA is not requesting all 2,534 hours, this provides reasonable assurance that the significant emission rate will not be exceeded.

For CO, PM and PM-10, potential emissions can be estimated similarly and are listed in Table 1, below.  Note that, for these pollutants, no credit is taken for contemporaneous emissions decreases, which provides additional assurance that the significant emission rates will not be exceeded.

For VOC, the emission factor for TOC from AP-42 Table 3.4-1 can be used to estimate emissions as follows:

(7.05 x 10-4 pounds/hp-hour)(1.341 hp/kW)(ton/2,000 pounds)(2,500 hours/year)(2,250 kW) = 2.65 tons/year

For CO2, lead, fluorides and mercury, emissions are estimated similarly, using the emission factors shown, and assuming a diesel fuel density of 7 pounds per gallon and heat content of 140,000 Btu per gallon.  For SO2, sulfuric acid mist, hydrogen sulfide and TRS, all of the available sulfur in the fuel at the fuel sulfur limit of 0.0015 percent is assumed to be converted to the relevant pollutant and all TRS is assumed to be hydrogen sulfide.  Again, for all of these pollutants, the estimates do not include contemporaneous emissions decreases.  As shown in Table 1 all of the potential emissions from the EP2 engine operating at 2,500 hours per year are less than the significant emission rates.  Therefore, a PSD analysis is not required for this proposed permit revision.

Table 1.  Potential Emissions from the EP2 Engine

| Pollutant | Emission Limit (gm/kW-hr) | Emission Factor | Source | Potential emissions (tons/year) | Significant Emission Rate (tons) |
| --- | --- | --- | --- | --- | --- |
| NOX | 7.8 |  |  | 39.31 | 40 |
| CO | 5 |  |  | 31 | 100 |
| PM | 0.27 |  |  | 1.67 | 25 |
| PM10 | 0.27 |  |  | 1.67 | 15 |
| SO2 |  | 0.0015 % sulfur |  | 0.0417 | 40 |
| TOC |  | 7.05 x 10-4 lb/hp-hr | AP-42 Table 3.4-1 | 2.65 | 40 |
| CO2 |  | 1.16 lb/hp-hr | AP-42 Table 3.4-1 | 4,375 | 75,000 |
| SAM |  | 0.0015 % sulfur |  | 0.0639 | 7 |
| Lead |  | 9 lb/1012 Btu | AP-42 Table 1.3-10 | 0.0003 | 0.6 |
| Fluorides2 |  | 0.0373 lb/1,000 gal | AP-42 Table 1.3-11 | 0.0074 | 3 |
| H2S |  | 0.0015 % sulfur |  | 0.0222 | 10 |
| TRS |  | 0.0015 % sulfur |  | 0.0222 | 10 |
| Mercury |  | 3 lb/1012 Btu | AP-42 Table 1.3-10 | 0.00008 | 0.1 |

1Includes 9.03 tons of contemporaneous emissions credits

2Emission factor for #6 fuel oil

3.  Application Review

Discussion of Emissions

As shown in the above tables, none of the projected emissions increases exceed the PSD significant increase rates.  Therefore, this proposed project is not subject to a Best Available Control Technology (BACT) determination at the requested allowable operation of up to 500 hours per year.  Pursuant to Rule 62-212.400(12), F.A.C., if the emissions unit ever exceeds 2,534 hours in any consecutive 12-month period, the PSD and BACT requirements shall apply as though construction had not yet commenced on the source.

State Requirements

Rule 62-296.320(4)(b)1 (General Visible Emissions Standard), Florida Administrative Code (F.A.C.), applies to this project.

Federal NSPS and NESHAP Provisions

This emissions unit, a compression ignition (CI) reciprocating internal combustion engine, is regulated under 40 CFR 63, Subpart ZZZZ, NESHAP for Stationary Reciprocating Internal Combustion Engines (RICE) adopted in Rule 62.204.800(11)(b), F.A.C. and 40 CFR 60, Subpart IIII, NSPS.  This RICE is not used as a fire pump.  It is located at a non-major source of HAP and has been modified, reconstructed or commenced construction on or after 6/12/2006 and has a post-2007 model year.

Other Draft Permit Requirements

There are no additional production and operation limitations, monitoring requirements, etc., because of this project.

4.  Preliminary Determination

The Department makes a preliminary determination that the proposed project will comply with all applicable state and federal air pollution regulations as conditioned in the draft permit.  This determination is based on a technical review of the complete application, reasonable assurances provided by the applicant, and the conditions specified in the draft permit.  Tom Cascio is the project engineer responsible for reviewing the application and drafting the permit.  Additional details of this analysis may be obtained by contacting the project engineer at the Office of Air Permitting and Compliance, 2600 Blair Stone Road, Tallahassee, Florida  32399-2400.