Sent by Electronic Mail – Received Receipt Requested

Permittee

| Florida Municipal Power Agency (FMPA) P.O. Box 6100 Key West, Florida 33041-6100 Authorized Representative: Edward Garcia, Director of Generation | Air Permit No. 0870003-013-AC Permit Expires: December 31, 2012 Minor Source Air Construction Permit Stock Island Power Plant Diesel Engine Hours of Operation Increase |
| --- | --- |

This is the final air construction permit, which authorizes an annual limit of 2,500 hours of operation for the EP2 diesel engine (EU 003) at the facility.  The proposed work will be conducted at the Stock Island Power Plant, which is a power generation plant (Standard Industrial Classification No. 4911).  The facility is located in Monroe County, at 6900 Front Street, in Stock Island, Florida.  The Universal Transverse Mercator (UTM) coordinates are Zone 17, 425.65 East; and 2716.67 North.

This final permit is organized into the following sections:  Section 1 (General Information); Section 2 (Administrative Requirements); Section 3 (Emissions Unit Specific Conditions); Section 4 (Appendices).  Because of the technical nature of the project, the permit contains numerous acronyms and abbreviations, which are defined in Appendix A of Section 4 of this permit.  As noted in the Final Determination provided with this final permit, no changes were made to the draft permit.

This air pollution construction permit is issued under the provisions of:  Chapter 403 of the Florida Statutes (F.S.) and Chapters 62-4, 62-204, 62-210, 62-212, 62-296 and 62-297 of the Florida Administrative Code (F.A.C.).  The permittee is authorized to conduct the proposed work in accordance with the conditions of this permit.  This project is subject to the general preconstruction review requirements in Rule 62-212.300, F.A.C. and is not subject to the preconstruction review requirements for major stationary sources in Rule 62-212.400, F.A.C. for the Prevention of Significant Deterioration (PSD) of Air Quality.

Upon issuance of this final permit, any party to this order has the right to seek judicial review of it under Section 120.68 of the Florida Statutes by filing a notice of appeal under Rule 9.110 of the Florida Rules of Appellate Procedure with the clerk of the Department of Environmental Protection in the Office of General Counsel (Mail Station #35, 3900 Commonwealth Boulevard, Tallahassee, Florida, 32399-3000) and by filing a copy of the notice of appeal accompanied by the applicable filing fees with the appropriate District Court of Appeal.  The notice must be filed within 30 days after this order is filed with the clerk of the Department.

Executed in Tallahassee, Florida

For the Division of Air Resource Management

(DRAFT)

________________________________________  __________

Jeffrey F. Koerner, P.E., Program Administrator     (Date)

Office of Permitting and Compliance

Division of Air resource Management

JFK/jh/tc

## CERTIFICATE OF SERVICE

The undersigned duly designated deputy agency clerk hereby certifies that this Final Air Permit package (including the Final Determination and Final Permit with Appendices) was sent by electronic mail, or a link to these documents made available electronically on a publicly accessible server, with received receipt requested before the close of business on the date shown in the Clerk’s Stamp to the persons listed below.

Edward Garcia, Florida Municipal Power Agency:  edward.garcia@keysenergy.com

# Jerome Guidry, P.E., Perigee Technical Services, Inc.:  jerome.guidry@att.net

# Ajaya Satyal, DEP South District Office:  ajaya.satyal@dep.state.fl.us

# Kathleen Forney, EPA Region 4:  forney.kathleen@epa.gov

# Barbara Friday, DEP Office of Air Permitting and Compliance:  barbara.friday@dep.state.fl.us

# Lynn Scearce, DEP Office of Air Permitting and Compliance:  lynn.scearce@dep.state.fl.us

# Clerk Stamp

# FILING AND ACKNOWLEDGMENT FILED, on this date, pursuant to Section 120.52(7), Florida Statutes, with the designated agency clerk, receipt of which is hereby acknowledged.

(DRAFT)

_____________________________________     ________________

(Clerk)	(Date)

Facility and Project Description

Existing Facility

This facility consists of seven regulated emission units:  Two diesel generators, four simple-cycle combustion turbines and a compression ignition (CI) peaking engine.  The total generating capacity of these units is 130.89 megawatts (MW).  To reduce pollution, a combination of control techniques is used including water injection, ignition timing retardation, and low sulfur fuel oil.  A selective catalytic reduction (SCR) unit must be installed to help control its NOX emissions when the operational hours of the 48 MW simple-cycle combustion turbine (EU 011) exceeds 2,500 hours, based on a 12 month rolling total.  The one CI engine (diesel peaking unit EU 003) is regulated under 40 CFR 63 Subpart ZZZZ and 40 CFR 60 Subpart IIII.  It was recently reconstructed.

| ID No. | Emission Unit Description |
| --- | --- |
| 003 | EP2 Diesel Peaking Unit #2 (2250 kW/3070 HP; 10.6 L/cylinder; 16 cylinders) - originally built in 1964; reconstructed in 2010. |
| 005 | 8.8 MW Medium Speed Diesel Generator [Unit #1; EPA ID D-1] |
| 006 | 8.8 MW Medium Speed Diesel Generator [Unit #2; EPA ID D-2] |
| 007 | 23.5 MW Simple Cycle Combustion Turbine [CT-1] |
| 008 | 19.77 MW Simple Cycle Combustion Turbine [CT-2] |
| 009 | 19.77 MW Simple Cycle Combustion Turbine [CT-3] |
| 011 | 48.00 MW Simple Cycle Combustion Turbine [CT4] |

Proposed Project

The existing facility previously contained three high-speed peaking generators powered by diesel fuel-fired engines.  Two of the three units were taken out of service as of December 28, 2009.  The third engine, designated as the EP2 engine (Emissions Unit 003 in the Air Resource Management System (ARMS) data base), was refurbished in 2010.  It is currently treated as an emissions unit that is exempt from permitting since FMPA accepted a fuel usage limit of 32,000 gallons of diesel fuel oil per year for this engine.  Because the engine has the potential to burn approximately 159 gallons of oil per hour, the self-imposed fuel usage limit will currently only allow operation for up to approximately 200 hours per year.  FMPA is requesting the authority to more fully utilize this generator to provide electrical energy to the local grid during periods of peak demand.  Providing this peak energy generation capability will allow FMPA to better meet near-term demand increases and to delay the need to invest capital in new power production units.  FMPA has provided information to show that this engine can be operated up to a maximum of 2,500 hours per year without triggering a net significant increase in actual emissions pursuant to the prevention of significant deterioration (PSD) rules.  However, any increase in actual emissions is considered to be a modification that requires an air construction permit to implement.

Facility Regulatory Classification

- The facility is not a major source of hazardous air pollutants (HAP).

- The facility has units subject to the acid rain provisions of the Clean Air Act (CAA).

- The facility is a Title V major source of air pollution in accordance with Chapter 213, F.A.C.

- The facility is a major stationary source in accordance with Rule 62-212.400(PSD), F.A.C.

- Permitting Authority:  The permitting authority for this project is the Office of Permitting and Compliance, Division of Air Resource Management, Florida Department of Environmental Protection (Department).  The Office of Permitting and Compliance’s mailing address is:  2600 Blair Stone Road (MS #5505), Tallahassee, Florida  32399-2400.

- Compliance Authority:  All documents related to compliance activities such as reports, tests, and notifications shall be submitted to the Department’s South District Office.  The mailing address and phone number of the South District Office are:  2295 Victoria Avenue, Suite 364, P.O. Box 2549, Fort Myers, Florida  33902; (239) 332-6975.

- Appendices:  The following Appendices are attached as part of this permit:  Appendix A (Citation Formats and Glossary of Common Terms); Appendix B (General Conditions): Appendix C (Common Conditions); Appendix D (Common Testing Requirements); and Appendix 40 CFR 60 Subpart A.

- Applicable Regulations, Forms and Application Procedures:  Unless otherwise specified in this permit, the construction and operation of the subject emissions units shall be in accordance with the capacities and specifications stated in the application.  The facility is subject to all applicable provisions of: Chapter 403, F.S.; and Chapters 62-4, 62-204, 62-210, 62-212, 62-213, 62-296 and 62-297, F.A.C.  Issuance of this permit does not relieve the permittee from compliance with any applicable federal, state, or local permitting or regulations.

- New or Additional Conditions:  For good cause shown and after notice and an administrative hearing, if requested, the Department may require the permittee to conform to new or additional conditions.  The Department shall allow the permittee a reasonable time to conform to the new or additional conditions, and on application of the permittee, the Department may grant additional time.  [Rule 62-4.080, F.A.C.]

- Modifications:  The permittee shall notify the Compliance Authority upon commencement of construction.  No new emissions unit shall be constructed and no existing emissions unit shall be modified without obtaining an air construction permit from the Department.  Such permit shall be obtained prior to beginning construction or modification.  [Rules 62-210.300(1) and 62-212.300(1)(a), F.A.C.]

- Source Obligation:

(a)	At such time that a particular source or modification becomes a major stationary source or major modification (as these terms were defined at the time the source obtained the enforceable limitation) solely by virtue of a relaxation in any enforceable limitation which was established after August 7, 1980, on the capacity of the source or modification otherwise to emit a pollutant, such as a restriction on hours of operation, then the requirements of subsections 62-212.400(4) through (12), F.A.C., shall apply to the source or modification as though construction had not yet commenced on the source or modification.

(b)	At such time that a particular source or modification becomes a major stationary source or major modification (as these terms were defined at the time the source obtained the enforceable limitation) solely by exceeding its projected actual emissions, then the requirements of subsections 62-212.400(4) through (12), F.A.C., shall apply to the source or modification as though construction had not yet commenced on the source or modification.

[Rule 62-212.400(12), F.A.C.]

This section of the permit addresses the following emissions unit.

| ID No. | Emission Unit Description |
| --- | --- |
| 003 | EP2 Diesel Peaking Unit #2 (2,250 kW/3,070 HP; 10.6 L/cylinder; 16 cylinders) - originally built in 1964; reconstructed in 2010; 6 foot stack height; 2 foot stack exit diameter. |

The following table provides important details for this emissions unit:

| Engine kW/HP | Date of Construction/ Reconstruction | Model Year | Primary Fuel | Type of Engine | Displacement in liters | Date of last modification or reconstruction |
| --- | --- | --- | --- | --- | --- | --- |
| 2,250 kW 3,070 HP | 1964/2010 | 1964 2010 | Diesel | Peaking | 169.6 (total) (10.9 l/cylinder) | 2010 |

{Permitting Note:  This compression ignition (CI) engine is regulated under 40 CFR 63, Subpart ZZZZ, National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines (RICE) adopted in Rule 62.204.800(11)(b), F.A.C. and 40 CFR 60, Subpart IIII, Standards of Performance for Stationary Compression Ignition Internal Combustion Engines.  Compliance with the requirements of 40 CFR 63, Subpart ZZZZ is met by meeting the requirements of 40 CFR 60, Subpart IIII.  No further requirements of 40 CFR 63, Subpart ZZZZ apply for this engine.  This permit section addresses a stationary CI RICE with a displacement greater than 10 liters per cylinder and less than 30 liters per cylinder, that is located at an area source of HAP and that has been reconstructed on or after 6/12/2006.  This engine was reconstructed to meet the same standards as a 2010 model year marine engine.}

Equipment

- Peaking Unit Diesel Engine:  The permittee is authorized to operate the existing diesel engine EP2 (ARMS ID No. 003) a maximum of 2,500 hours per calendar year.  [Application No. 0830007-013-AC; Rules 62-210.200 (Definitions - Potential to Emit (PTE) & 62-212.400(12), F.A.C.]

Performance Restrictions

- Authorized Fuel:  The Stationary Reciprocating Internal Combustion Engines (RICE) must use diesel fuel that meets the following requirements for non-road diesel fuel:

- Sulfur Content.  The sulfur content shall not exceed = 15 parts per million (ppm) = 0.0015% by weight (ultra low sulfur) for non-road fuel.

- Cetane and Aromatic.  The fuel must have a minimum cetane index of 40 or must have a maximum aromatic content of 35 volume percent.

[40 CFR 60.4207(b) and 80.510(b); Rule 62-210.200(PTE), F.A.C.]

- Operation and Maintenance:  The owner or operator must operate and maintain the stationary CI internal combustion engine according to the manufacturer's written instructions or procedures developed by the owner or operator that are approved by the engine manufacturer.  In addition, owners and operators may only change those settings that are permitted by the manufacturer.  The owner or operator must also meet the emission limits of 40 CFR 94.8.  [40 CFR 60.4211(a) & (c)]

##### Emissions Standards

- THC + NOX Emissions:  Total hydrocarbons (THC) and nitrogen oxides (NOX) emissions shall not exceed 7.8 grams per kilowatt hour (g/kW-hr).  [40 CFR 60.4204(b), 40 CFR 60.4201(d), 40 CFR 94.8]

- CO Emissions:  Carbon monoxide (CO) emissions shall not exceed 5.0 g/kW-hr.  [40 CFR 60.4204(b), 40 CFR 60.4201(d), 40 CFR 94.8]

- PM Emissions:  Particulate matter (PM) emissions shall not exceed 0.27 g/kW-hr.  [40 CFR 60.4204(b), 40 CFR 60.4201(d), 40 CFR 94.8]

Monitoring Requirements

- Hour Meter:  The owner or operator must install, maintain and operate a non-resettable hour meter.  [Rule 62-4.070, F.A.C.]

##### Compliance Requirements

- Initial Compliance Requirements:  Initial compliance shall be demonstrated by one of the following methods:

- Certification.  Purchasing, or otherwise owning or operating, an engine certified to the emission standards specified in Specific Conditions 4. – 6.

- Performance Tests.  Conducting a performance test to demonstrate initial compliance with the emission standards according to the requirements specified in §60.4212 or §60.4213, as appropriate.  The test must be conducted within 60 days after the engine commences operation after the modification or reconstruction.

[40 CFR 60.4211(e)]

- Subsequent Compliance Requirements:  If the owner or operator does not install, configure, operate, and maintain the engine according to the manufacturer's emission-related written instructions, or emission-related settings are changed in a way that is not permitted by the manufacturer, compliance must be demonstrated as follows:

- Maintenance Plan.  Keep a maintenance plan and records of conducted maintenance and must, to the extent practicable, maintain and operate the engine in a manner consistent with good air pollution control practice for minimizing emissions.

- Performance Tests.  In addition, an initial performance test must be conducted to demonstrate compliance with the emission limits in Specific Conditions 4. – 6. within 1 year of startup, or within 1 year after the engine is no longer installed, configured, operated, and maintained in accordance with the manufacturer's emission-related written instructions, or within 1 year after the emission-related settings are changed in a way that is not permitted by the manufacturer.  Subsequent performance testing must be conducted every 8,760 hours of engine operation or 3 years, whichever comes first, thereafter to demonstrate compliance with the emission limits.

[40 CFR 60.4211(g)(3)]

- Testing Requirements:  Any required performance tests must be conducted according to the following:

- The performance test must be conducted according to the in-use testing procedures in 40 CFR 1042, Subpart F, which also references 40 CFR 1065, available at the following links:
40 CFR 1042 – Control of Emissions From New and In-use Marine Compressions-Ignition Engines 
40 CFR 1065 – Engine Testing Procedures

- Exhaust emissions must not exceed the not to exceed (NTE) numerical requirements, rounded to the same number of decimal places as the standards in Specific Conditions 4. – 6., determined from the following equation:  NTE requirement for each pollutant = (1.25) x (Standard).

[40 CFR 60.4212(a) – (c)]

Records and Reports

- Test Report:  The results of any required compliance shall be submitted to the Department’s South District Office.  See Appendix D, Common Testing Requirements.  [Rule 62-297, F.A.C.]

- Annual Operating Report:

a.	The permittee shall submit to the Compliance Authority, each calendar year, on or before April 1st, a completed DEP Form No. 62-210.900(5), “Annual Operating Report for Air Pollutant Emitting Facility”, for the preceding calendar year.

b.	Emissions shall be computed in accordance with the provisions of Rule 62-210.370(2), F.A.C.

[Rules 62-210.370(2) & (3), and 62-213.440(3)(a)2., F.A.C.]

- Notifications and Records:  The following requirements must be met:

- Initial Notification.  Submit an initial notification as required in §60.7(a)(1).  The notification must include the following information:

  - Name and address of the owner or operator;

  - The address of the affected source;

  - Engine information including make, model, engine family, serial number, model year, maximum engine power, and engine displacement;

  - Emission control equipment; and

  - Fuel used.

- Records.  The following records must be kept:

  - All notifications submitted to comply with this subpart and all documentation supporting any notification.

  - Maintenance conducted on the engine.

  - If the stationary CI internal combustion is a certified engine, documentation from the manufacturer that the engine is certified to meet the emission standards.

  - If the stationary CI internal combustion is not a certified engine, documentation that the engine meets the emission standards.

[40 CFR 60.4214(a)]

- Record Retention:

- The owner or operator must keep records in a suitable and readily available form for expeditious reviews.  Year-to-date hours of operation of the unit and fuel usage in gallons for the unit are to be monitored and recorded.  Records concerning maintenance conducted on the engine must also be kept, and documentation from the manufacturer that the engine is certified to meet the emission standards must be on file.

- The owner or operator must keep each record readily accessible in hard copy or electronic form for at least 5 years after the date of each occurrence, measurement, maintenance, corrective action, report, or record.

[40 CFR 63.6660 and 40 CFR 63.10(b)(1)]

General Provisions

- NSPS 40 CFR 60, Subpart A:  The engine shall comply with the requirements of 40 CFR 60, Subpart A, General Provisions, listed below, which have been adopted by reference in Rule 62-204.800(8)(d), F.A.C.; except that the Secretary is not the Administrator for purposes of 40 CFR 60.4, 40 CFR 60.8(b)(2) and (3), 40 CFR 60.11(e)(7) and (8), 40 CFR 60.13(g), (i) and (j)(2), and 40 CFR 60.16.  See Appendix 40 CFR 60 Subpart A included with this permit.

| General Provisions Citation | Subject of Citation |
| --- | --- |
| §60.1 | General applicability of the General Provisions |
| §60.2 | Definitions (additional terms defined in §60.4219) |
| §60.3 | Units and abbreviations |
| §60.4 | Address |
| §60.5 | Determination of construction or modification |
| §60.6 | Review of plans |
| §60.7 | Notification and Recordkeeping (only as specified in Condition 13.) |
| §60.8 | Performance tests (only if engine is not certified) |
| §60.9 | Availability of information |
| §60.10 | State Authority |
| §60.12 | Circumvention |
| §60.14 | Modification |
| §60.15 | Reconstruction |
| §60.16 | Priority list |
| §60.17 | Incorporations by reference |
| §60.19 | General notification and reporting requirements |

[Rule 62-204.800(8)(d), F.A.C.]