PERMITTEE

Harvest Power, Inc.

221 Crescent Street, Suite 402

Waltham, Massachusetts  02453

PERMITTING AUTHORITY

Florida Department of Environmental Protection (Department)

Division of Air Resource Management

Office of Permitting and Compliance (OPC)

2600 Blair Stone Road, MS #5505

Tallahassee, Florida 32399-2400

PROJECT

DEP File No. 0951340-001-AC (PSD-FL-418)

Biogas-to-Energy and Fertilizer Project

Orange County

Harvest Energy Orlando, LLC proposes to construct and operate a biogas-to-energy and fertilizer plant.  The facility will receive food waste, thickened wastewater activated sludge, and other organic materials.  The materials will be digested and converted to biogas and fertilizer.  The project will be constructed on land leased from Reedy Creek Improvement District (RCID) and collocated with the existing RCID’s wastewater treatment plant.  The RCID and Walt Disney World currently operate under a single Title V air permit as a single facility.  Construction is scheduled to commence in 2012 and be completed in 2013.

The proposed new plant will consist of five main sections:  a feedstock receiving and pre-treatment process; an anaerobic digestion process; a biogas, power generation, and heat recovery process; an odor removal process; and a digestate management/fertilizer production process.  Biogas produced by the digesters will be directed to a biogas scrubber to remove hydrogen sulfide and pass through a condensate trap/gravel filter to remove water before being fired in the two 1.6 MW reciprocating internal combustion engine/electrical generator sets.  If the engines are unavailable or more gas is produced than the engines can accommodate, a backup flare will combust the excess biogas before it is scrubbed.  Emissions of organic compounds and odor-causing pollutants from the receiving building, three holding tanks, and the digestate handling and drying system will be minimized by the installation of a bio-scrubber designed for at least 90% removal of organic compounds.

Organic waste entering the facility will undergo a pre-treatment process to remove contaminants, such as glass, metals, plastic, etc.  All inorganic material will be shipped off site to a landfill.  The organic waste will be turned into a slurry and then sent to two continuously stirred tank reactor digesters, which break down the organics in the slurry to convert it to primarily methane and carbon dioxide.  Exhaust from the engine/generator sets will be used to heat oil for an indirectly heated dryer.  The engine/generator sets will also be equipped with water jackets to heat water for use in other processes at the facility.  The remaining solids will be sent through a centrifuge to remove water and then to the indirectly heated dryer to further reduce the water content to produce a final fertilizer product.

This project is considered an expansion of this existing facility and is subject to PSD preconstruction review in accordance with Rule 62-212.400, F.A.C.  Determinations of Best Available Control Technology (BACT) were required for volatile organic compounds (VOC) and carbon monoxide (CO).

NOTICES AND PUBLICATION

Harvest Energy Orlando, LLC submitted an air construction permit application on March 22, 2012.  On May 31, 2012, the Permitting Authority gave notice of its intent to issue an air permit to the applicant for the described project.  The applicant published the Public Notice of Intent to Issue Air Permit for this project on June 3, 2012 in the Orlando Sentinel.

The complete project file including the application, Draft Permit, Technical Evaluation and Preliminary Determination (TEPD, including draft BACT determinations), key correspondence and comments regarding the draft permit are available at the following web link:

www.dep.state.fl.us/air/emission/bioenergy/harvest_energy.htm

COMMENTS on the draft permit

No comments were received from the public or the EPA on the draft permit during the 30-day comment period that ended on July 1, 2012.  On June 21, 2012, Harvest Power, Inc. provided comments by electronic mail.  These comments are available at the link given above under the heading of “Comments.”  Each comment from Harvest Power listed by page number and heading is described below along with the Departments response:

- Draft Permit, Page 3 of 11, Proposed Project:  The description of the proposed project states that the project is considered to be an expansion of the Reedy Creek Improvement District (RCID) facility.  HP disagrees with this conclusion, as HP will have complete control of the physical location, with RCID having no authority to make decisions regarding operation, emissions controls, or any other business operations at the Harvest Energy Garden – Orlando facility.  However, in the interest of time, in order to begin construction and for HP to meet its contractual obligations, HP will concede the point at this time.  HP does appreciate FDEP’s statement that HP will be issued separate PSD and Title V permits from RCID.

Department Response:  The Department acknowledges the comment, but stands by its original position summarized in Subsection 3.2 of the Technical Evaluation and Preliminary Determination.

- Draft Permit, Page 7 of 11, Authorized Fuel:  The draft permit states that only biogas is authorized to be fired in the engine/generator sets; however, biogas will not be immediately available to fuel the engines.  Prior to biosolids being introduced to the anaerobic digestion process, the system will need to be tested for leaks, gas storage, and gas handling, as well as connection to both the engines and the flare.  This testing will require using alternative fuels such as propane, natural gas, or landfill gas/biogas from another facility.  HP requests that FDEP add propane, natural gas, and biogas/landfill gas from another facility as authorized fuels during the initial startup testing period.  The suggested permit language is given below:

- Propane, natural gas, or biogas/landfill gas from another facility may be combusted in the engine/generator sets during the initial startup testing prior to full commissioning of the facility.  Once biosolids have been added to the anaerobic digestion system, and biogas is being generated, only biogas shall be fired in the engine/generator sets.  [Design, Application No. 0951340-001-AC, and Rule 62-210.200(PTE), F.A.C.]

Department Response:  The Department agrees that flexibility must be provided during the shakedown and initial commissioning of the facility.  The permit language of Specific Condition 3.A.5, Authorized Fuel will be changed to reflect that propane and natural gas can be combusted in the engine/generator sets for initial startup and testing purposes prior to the full commissioning of the facility.

- Draft Permit, Page 7 of 11, Emission Standards:  The emission standards given in specific conditions Nos. 10, 11, and 12 give the carbon monoxide (CO), volatile organic compound (VOC), and nitrogen oxides (NOX) emission limits in grams per brake horsepower per hour (g/bhp-hr), with equivalent pound per hour (lb/hr) values.  It is understood that these emission rates are based on the New Source Performance Standards (NSPS); however, brake horsepower is a design criteria, and not a measureable factor during operation of the engines.  HP suggests that the emission standards either be given in lb/hr quantities (with the brake horsepower limits given as equivalent rates), or that a conversion of electrical power output in kilowatts (kW) to mechanical power (bhp) be given in order to be able to compare the actual emissions and actual power output to the published emission standards.  The documentation provided by the engine manufacturer gives a conversion factor of approximately 1.4 brake horsepower per kilowatt (bhp/kW).  The suggested permit language is given below:

- CO Standard:  The emissions of CO from each engine/generator set shall not exceed 24.7 lb/hour and 7.0 g/kW-hr (equivalent to 5.0 g/bhp-hour).  [NSPS Subpart JJJJ in 40 CFR 60 and Rule 62-212.400(BACT), F.A.C.]

- VOC Standard:  The emissions of VOC from each engine/generator set shall not exceed 4.9 lb/hr and 1.4 g/kW-hr (equivalent to 1.0 g/bhp-hour).  When calculating emissions of VOC, emissions of formaldehyde should not be included.  [NSPS Subpart JJJJ in 40 CFR 60 and Rule 62-212.400(BACT), F.A.C.]

- NOX Standard:  The emissions of NOX from each engine/generator set shall not exceed 9.9 lb/hr and 2.8 g/kW-hr (equivalent to 2.0 g/bhp-hour).  [NSPS Subpart JJJJ in 40 CFR 60.]

Department Response:  The Department agrees that the power output of the engine/generator sets in kilowatts (kW) is a more readily measured value than the break horsepower (bhp).  Reviewing the documentation provided by Caterpillar for the G3520 generator set that will be used for this project, the electrical efficiency of the generator ranged from 92.7% at 25% load to 96.2% at 100% load.  This corresponds to conversion factors (bhp/kW) ranging from 1.44 to 1.39.  Since the generator sets will be operating the vast majority of the time at high load conditions and stack testing for compliance purposes must take place at the permitted capacity, a conversion factor of 1.4 is appropriate.  Additionally, since the pounds per hour rates for CO, VOC and NOX are unchanged; the Department agrees to convert the g/bhp-hr emission rates to their equivalent in g/kW-hr.  Specific Conditions 3.A.10, 3.A.11 and 3.A.12 pertaining to the CO, VOC and NOX emission rates, respectively, will be changed accordingly.  To show compliance with NSPS 40 CFR 60, Subpart JJJJ, compliance test results for the generators sets must be report in both g/kW-hr and g/bhp-hr.  The conversion from g/kW-hr to g/bhp-hr must be based on the appropriate electrical efficiency at the engine load at which the compliance tests were conducted.  The language of Specific Condition 3.A.23, Test Reports will be changed to reflect this new reporting requirement.

- Draft Permit, Page 8 of 11, Initial Compliance Tests:  The draft permit states that each engine/generator set shall be tested to demonstrate initial compliance with the emission standards for CO, NOX, and VOC within 60 days after achieving permitted capacity, but no later than 180 days after initial startup of each unit.  The Harvest Energy Garden – Orlando facility will achieve its permitted biogas generation and emissions capacity when feedstock and biogas production quantities reach build-out conditions at the facility at a future time.  Therefore, HP proposes that the initial compliance test be performed within 180 days after facility commissioning starts when biosolids have been added to the anaerobic digestions system and biogas generation has begun.  The suggested permit language is given below for the engine units, which can also be used for the Testing Requirements for the flare:

- Initial Compliance Tests: Each engine/generator set shall be tested to demonstrate initial compliance with the emissions standards for CO, NOX, and VOC pursuant to the NSPS Subpart JJJJ provisions in 40 CFR 60.  The initial compliance test must be conducted within 60 days after achieving permitted capacity, but no later than 180 days after the start of facility commissioning when biosolids have been added to the anaerobic digestion system and biogas is being generated.  [NSPS Subpart JJJJ in 40 CFR 60 and Rules 62-204.800, 62-297.310(7), and 62-212.400(BACT), F.A.C. (for CO/VOC emissions).]

Department Response:  The Department agrees that flexibility must be provided during the shakedown and initial commissioning of the facility.  The permit language of Specific Condition 3.A.16, Initial Compliance Tests will be changed to reflect that the 180 days time limit starts upon the addition of biosolids to the anaerobic digester.

- Draft Permit, Page 9 of 11, Monthly Records:  The draft permit states the average power produced (bhp) of each engine must be recorded monthly.  As stated previously, bhp is not a measurable quantity from the engines, and must be calculated based on the electrical power output (in kW).  If electrical power output is recorded and used with the suggested changes to the emissions standards described above, the intent of the requirement (to have a record of the monthly and 12-month rolling NOX and SO2 emissions) will still be maintained.  The suggested permit language is given below:

- Monthly Records: Within ten calendar days following each month, the permittee shall observe and record the total monthly number of hours of operation of each engine, the average electrical power produced (kW) of each engine, and the calculated monthly and 12-month rolling total emissions of NOX and SO2 to demonstrate compliance with the emissions caps.  [Rules 62-4.070(3), F.A.C.]

Department Response:  The Department agrees that the language of this condition should be changed to come into agreement with the changes in Specific Conditions 3.A.10, 3.A.11 and 3.A.12 where CO, VOC and NOX emission rates were changed from a g/bhp-hr basis to a g/kW-hr basis. The permit language of Specific Condition 3.A.22, Monthly Records will be changed to reflect that emission rates are on a g/kW-hr basis for the purpose of compliance with the NOX and SO2 emission caps.

- Draft Permit, Page 10 of 11, Authorized Fuel:  The draft permit states that only biogas is authorized to be fired in the flare; however, biogas will not be immediately available for the flare to burn.  As stated previously, prior to biosolids being introduced to the anaerobic digestion process, the system will need to be tested for leaks, gas storage, and gas handling, as well as connection to both the engines and the flare.  Therefore, HP suggests that other fuels be added as an authorized fuel during the initial startup testing period.  The suggested permit language is given below:

- Authorized Fuel: Propane, natural gas, or biogas/landfill gas from another facility may be combusted in the flare during the initial startup testing prior to full commissioning of the facility.  After the start of the facility commissioning when biosolids have been added to the anaerobic digestion system, and biogas is being generated, only biogas shall be fired in the flare.  [Application No. 0951340-001-AC, and Rule 62-210.200(PTE), F.A.C.]

Department Response:  The Department agrees that flexibility must be provided during the shakedown and initial commissioning of the facility.  The permit language of Specific Condition 3.B.3, Authorized Fuel will be changed to reflect that propane and natural gas can be combusted in the flare for initial startup and testing purposes prior to the full commissioning of the facility.

- Draft Permit, Page 11 of 11, Initial Compliance Tests:  The draft permit states that the flare shall be tested to demonstrate initial compliance with the visible emissions standards within 60 days after achieving permitted capacity, but no later than 180 days after initial startup of the unit.  As stated above, it is unknown at this time when the facility will achieve its permitted capacity.  The suggested permit language is given below:

- Initial Compliance Tests: The emission unit shall be tested to demonstrate initial compliance for visible emissions.  The initial compliance test must be conducted within 60 days after achieving permitted capacity, but no later than 180 days after the start of facility commissioning when biosolids have been added to the anaerobic digestion system and biogas is being generated.  [Rules 62-4.070(3) and 62-297.310(7), F.A.C.]

Department Response:  The Department agrees that flexibility must be provided during the shakedown and initial commissioning of the facility.  The permit language of Specific Condition 3.B.8, Initial Compliance Tests will be changed to reflect that the 180 days time limit starts upon the addition of biosolids to the anaerobic digester.

Finally, to reflect the change of CO, VOC and NOX emission rate limits from a g/bhp-hr basis to a g/kW-hr basis, the NOX emission cap equation given in Specific Conditions 3.A.13 and 3.B.6 of the permit must be changed.  The units of the variables in the equation will be changed to a kW-hr and g/kW-hr basis for consistency.

Harvest Energy Orlando, LLC comments affected wording in Subsections 3.A and 3.B of the draft permit.

Finalization of the BACT determinations

The Department hereby finalizes the BACT determinations as drafted in the TEPD for VOC and CO with the basis of the limits changed from g-bhp-hr to g/kW-hr.

www.dep.state.fl.us/air/emission/bioenergy/harvest_energy/Technical%20Evaluation%20and%20Preliminary%20Determination.pdf

The BACT emission limits, practices and technologies for each emission unit are incorporated within the conditions of the Final Permit.

CONCLUSION

The final action of the Department is to issue the final permit with the corrections described above.