### TECHNICAL EVALUATION

&

PRELIMINARY DETERMINATION

#### APPLICANT

Solid Waste Authority of Palm Beach County

7501 North Jog Road

West Palm Beach, Florida 33412

Palm Beach Renewable Energy Park

Facility ID No. 0990234

#### PROJECT

# Project No. 0990234-032-AC

Application for Minor Source Air Construction Permit

Palm Beach Renewable Energy Facility No. 2, Revision to Authorized Wastes

#### COUNTY

Palm Beach County, Florida

PERMITTING AUTHORITY

Florida Department of Environmental Protection

Division of Air Resource Management

Office of Permitting and Compliance

2600 Blair Stone Road, MS#5505

Tallahassee, Florida  32399-2400

November 13, 2014

- General Project INFORMATION

  - Air Pollution Regulations

Projects at stationary sources with the potential to emit air pollution are subject to the applicable environmental laws specified in Section 403 of the Florida Statutes (F.S.).  The statutes authorize the Department of Environmental Protection (Department) to establish regulations regarding air quality as part of the Florida Administrative Code (F.A.C.), which includes the following applicable chapters:  62-4 (Permits); 62-204 (Air Pollution Control – General Provisions); 62-210 (Stationary Sources – General Requirements); 62-212 (Stationary Sources – Preconstruction Review); 62-213 (Operation Permits for Major Sources of Air Pollution); 62-296 (Stationary Sources - Emission Standards); and 62-297 (Stationary Sources – Emissions Monitoring).  Specifically, air construction permits are required pursuant to Chapters 62-4, 62-210 and 62-212, F.A.C.

In addition, the U. S. Environmental Protection Agency (EPA) establishes air quality regulations in Title 40 of the Code of Federal Regulations (CFR).  Part 60 specifies New Source Performance Standards (NSPS) for numerous industrial categories.  Part 61 specifies National Emission Standards for Hazardous Air Pollutants (NESHAP) based on specific pollutants.  Part 63 specifies NESHAP based on the Maximum Achievable Control Technology (MACT) for numerous industrial categories.  The Department adopts these federal regulations in Rule 62-204.800, F.A.C.

  - Glossary of Common Terms

Because of the technical nature of the project, the permit contains numerous acronyms and abbreviations, which are defined in Appendix A of this permit.

  - Facility Description and Location

The existing Palm Beach Renewable Energy Park (PBREP) contains a municipal solid waste (MSW) facility categorized under Standard Industrial Classification Number (No.) 4953.  The existing facility, known as Palm Beach Renewable Energy Facility No. 1. (PBREF-1) is located in Palm Beach County (see Figure 1) at 7501 North Jog Road in West Palm Beach, Florida (see Figure 2).  The Palm Beach Renewable Energy Facility No. 2 (PBREF-2) includes three new municipal waste combustors at the PBREP site.  The UTM coordinates are Zone 17, 585.3 kilometers (km) East, and 2961.7 km North.  A satellite view of the facility where the under construction PBREF-2 is clearly visible is shown in

Palm Beach
County

Figure 1.  Location of Palm Beach County.	Figure 2.  Location of PBREP in Palm Beach County.

PBREF-2

PBREF-1

Figure 3. Satellite View of the PBREP.

This site is in an area that is in attainment (or designated as unclassifiable) for all air pollutants subject to Ambient Air Quality Standards (AAQS).

  - Facility Regulatory Categories

- The existing PBREF-1 and the new PBREF-2 are major sources of HAP.

- The existing PBREF-1 and the new PBREF-2 are not subject to the acid rain provisions of the Clean Air Act (CAA).

- The existing PBREF-1 and the new PBREF-2 is a Title V major source of air pollution in accordance with Chapter 62-213, F.A.C.

- The existing PBREF-1 is a major stationary source in accordance with Rule 62-212.400 (PSD), F.A.C.

- The new PBREF-2 is a modification of a major stationary source in accordance with Rule 62-212.400 (PSD), F.A.C.

- The new PBREF-2 is subject to New Source Performance Standards (NSPS) under Section 111 of the CAA and National Emissions Standards for Hazardous Air Pollutants (NESHAP) under Section 112 of the CAA which are incorporated by reference in Chapter 62-204.800, F.A.C.

  - Project Description

The Solid Waste Authority (SWA) of Palm Beach County applied on July 11, 2014, to the Department for a minor source air construction (AC) permit.  The applicant then modified the application with a revised submission on July 25, 2014. The minor source AC permit is for revisions to the previously issued AC/Prevention of Significant Deterioration (PSD) permits, Permit Nos. 0990234-017-AC/PSD-FL-413, 0990234-023-AC/PSD-FL-413A (Project), and 0990234-028-AC/PSD-FL-413B.

In the July 11, 2014, application, the applicant requested that the air construction permit be modified to authorize additional wastes for combustion at the facility, including materials for witnessed destruction (such as expired or off-specification consumer goods and pharmaceuticals), biosolids, livestock waste, waste processing residue from ethanol production, waste gasification process residue, combustible residue from recycling of construction and demolition debris, residue from processing MSW to make refuse-derived fuel, residue from processing recovered materials, and residue from processing recyclable materials.  The applicant also requested that the limit on the proportion of non-MSW in segregated loads to be combusted at the facility be raised from 5% to 20% by weight.  In the July 25, 2014, addendum to the application, the applicant requested small changes to emissions testing procedures and requirements and clarification regarding emissions testing requirements.

  - Processing Schedule

- 7/11/2014	Received the application for a minor source air pollution construction permit.

- 7/25/2014	Received additional information; application complete.

- 11/13/2014	Issued draft permit package.

- PSD Applicability

  - General PSD Applicability

The Department regulates major stationary sources in accordance with Florida’s PSD program pursuant to Rule 62-212.400, F.A.C.  PSD preconstruction review is required in areas that are currently in attainment with the state and federal ambient air quality standards (AAQS) or areas designated as “unclassifiable” for these regulated pollutants.  The project is located in Palm Beach County, which is in an area that is currently in attainment with the state and federal AAQS or otherwise designated as unclassifiable.

The key requirement of a PSD review include:  employment of Best Available Control Technology; a demonstration that the project will not cause or contribute to a violation of a state of federal AAQS or increment; and a demonstration that the project will not cause adverse impacts to Air Quality Related Values (AQRVs) such as visibility, soils and vegetation.

Commonly addressed PSD pollutants include:  carbon monoxide (CO), nitrogen oxides (NOX), particulate matter (PM), PM with a mean diameter of 10 micron or less (PM10), PM with a mean diameter of 2.5 microns or less (PM2.5), sulfur dioxide (SO2), volatile organic compounds (VOC), sulfuric acid mist (SAM), lead (Pb), fluorides (F), and mercury (Hg).  Additional PSD pollutants that are more common to certain other industries include: hydrogen sulfide (H2S), TRS including H2S, reduced sulfur compounds (RSC) including H2S, municipal waste combustor (MWC) organics measured as total tetra- through octa-chlorinated dibenzo-p-dioxins and dibenzofurans (dioxin/furan), MWC metals measured as PM; MWC acid gases measured as SO2 and hydrogen chloride (HCl), and municipal solid waste (MSW) landfill emissions as non-methane organic compounds (NMOC).

Greenhouse gases (GHGs) is defined at section 40 CFR 86.1818-12(a) as the aggregate group of gases including CO2, nitrous oxide (N2O), methane CH4, hydrofluorocarbons (HFCs), perfluorocarbons (PFCs), and sulfur hexafluoride (SF6).  GHGs is expressed as CO2-equivalent (CO2e).

  - Definition of a Major Stationary Source

As defined in Rule 62-210.200(Definitions), F.A.C., a stationary source is a “major stationary source” (major PSD source) if it emits or has the potential to emit (PTE):

- 250 tons per year (tons/year) or more of any PSD pollutant; or

- 100 tons/year or more of any PSD pollutant and the facility belongs to one of the 28 listed PSD major facility categories;

- For the special case of greenhouse gases (GHGs), the facility must first be shown to emit or have a PTE of 100,000 tons/year of GHGs as carbon dioxide equivalent (CO2e) to possibly be subject to regulation.

The listed PSD major facility categories includes “municipal incinerators capable of charging more than 250 tons of refuse per day”.  The given category applies to the PBREF-2.  PBREF-2 is a major stationary source based on actual emissions of and potential to emit 100 tons/year or more of several individual PSD pollutants.

If emissions of GHGs expressed as CO2e emissions are greater than 100,000 tons/year, then the total (unweighted) GHGs mass emissions are compared with the 100 and 250 tons/year thresholds to determine whether the source is a major stationary source.

Once a new facility is considered a major stationary source based on one PSD pollutant, then other PSD pollutants are reviewed for PSD applicability based on the respective Significant Emission Rate (SER) defined and specified in Rule 62-210.200, F.A.C.  Each pollutant projected to be emitted at a rate equal to or greater than its respective SER is also considered to be “significant” and subject to PSD preconstruction review, including a BACT determination.

Refer to Table 1.  Although a new stationary source may be “major” for a single PSD pollutant, the project must include BACT controls for any PSD pollutant that exceeds the corresponding significant emission rates (SERs) listed in the table below.

Table 1 - List of Significant Emission Rates by PSD-Pollutant. 1

| Pollutant | SER (tons/year) | Pollutant | SER (tons/year) 4 |
| --- | --- | --- | --- |
| CO | 100 | NOX | 40 |
| PM/PM10/PM2.5 | 25/15/10 | Ozone (VOC) 2 | 40 |
| PM2.5 (NOX) | 40 | PM2.5 (SO2) | 40 |
| Ozone (NOX) 2 | 40 | SAM | 7 |
| SO2 | 40 | Pb | 0.6 |
| Hg | 0.1 | Fluoride (F) | 3 |
| MWC metals as PM | 15 | MWC acid gases as SO2 & HCl | 40 |
| MWC organics as dioxin/furan | 3.5 x 10-6 | GHGs (total mass basis) | 0 3 |
| - Excluding pollutants specific to the Pulp and Paper industry and MSW landfills. - Ozone (O3) is regulated by its precursors (VOC and NOX). PSD for PM2.5 can be triggered by its precursors (NOX and SO2). - Pursuant to 40 CFR 52.21(b)(23)(ii), pollutants with no SER listed at 40 CFR 52.21(b)(23)(i) have a SER of zero tons/year. - SER also means any emissions rate or any net emissions increase associated with a major stationary source or major modification which would construct within 10 km of a Class I area and have an impact on such area equal to or greater than 1 μg/m3, 24-hour average. |  |  |  |

  - Definition of Major Modification

“Major modifications” at major stationary sources are also subject to PSD review.  According to Rule 
62-210.200(Definitions), F.A.C., Major Modification (of a Major Stationary Source) is defined as follows:

- Any physical change in or change in the method of operation of a major stationary source that would result in a significant emissions increase of a PSD pollutant and a significant net emissions increase of that pollutant from the major stationary source.  (Refer to Table 1 above)

- Any significant emissions increase from any emissions units or net emissions increase at a major stationary source that is significant for volatile organic compounds or nitrogen oxides shall be considered significant for ozone.  (Refer to Table 1 above)

- through (d).  These paragraphs are not relevant to this review

For a major modification of an existing major stationary source, the review must include a BACT determination for any PSD pollutant that exceeds the respective SER.  The review must include demonstrations that the project will not cause or contribute to a violation of an AAQS or increment and that the project will not adversely affect AQRVs.

GHGs becomes subject to regulation at a major modification if project emissions as CO2e are greater than 75,000 tons/year and mass GHGs exceed zero tons/year.  The effects of the Supreme Court opinion about this provision on the Department’s rules are also under review.

  - Previous PSD Review and Construction Status

The original project to construct the three MWCs was subject to the requirements of 40 Code of Federal Regulations (CFR) Part 60, Subpart Eb - Standards of Performance for Large MWC, issued in May 2006.  These requirements include emissions limits for typical air pollutants as well as the Maximum Achievable Control Technology (MACT) for hazardous air pollutants (HAP).

The original project also triggered PSD and required a determination of BACT for the following pollutants: NOX, CO, SO2, VOC, PM, PM10, MWC metals as PM, MWC acid gases as SO2 and HCl, F, SAM and MWC organics as D/F.

The BACT control equipment for multi-pollutant control for the project consists of good combustion practices (GCP), spray dryers (SD), fabric filter (FF) baghouses, activated carbon injection (CI) and selective catalytic reduction (SCR).  The control equipment minimizes emissions of Hg and a BACT determination was not required for this pollutant.

All of the BACT emission limits for the project are at least as stringent as the requirements of Subpart Eb.  In particular, the emission limitation for NOX is much more stringent at 50 parts per million by volume, dry at 
7 percent (%) oxygen (O2), i.e., ppmvd @ 7% O2, compared with the Subpart Eb limit of 150 ppmvd @ 7% O2. The BACT technology to achieve the NOX limit is specified as SCR rather than selective non-catalytic reduction (SNCR).  SCR will also reduce emissions of ammonia (NH3) and VOC, which (like NOX and SO2) are precursors in the formation of fine PM in the exhaust and the environment.

Further details regarding the original permit and previous minor revisions are available at the following web page:  http://www.dep.state.fl.us/Air/emission/bioenergy/palm_beach.htm  Additional facts are available at the facility web site at:  http://www.swa.org/pdf/PBRWF_2_-_12.10.12.pdf  Construction has not yet been completed.  The following link is to a camera showing the status of construction:  http://www.swa.org/vm95webcam/  Figure 4 below was downloaded from the webcam on August 28, 2014.  The PBREF No. 2 will begin commercial operation in 2015.

Figure 4.  Ongoing Construction of PBREF No. 2 as of August 28, 2014.

  - PSD Applicability for New Project

With respect to the application under review, the method to determine whether the present project is a major source modification is to compare “baseline actual emissions (BAE)” with “projected actual emissions (PAE)” and compare the differences with the SER listed in Table 1.

According to paragraph 62-210.200(194), F.A.C., for the purposes of Rule 62-212.400 (PSD), F.A.C., a new emissions unit is any emission unit that is or will be newly constructed and that has existed for less than 2 years from the date such emissions unit first operated.  The three new MWCs at the PBREP are clearly new emissions units.

According to paragraph 62-210.200(28)(c), F.A.C., for a new emissions unit, the BAE for purposes of determining the emissions increase that will result from the initial construction and operation of such unit shall equal zero; and thereafter, for all other purposes, shall equal the unit's potential to emit (PTE).

No changes in emissions limits are requested.  Both the BAE and the PAE of the three new MWC units will equal their respective PTEs.  Therefore the difference in the two quantities is zero, and the project is not a modification with respect to the PSD rules.

If, for example, there had been any increase in the emission limits of any pollutant, it would be necessary to consider whether the total increase from the original project and the present modification would trigger PSD.

- Department review

  - Brief Discussion of Emissions

No changes in permitted emissions are requested in this application.  The emissions and emissions units that comprise PBREF-2 have been detailed in previous AC/PSD Permit Nos. 0990234-017-AC/PSD-FL-413, 0990234-023-AC/PSD-FL-413A (Project), and 0990234-028-AC/PSD-FL-413B.  The PBREF-2 emissions totals and PSD applicability are unchanged from Permit No. 0990234-028-AC/PSD-FL-413B.

    - Changes in waste mix permitted to be burned in MWCs (Permit Condition 12)

Applicant request:  SWA has requested that the percentage by weight consisting of waste tires permitted to be burned at the facility be raised from 3% to 5%.  The applicant has also requested that permitted wastes include materials for witnessed destruction (such as expired or off-specification consumer goods and pharmaceuticals), biosolids, livestock waste, waste processing residue from ethanol production, waste gasification process residue, combustible residue from recycling of construction and demolition debris, residue from processing MSW to make refuse-derived fuel, residue from processing recovered materials, and residue from processing recyclable materials.  Additionally, the applicant has requested that the limit on the proportion of non-MSW in segregated loads to be combusted at the facility be raised from 5% to 20% by weight, with a 5% limit on most individual categories of such wastes.

Department response:  This request is consistent with Section 403.707(1), Florida Statutes, which states that “… [DEP] shall allow waste-to-energy facilities to maximize acceptance and processing of nonhazardous solid and liquid waste.”  The state-of-the-art pollution control equipment that is being installed at PBREF-2, including spray dryers, activated carbon injection, fabric filter baghouses, and selective catalytic reduction, will prevent this requested change in permissible wastes from appreciably affecting emissions.  Additionally, initial compliance testing and either continuous monitoring or annual stack tests will be performed to measure emissions and demonstrate compliance with emissions standards for NOx, VOC, CO, SO2, HCl, PM, Pb, Cd, Hg, and dioxins/furans as well as visible emissions and ammonia slip.  Also, Permit Condition 13 requires that any non-MSW materials received in a segregated load be well mixed with MSW in the refuse pit, or be alternately charged with MSW in the hopper. If unexpected emissions do occur, these regular measurements would show them.

Biosolids are becoming an important component of the waste burned in municipal waste combustors across Florida.  Several of the largest waste combustors across the state are authorized to burn biosolids: waste combusted at the Hillsborough and Lee County facilities may consist of up to 5% biosolids by weight, while waste at the South Broward and North Broward facilities may consist of up to 15% biosolids (pending the results of initial testing).  The 5% biosolids limit at PBREF-2 is in line with the limits at these other facilities.  As was noted in the Technical Evaluation and Preliminary Determination for biosolids at the North Broward facility (Permit No. 0112120-017-AC), dried biosolids can have a heat content of up to 10,300 BTU/lb, and the very high temperatures at which waste is combusted destroy essentially all pathogens in the waste.  A 5% limit on tires is also in place at the Lee County municipal waste combustor; most other MWCs in the state are permitted to burn waste tires as up to 3% of their waste mix.

Some of these materials are rather novel for Florida municipal waste combustors.  Waste processing residue from ethanol production (5% limit), waste gasification process residue (5% limit), and livestock waste (including straw, wood shavings, hay, feed, and excreta) (10% limit) are not commonly used in MWCs.  However, these materials are quite similar to the carbonaceous fuels such as biomass and plastics that are commonly burned in electrical generating units and municipal waste combustors.  High combustion temperatures would also destroy any potential pathogens in livestock waste materials.  The residues generated when recycling construction and demolition debris, when processing MSW to make refuse-derived fuel, when processing recovered materials, and when processing recyclables are also novel MWC fuels.  However, these materials would not be expected to differ substantially in composition from traditional MSW.

This change in permitted wastes has been incorporated into the air construction permit.

    - Clarification on the use of continuous emissions monitors to demonstrate compliance 
(Conditions 17 and 19)

Applicant request:  SWA has requested clarification that tests, including initial compliance demonstrations, for emissions of SO2, NOX, and CO may be performed by certified continuous emissions monitors (CEMS).

Department response:  The facility will include CEMS for these three pollutants.  These CEMS incorporate EPA-approved instrumental measurement methods for SO2 (Method 6C), NOX (Method 7E), and CO (Method 10).  The permit for the facility also includes requirements for quality assurance and quality control for the CEMS, as well as initial performance specification tests to certify this equipment.  The use of CEMS for these purposes is common and reasonable, and this clarification has been incorporated.

    - Modification to testing requirements for NOX and HCl (Condition 17)

Applicant request:  SWA has requested that the item regarding NOX testing in Condition 17 not require the NOX test to occur with the air heater operating “at the highest heat input possible” during the test.  This change was requested because operating the air heater at the highest heat input possible can adversely affect performance, according to SWA.  The applicant has also requested permission to modify the test method for HCl (Method 26) to use full-size impingers in lieu of midget impingers and to use one empty impinger in lieu of two sodium hydroxide impingers.

Department response:  Removing the requirement to perform the NOX measurement with the air heater operating at the highest heat input possible will result in a measurement that is more representative of regular operating operations.  Perhaps more importantly, because the facility will measure emissions of NOX and demonstrate compliance with NOX emissions limits continuously using a CEMS, emissions and compliance are verified under all operating conditions.  The modification to the HCl method will bring this requirement in line with the method already in use at the existing PBREF-1, in construction Permit No. 0990234-019-AC/PSD-FL-108I and in operating Permit No. 0990234-031-AV.  Additionally, on the Method 26 website, EPA writes that such changes to HCl test methods are reasonable ones that can be approved routinely.  These changes have been incorporated.

    - Modification to testing requirements for dioxins and furans (Conditions, 16, 19, 21 and 22)

Applicant request:  SWA has requested that the requirement for quarterly dioxin and furan (D/F) testing for each municipal waste combustor unit be reduced from two years to one year.

Department response:  Confidence in the ability of selective catalytic reduction (SCR) systems to greatly reduce D/F emissions continues to grow.  SCR manufacturers and catalyst manufacturers now market the D/F reduction capabilities of SCR.  One year of quarterly D/F testing will still result in at least 12 D/F tests (three units, four D/F tests per unit), which will provide considerable information on D/F emissions from PBREF-2.  Specific Conditions 16 and 22 of the permit set the D/F emissions limit as the lesser of either 10 ng/dscm, or the average of all quarterly D/F emissions tests multiplied by a factor of 10.  One year of tests will likely be sufficient to understand the performance of the SCR system for reducing D/F emissions and for quantifying D/F emissions from PBREF-2.  The option to terminate quarterly D/F testing after one year, upon approval by the Department pending the results of initial D/F testing, has been incorporated into the draft permit.  It has also been clarified that the initial 10 ng/dscm emissions limit applies until the completion of D/F testing, at which time the new limit resulting from the D/F testing will be issued by the Department, regardless of the status of the facility’s application for a Title V operating permit.  After the completion of quarterly D/F testing, annual D/F compliance tests are still required.

- Preliminary Determination

The Department makes a preliminary determination that the proposed project will comply with all applicable state and federal air pollution regulations as conditioned by the draft permit.  This determination is based on a technical review of the complete application, reasonable assurances provided by the applicant, and the conditions specified in the draft permit.  No air quality modeling analysis is required because the project does not result in a significant increase in emissions.  John Dawson is the project engineer responsible for reviewing the application and drafting the permit.  Additional details of this analysis may be obtained by contacting him by telephone at 850-717-9085, by e-mail at john.dawson@dep.state.fl.us, or at the Department’s Office of Permitting and Compliance at Mail Station #5505, 2600 Blair Stone Road, Tallahassee, Florida  32399-2400.

In making this calculation, the values listed in 40 CFR 98, Subpart A, Table A-1 are used to weight emissions by their respective Global Warming Potential (GWP).  For example, the current GWP factors for four of the GHGs are:  CO2 = 1; CH4 = 25; N2O = 298 and SF6 = 22,800.

This procedure was held to be invalid at the federal level due to a U.S. Supreme Court opinion dated June 23, 2014.  
Link to Supreme Court Opinion  The Department is reviewing the effects of the decision on its own rules.  EPA issued guidance regarding implementation of the decision on July 24, 2014.  Link to EPA Guidance