##### PERMITTEE

Florida Power Corporation

d/b/a Progress Energy Florida (PEF), Inc.

Direct Subsidiary of Duke Energy Corporation

1729 Baillies Bluff Road

Holiday, Florida 34691-9753

##### Permitting Authority

Florida Department of Environmental Protection (Department)

Division of Air Resource Management

Office of Permitting and Compliance

2600 Blair Stone Road, MS #5505

Tallahassee, Florida  32399-2400

##### PROJECT

Air Permit No. 1010017-013-AC (PSD-FL-419)

Anclote Power Plant Units 1 and 2

Natural Gas Conversion Project

This is the final air construction permit, which authorizes conversion of Units 1 and 2 and associated equipment from present use of heavy fuel oil and natural gas to exclusive use of natural gas and establishes permit limits for nitrogen oxides (NOX) and carbon monoxide (CO).  The proposed work will be conducted at the existing Anclote Power Plant, located in Pasco County at 1729 Baillies Bluff Road, Holiday, Florida.  The UTM coordinates are Zone 17, 324.4 km East and 3118.7 km North.

##### NOTICE AND PUBLICATION

The Department distributed a major stationary source modification air construction (PSD) draft permit package on July 30, 2012.  The applicant published the Public Notice in the Pasco Times on August 4, 2012.  The Department received the proof of publication on August 9, 2012.  No requests for administrative hearings or requests for extensions of time to file a petition for administrative hearing were received.

# COMMENTS

No comments on the draft permit were received from individual members of the public.  Comments were received from the applicant (PEF) on August 28, 2012 and from the EPA Region 4 Office on September 4, 2012.

- REVIEW OF COMMENTS FROM PROGRESS ENERGY FLORIDA

The comments from PEF were received within the 30-day comment period.  Link to PEF Comments .  The key comments contained in the PEF document are repeated or paraphrased (in italics) below and followed by the Department’s response.

- Permit Facility Description:  The date in which natural gas firing capability was installed is incorrect.  The year noted (1998) was the year in which the final permit authorizing the installation of the natural gas burners was issued ….”  PEF requests the following change in the Facility Description Section (shown in strike-out and double underlined format):

Units 1 and 2 are residual fuel oil and natural gas-fired steam electric generating units.  Each boiler provides steam to a steam turbine-electric generator with a gross nameplate rating of 556.2 megawatts (MW).  Units 1 and 2 began commercial operation in 1974 and 1978, respectively as residual fuel oil units.  Limited natural gas firing capability of 2,300 million Btu per hour (MMBtu/hour) was installed on each in 1998.  An Air Construction permit for installation of limited natural gas firing capability of 2,300 million Btu per hour (MMBtu/hour) was issued in October 1998.

Department Response:  The Department will make the requested change.

- Section 3.A., Specific Condition 1:  Same comment as above.  PEF requests correction of the date given in the condition from 1999 to 1998.

Department Response:  The Department will make the requested change.

- Section 3.A., Specific Condition 2:  PEF would like to specifically call out the known work items presently consolidated as Specific Condition 2.f. “Other modifications to maintain the gross generating capacity or improve the net generating capacity of the units”.  Revise Specific Condition 2 as follows:

Natural Gas Conversion ProjectUU:  For Units 1 and 2, the permittee is authorized to perform the following work to convert Units 1 and 2 and associated equipment from present use of heavy fuel oil and natural gas to exclusive use of natural gas.

  - Three additional levels of natural gas burners per furnace;

  - Superheater surface area reductions;

  - Disabling of residual fuel oil firing capability;

  - Upgrade of superheater metallurgy;

  - Upgrade of the burner control and management system;

- Replacement/upgrade of the forced draft (FD) fan in each unit;

- Addition of two (2) fuel gas heaters;

- Modifications to the natural gas delivery systems;

- Replacement of the existing natural gas metering and regulating (M&R) station;

- f	Other modifications to maintain the gross generating capacity or improve the net generating capacity of the units.

- Section 3.A., Specific Condition 7.c. – Visible Emissions:  Because this conversion includes the retrofit of existing boilers with new burners and the inclusion of Close Coupled Overfire Air (CCOFA) for NOX control, the magnitude of opacity determined via Continuous Opacity Monitoring Systems (COMS) during specific periods of operation is unknown at this time. Therefore, in an effort to accommodate possible elevated opacity levels during these periods, PEF requests the following change:

c.	Visible Emissions:  As determined by COMS data or EPA Method 9, after December 31, 2013 and after June 30, 2014 visible emissions from Unit 1 and Unit 2, respectively, with the exception of Condition 7.c.1 and 7.c.(2) below, shall not exceed 15 percent (%) opacity based on a 6-minute block average, except for one 6-minute period per hour of not more than 20%.  For periods of startup, shutdown and malfunction, visible emissions shall not exceed 20% opacity except for one 6-minute period per hour of not more than 27% as determined by COMS data or EPA Method 9.

  - Excess Emissions - Startup and Shutdown. Excess emissions resulting from startup or shutdown shall be permitted provided that best operational practices to minimize emissions are adhered to and the duration of excess emissions shall be minimized.  [Rule 62-210.700(2), F.A.C.]

  - Excess Emissions - Malfunctions. Excess emissions resulting from malfunction shall be permitted providing (1) best operational practices to minimize emissions are adhered to and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration. [Rule 62-210.700(1), F.A.C.]

Department Response:  The visible emissions limits including those during startup, shutdown and malfunction constitute BACT and should be numerically limited during those events.  Natural gas firing should cause minimal emissions.  There could be some color to the plume due to allowable NOX emissions which is the reason that the limit was set at 15% during normal operations instead of 10%.  Following termination of residual fuel oil use, the natural gas exhaust will for a few months scour surfaces of solid materials and condensed sulfuric acid mist to cause some excess visible emissions likely less than the limits specified by the Department.  The Department will finalize the visible emission (opacity) limits as proposed.

Section 3.A., Specific Condition 13. – Compliance by COMS and CEMS:  Because COMS data is the manner in which the units demonstrate compliance with the opacity standard please clarify if annual visible emissions (VE) test via EPA Method 9 is required on an annual basis. In addition, the term “reestablishing commercial operation” is confusing and PEF request the following change in condition language:

Compliance by COMS and CEMS: Compliance with the standards for opacity and emissions of CO and NOX shall be demonstrated with data collected from the required continuous monitoring systems.  Within 90 days of reaching 90% of the design heat input of 5,500 MMBtu/hr/unit [while] firing the new gas burners in reestablishing commercial operation of each unit, but not later than 180 days after firing the new gas burners, the permittee shall certify proper operation of each required monitor.

Department Response:  The Department will make the requested change based on reaching 4,950 MMBtu/hr/unit, which equals 90% of 5,500 MMBtu/hour/unit.

- Section 3.C., Specific Condition 1. – NESHAP Subpart DDDDD Applicability:  After the conversion to natural gas, the facility will not be a major source of hazardous air pollutants (HAP).  NESHAP Subpart DDDDD does not apply and the condition should be deleted.

Department Response:  The Department consulted with EPA and received the following input that supports the applicant’s position.

- If the facility converts to exclusive use of natural gas before the first substantive compliance date (which April 16, 2015 for existing sources), then they would avoid applicability of the Mercury Air Toxics Standard (MATS – also known as NESHAP Subpart UUUUU).

- MATS regulates all coal and oil fired electric generating units with a capacity of 25 MW or greater - the rule does not distinguish between major and area sources.

- The area source boiler rule (NESHAP Subpart JJJJJJ) does not regulate natural gas boilers.  Per 63.7491(a), the major source boiler rule (5D) does not regulate “Electric Utility Steam Generating Units” as defined in 63.7575.

The Department will strike the condition and renumber the rest of the conditions in the mentioned section.

- Section 3.C., Specific Condition 3. – Natural Gas Fired Process Heaters BACT Emissions Limits:  The facility was required to only assess BACT for CO.  Therefore, please delete all pollutants other than CO in this specific condition.

Department Response:  The Department agrees and will remove references to BACT determinations for all pollutants other than CO.  The potential emissions of all pollutants from these small (16.5 MMBtu/hour) are minimal and do not affect PSD applicability

- Comments Regarding the Technical Evaluation and Preliminary Determination (TEPD):  The applicant suggested a number of corrections and clarifications regarding the TEPD document distributed with the Department’s draft PSD permit package.

Department Response:  The applicant’s comments regarding the TEPD document are available at the link provided above.  Some of the corrections and clarifications are the same as indicated above regarding the draft permit and have been resolved through the changes made in the final permit.  Others involve differences of opinions, including the rationale provided by the applicant when rejecting oxidation catalyst to achieve BACT for CO.  (Neither the Department nor the applicant believe oxidation catalyst is actually required).  The EPA also commented on this matter as discussed in detail further below.  The applicant’s comments are acknowledged in this Final Determination.  Issuance of a corrected or modified TEPD document is not required.

- REVIEW OF COMMENTS FROM EPA REGION 4

The Department received written comments from EPA Region 4 on September 4, 2012; 31 days after publication of the Public Notice.  Link to EPA Comments .  These written comments will nevertheless be considered because the public comment period ended on a recognized National holiday (Labor Day).

The key comments contained in the EPA Region 4 document are repeated or paraphrased (in italics) below and followed by the Department’s response.

- General EPA Comment:  “There are a few points of concern in the emissions calculations performed by both the applicant and the FDEP” (who recalculated the emissions based on a revised heat input capacity).

Department Response:  To clarify, these pre-NSPS units have never had enforceable heat input capacity limits.  In the Title V permit terms such capacity are indeed used, but conditions are included that explain the meaning of these terms in the relevant context.  Condition A.1 of the current Title V permit No. 1010017-012 includes the following permitting note:

“The heat input limitations have been placed in each permit to identify the capacity of each unit for the purposes of confirming that emissions testing is conducted within 90 to 100 percent of the unit’s rated capacity (or to limit future operation to 110 percent of the test load), to establish appropriate emission limits and to aid in determining future rule applicability.  Regular record keeping is not required for heat input.”

Each unit is equipped with steam turbine-electric generator (STG) that has a gross nameplate rating of 556.2 megawatts (MW).  The boilers are sufficiently robust and stout while firing residual fuel oil (as designed) to produce sufficient steam to achieve the full gross nameplate rating (some of which is consumed by the parasitic loads needed to operate the plant equipment, including fuel oil handling).  The emission estimates were based on greater heat input to achieve the same gross nameplate rating when using the alternative fuel (natural gas) which is less efficient within a furnace of a given size than the design fuel (residual fuel oil).  At this time, the amount of natural gas that can actually be burned after the project modifications is not known, except that it will likely be less than the value used to estimate emissions.

The purpose of the project, as understood by the Department, is to allow the units to operate during the remainder of their useful lives under the constraints of several federally mandated regulations including the Mercury and Air Toxics Standards (MATS), the Best Available Retrofit Technology (BART) Rules, and the alternative to the vacated Cross State Air Pollution Rule (CSAPR) – the Clean Air Interstate Rule (CAIR).  This explanation is to dispel the possible notion that the project is an expansion of capacity.

- Reference EPA Comment 1.a., 2-Step Applicability Procedure:  “Applicability for a modification involves a two-step process which includes evaluating the emissions increase (Step 1) and then the net emissions increase (Step 2) of the modification”.

Department Response:  The Department’s definition of “major source modification” is contained in 
Rule 62-210.200 Definitions, F.A.C.  It states:

(191) “Major Modification” – (a) Any physical change in or change in the method of operation of a major stationary source that would result in (1) a significant emissions increase of a PSD pollutant and (2) a significant net emissions increase of that pollutant from the major stationary source.  (The Department added the numbers 1 and 2 as well as the emphases)

The two steps described by EPA are imbedded in the Department’s definition of a major modification.  A demonstration that a significant emission increase does not occur is sufficient to determine that PSD does not apply without necessitating a second demonstration that a significant net emissions increase does not occur.

Unfortunately, the Department used the term “net emissions increase” in a few places in the discussion when the Department was conducting Step 1 to determine “emissions increases” (not net emissions increases), which equal the projected actual emissions minus the baseline actual emissions as shown in the diagram below.

Figure 1.  Step 1 of a Two-Step Determination of Major Modification

In determining PSD applicability, it was enough to show that there were not significant emissions increases thus obviating the need to go to Step 2.  The result is that for all pollutants, except CO, there are not significant emissions increases.

- Reference EPA Comment 1.a., Step 2 Netting Required:  “If the project shows a significant increase in emissions, netting analysis is required”.

Department Response:  The Department believes netting is allowed (if performed correctly) but not required.

- Reference EPA Comment 1.a., Step 2 Creditable Emissions increases and Decreases:  “The netting analysis should include both increases and decreases over the contemporaneous period.

Department Response:  The two residual oil and natural gas fueled units are overwhelmingly the only sources of any consequence on site.  They have not been modified for many years.  A PSD permit was issued for the two “helper cooling towers” that are the source of particulate matter (PM) emissions.  These are not being modified as part of the project, although a clarification is included regarding their use for 9,000 aggregated hours/year for the two towers instead of 4,500 hours/year for each tower (which also equals 9,000 hours for the two when combined).

The natural gas heaters were included in the analysis conducted by the applicant, but were overlooked by the Department when conducting its own calculations.  However, BACT emission limits were specified for these sources as part of the entire project.

- Reference EPA Comment 1.b., Startup, Shutdown, and Fugitive Emissions not Indicated:  “The application and the preliminary determination do not indicate if startup, shutdown, and fugitive emissions were included in the emission calculations”.

Department Response:  The startup and shutdown emission were included, though not delineated, for SO2 and NOX.  The baseline emissions for SO2 and NOX were derived from the EPA Air Markets Program Data link which captures all modes of acid rain unit operations.  Then startup emissions in the future for SO2 are imbedded in the projected actual emissions and are a straight function of fuel use.  Note that the potential to emit (PTE) SO2 is being reduced from approximately 120,000 tons/year to approximately 120 tons/year.

NOX emissions are highest at maximum production when the furnace temperature (and NOX formation potential) is at the maximum level.  Separate delineation of startup and shutdown NOX emissions would make very little difference in the calculations and none at all regarding PSD applicability.

In the case of PM/PM10, the startup and shutdown emissions from residual oil firing are much greater than those from firing natural gas.  Such startup and shutdown emissions will be much less in the future than in the past.  At low furnace temperature, residual fuel oil firing results in emissions of char particles (and CO) that do not achieve burnout within the furnace and are thus emitted.

The Department believes that if the applicant had included estimates of CO startup and shutdown emissions as well as low-to-medium load emissions when conducting estimates of baseline actual emissions, the most likely outcome is that PSD for CO would not have been triggered for the conversion to natural gas.  Due to lack of data, conservatively low estimates were made regarding past emissions and conservatively high estimates were made regarding future emissions of CO and volatile organic compounds (VOC).

The Department will emphasize to applicants to submit more complete information regarding these issues, but notes the overwhelmingly positive features of this particular project with respect to lower contribution to ozone formation, lower contribution to fine particulate formation, lower ground level SO2 and NO2 concentrations, lower contribution to interstate pollutant transport and lower emissions of hazardous air pollutants (HAP).

- EPA Comment 2, 1st Paragraph, Technical Feasibility of Oxidation Catalyst (Ox-cat):  “The applicant and the FDEP determined the use of an oxidation catalyst not technically feasible due to lack of demonstration for large fossil fuel-fired boilers.  However given that oxidation catalysts are available for boilers that are significantly smaller in size than the boilers proposed in this project, (e.g., Port Dolphin LNG issued by the EPA), the FDEP should provide additional technical information why an oxidation catalyst cannot be used on very large boilers.”

Department Response:  The Department did not determine that Ox-cat is technically infeasible and rejected the reasons given by the applicant for technical infeasibility.  In the Technical Evaluation and Preliminary Determination (TEPD) document, page 17, section titled, “Department’s Assessment of Applicant’s CO BACT Proposal”, the Department states:

“The Department disagrees with the rationale provided in support of the claim that Ox-cat is not technically feasible”.

The Department appreciates the determination that Ox-cat was considered as a technically feasible control technology for the three 278 MMBtu/hour marine boilers included in the Port Dolphin Liquefied Natural Gas (LNG) Terminal and Regasification project.  EPA concluded that further reduction by Ox-cat was cost-prohibitive at $29,938 cost/ton of CO removed.  Link to EPA Port Dolphin Evaluation .  The Department notes that only an annual test is required to demonstrate compliance with the low CO emission standard. 
Link to Port Dolphin PSD Permit .

The Department believes Ox-cat is technically feasible for natural gas-fired boilers and can be used on very large boilers.  However, it is often not cost-effective (e.g. as a retrofit) and seldom required to achieve BACT on large natural gas-fueled boilers (or apparently small ones per EPA).

- EPA Comment 2, 2nd Paragraph, Ox-cat Cost Analysis:  “The BACT analysis for the natural gas-fired boilers in the preliminary determination described a hypothetical cost comparison, page 19.  However the applicant did not provide a cost analysis in their application, and FDEP has not provided a detailed cost analysis in the preliminary determination”.

Department Response:  The Department concurs with these statements.

- EPA Comment 2, 2nd Paragraph, Cost Effectiveness:  “Since the preliminary determination includes this hypothetical statement and also a statement that an oxidation catalyst may be cost effective, it is unclear whether FDEP has concluded that catalytic oxidation is technically or economically infeasible.  This inconsistency should be clarified, and a full cost analysis should be included unless a demonstration can be made that catalytic oxidation is technically infeasible”.

Department Response:  A demonstration has not and cannot be made that catalytic oxidation is technically infeasible.  The Department reiterates the following conclusions:

- Ox-cat is technically feasible for natural gas-fired boilers and can be used on very large boilers;

- Ox-cat is not cost-effective for this project; and

- The correct BACT CO emission standard for this specific project is 0.15 pounds per million Btu heat input (lb/MMBtu).

Ox-cat has never been required for a gas-fired boiler in the size category of Anclote Units 1 and 2 let alone as a retrofit.  Further information is included in Section III of this Final Determination.

- EPA Comment 3.a, Tables should be corrected and other added:  “Table 7 in the preliminary determination provides the emissions for only the two generators and does not contain the natural gas heaters or any other possible facility emissions.  Additional tables should be added to the preliminary determination for each emission unit.  Also a summary table should be added that accounts for the netting analysis”.

Department Response:  As stated above, a netting analysis (i.e. Step 2), though allowed, is not required.  The following table is a list of the emissions units (EU) including the gas heaters added by the project.

# Table 1.  List of Emissions Units located at the Anclote Plant

| EU No. | ## Brief Description |
| --- | --- |
| Regulated Emissions Units |  |
| 001 | Fossil Fuel Fired Steam Generator Unit No. 1 (modified by the project, PSD/BACT for CO) |
| 002 | Fossil Fuel Fired Steam Generator Unit No. 2 (modified by the project, PSD/BACT for CO) |
| 007 | Two, 12-cell Mechanical Draft Helper Cooling Towers (PSD/BACT for PM in 2006) |
| 008 | Three relocatable Diesel Fired Engine Driven Generators (shared among six PEF facilities) |
| 009 | Two 16.5 MMBtu/hour Natural Gas Fuel Heaters (Added by the project, PSD/BACT for CO) |
| Unregulated Emissions Units and/or Activities |  |
| 003 | Surface Coating Operations |
| 005 | Emergency Diesel Generator |
| 006 | Diesel Air Compressor |

The two fossil-fuel-fired steam generators are almost identical and each will require as much as 5,500 MMBtu/hour of heat input to provide sufficient steam to drive its respective 556.2 MW (gross) steam turbine-electric generator.  For all practical purposes the only meaningful emissions units on the site.  Units 1 and 2 are the overwhelming features in terms of capacity.  All else is ancillary equipment.

As discussed above, there is every reason to believe that startup, shut down and fugitive emissions will be reduced for Units 1 and 2 when switching to natural gas.  The initial project that added limited natural gas capability was approved in 1998 pursuant to the electric generating unit pollution control project (PCP) exemption (since vacated), largely to reduce visible emissions and PM/sulfuric acid mist fallout.  Any startup and shutdown PM emissions from the helper cooling towers (that underwent a PSD/BACT determination for PM in 2006) will not change due to the project and any conceivable projected actual emissions and demand increases will be cancelled out by baseline emissions and demand growth exclusion.

The three relocatable diesel engine generators are shared between six facilities located in Pinellas, Pasco, Polk, Sumter and Citrus Counties.  Each has a rating of 0.82 MW.  Any startup and shutdown emission changes would be trivial compared with the changes due to Units 1 and 2.

The values given in Table 7 of the preliminary determination would increase as follows by inclusion of the gas heater emissions:  CO = 5.3 tons/year; VOC = 0.35 tons/year; NOX = 6.3 tons/year; SO2 = 0.18 tons/year; greenhouse gases (GHG) as equivalent carbon dioxide (CO2e) = 3,790 tons/year.  Table 7 from the preliminary determination is reproduced below as Table 2.  It has been updated and corrected to clarify that the estimates and conclusions are those of the Department and not those originally submitted by the applicant.  Addition of the emissions from the gas heaters to the 4th and 5th columns, while correct, makes no material difference in the conclusions given in the 6th column.

Table 2.  Department’s Emissions Estimates and PSD Applicability for Units 1, 2 and Gas heaters

| Pollutant | 24-Month Baseline Period (Selected Years) | Applicant Baseline Actual Emissions (tons/year) | Department Projected Actual Emissions (tons/year) | Projected Increase (tons/year) | > PSD SER? (tons/year) Yes/No |
| --- | --- | --- | --- | --- | --- |
| CO 1 | 2006 – 2007 | 506 | 3,025 1 + 5.3 | 2,519 + 5.3 | > 100? Yes |
| VOC | 2006 – 2007 | 78 | 84 + 0.35 | 6 + 0.35 | > 40? No |
| NOX | 2006 – 2007 | 6,540 | 3,781 + 6.35 | -2,759 + 6.35 | > 40? No |
| SO2 | 2006 – 2007 | 25,273 | 60 + 0.18 | -25,213 + 0.18 | > 40? No |
| GHG (CO2e) | 2006 – 2007 | 2,517,405 | 1,955,983 + 3,790 | -541,422 + 3,790 | > 75,000? No |
| Heat Input | 2006 - 2007 | 38,793,879 | 33,607,954 | -5,185,925 | Not Applicable |
| - The Department estimates 3,025 tons CO/year from Units 1 and 2 based on capacity factors and heat rates for 2014 in company submittals to Florida PSC. The Department estimates 8,673 tons/year as the PTE. |  |  |  |  |  |

- EPA Comment 3.b., Natural Gas Boilers versus Municipal Waste Combustors:  “The preliminary determination contains an evaluation of the applicant’s BACT analysis, page 19.  The analysis references municipal waste combustors as a comparable facility; however, there are a few large natural gas-fired boilers, generators, in the RACT/BACT/LAER clearinghouse that would provide a more relevant comparison e.g., Cleco Power Inc., LA”.

Department Response:  The Department agrees with the statements in principle.  The Department included detailed analyses of continuous emissions monitoring systems (CEMS) data from coal units optimized for NOX while achieving BACT-level CO control.  The Department made reference as well to municipal waste combustors (MWC) for which there is also a significant body of data from CEMS to help establish context for further discussion.  Usable data from large gas-fired boilers is difficult to obtain.  Otherwise, the applicant would have acquired it, included it with the application and possibly avoided PSD.

Cleco Power

The Department appreciates mention of the Cleco Power, Inc.  The reference cited in EPA’s comment is from the Table 15 of the application.  The determination was made by State of Louisiana Department of Environmental Quality (DEQ) in 2008 and the BACT CO limit for the 523 MW Rodemacher Unit 2) is 0.15 lb/MMBtu.  The Department agrees the reference is relevant and the BACT is equal to the Department’s determination for Anclote Units 1 and 2.

The matter is a little more complicated than pointing to an apparently similar project.  The unit remains a coal and natural gas-fueled unit.  For example a reference from Cleco’s 2011 Annual Report and Form 10-K ( Link to Cleco Annual Report ) regarding Cleco Rodemacher Unit 2 states:

“The coal supply agreements are fixed-priced for each year of the contract and together provide for the full requirements to support Cleco Power’s minimum planned dispatch of Rodemacher Unit 2 (four million tons total over the seven-year period)” …… “With respect to transportation of coal, Cleco Power has amended and extended an agreement with Union Pacific Railroad Company for transportation of coal from Wyoming’s Powder River Basin to Rodemacher Unit 2 through December 31, 2016”.

Monteville Power LLC

A promising example from the table is the Montville Power LLC, which is listed as an 82 MW natural gas boiler with Ox-cat to achieve a BACT CO limit of 0.084 lb/MMBtu.  Initially, the reference suggests (and the Department agrees) that Ox-cat is technically feasible for natural gas boilers.

An actual review of the permit, however, reveals the Monteville Power project is actually a conversion from an 82 MW natural gas-fueled unit to a 42 MW woody biomass fueled unit.  
Link to Monteville Permit .  The project description in the permit states:

“The 82 MW utility boiler, currently referred to as Unit 5, has been converted to combust biomass (clean wood) as a base load utility power plant with a net capacity of 42 MW.  The boiler shall be able to transition to natural gas or distillate firing at a net 82 MW for a limited annual capacity factor of seven percent.  The plant will utilize a stoker grate combustor (biomass firing) with regenerative selective catalytic reduction (RSCR) and Low NOX burners (fossil fuel firing) for NOX control, an electrostatic precipitator (ESP) and multi-cyclones for particulate matter control, an oxidation catalyst for CO, VOC and organic HAP control”.

Interestingly, the unit is a stoker grate combustor, much like a MWC.  Actually, the project is subsidized by participation in the State of Connecticut’s Renewable Portfolio Standard (RPS) that progressively increases the percentage of electricity that participants in Connecticutt’s power market must generate from renewable energy.  Link to CT RPS Overview .  Typically, the inclusion of Ox-cat for these biomass units greatly reduces the organic HAP and allows such units to avoid onerous Subpart DDDDD Boiler MACT standards (especially for PM) applicable to new or reconstructed units.

Virginia Power Possum Point Units 3 and 4

This facility was also included in the mentioned table.  Units 3 and 4 are vintage 1950’s and 1970’s coal units that were converted to burn natural gas in 2003 pursuant to a $1.2 billion multiple facility consent decree with EPA.   Consent Decree .  Units 3 and 4 are described as in the consent decree as 114 MW and 237 MW (nominal nameplate) units, respectively).  The permitted BACT CO limit is 0.024 lb/MMBtu.  The permitted NOX limit is 0.20 lb/MMBtu, however the units may emit more than 219 tons/year.  The units have Low NOX burners (LNB) and were converted at a total cost of $10,000,000.  They do not have Ox-cat.  The manner and extent to which overfire air injection is practiced is not known.

The Department accessed the Statement of Basis (SOB) and the Title V operation permit for the Possum Point Power Plant that was issued by the State of Virginia in 2010.  Link to Possum Point SOB , 
Link to Possum Point Title V Permit .

Units 3 and 4 are described as tangentially-fired natural gas boilers (Combustion Engineering) built 1955 and 1962, respectively and converted from coal firing in 2003.  The rated capacities are given in the permit as 1,150 and 2,350 MMBtu/hr, respectively (i.e. roughly 20 and 40% of the capacity of each Anclote unit).

Following is the explanatory excerpt regarding the CO limits:

“Both the short-term and annual CO emission limits are from Condition 23 of the 10/05/01 (amended 11/18/02, 12/8/04 and 7/11/08) PSD/Non-attainment Permit. The hourly and annual rate limits were confirmed by dispersion modeling for that permitting action to keep the facility from contributing to a violation of the NAAQS.  The heat input-based limits represent BACT”.

The CO limit is 0.024 lb/MMBtu.  CEMS are required.  However, compliance testing is stack tests triggered by indications from the CEMS.  According to the permit:

“The CEMS data for CO emissions may be grounds for DEQ to request that a stack test be performed to prove compliance, especially, but not limited to a case in which the permittee has not taken corrective action when the data indicate that a non-compliance condition may exist”.

Since the conversion, the Units have been operated on a minimal basis.  Among the reasons are the severe NOX annual mass emission limit and construction of a new and efficient gas-fueled combined cycle unit.  Today, Units 3 and 4 operate as peaking units on very hot summer days and very cold winter days.  For example, since 2004 Unit 3 has operated at an annual capacity factor ranging from 0.2% to 13.5% while Unit 4 has operated at an annual capacity factor ranging from 0.1% to 11.6%.

Although continuously measured, the BACT CO limits for Units 3 and 4 are not continuously enforceable.  The Department contacted the State of Virginia DEQ and was able to obtain one test for compliance testing on the 96 MW Unit 3.  An 18-hour CEMS-based record is shown in Figure 2.

Figure 2.  CEMS Record used to Demonstrate Compliance at Possum Point Unit 3 (7/18-19, 2011)

The results indicate that very low emissions are possible in a small electric generating unit converted from coal to natural gas.  The data are useful because they support the conclusion that Ox-cat is not necessary or cost-effective to achieve low CO values in natural gas-fueled electric power generating units equipped with LNB and meeting low NOX values.  Furthermore, the data are consistent with the hypothesis that PSD would not likely have been triggered by the natural gas conversion project at the Anclote Plant.

Lewis Creek Plant

During discussions with EPA staff, the Lewis Creek Plant (included in the mentioned application table) was pointed out as one that has a low CO limit of 15 parts per million (ppm).  That one was likely included in the table by mistake because the units are actually large gas-fueled combustion turbines operating in combined cycle (with heat recovery steam generators) that are usually characterized by very low CO emissions.  The Department typically permits such units with BACT CO limits of 5 ppm and without Ox-cat.

AES Huntington Beach (not in RACT/BACT/LAER Clearinghouse)

Huntington Beach Units 3 and 4 are identical (225 MW), vintage 1950’s, natural gas-fueled steam-electric units that were retired from use in 1995.  Subsequent rebuilding and upgrading was expedited by certification pursuant to an Executive Order from the California Governor, Gray Davis, to address California's electricity supply emergency.

In May 2001 the California Energy Commission approved AES’s proposed 450 megawatt Huntington Beach Units 3 and 4 Retool Project with the following requirements:

- Power plant NOX emissions will be minimized by flue gas recirculation (FGR), LNB and Selective Catalytic Reduction (SCR); and

- AES shall control CO by using an oxidizing catalyst to meet BACT emission limitations of 
5 ppm averaged over one hour.  AES shall install a CEMS for CO.  AES has obtained CO offsets.

Link to Certification .  The units were restarted in 2002 pursuant to the certification by the California Energy Commission.

The South Coast AQMD, where Huntington Beach is located, defines BACT for non-attainment pollutants such as CO in the same manner as Lowest Achievable Emission rate (LAER), which makes no provision for cost.  The South Coast Air Quality Management District (AQMD) designated the CO limit as BACT in 2006.  The SC AQMD report indicates that the units comply with the CO limit and essentially emit zero CO at full load.  Link to SCAQDM BACT .  A short report about the results is available at:  AES Huntington - Cleanest Plant .  The results prove that in practice Ox-cat is technically feasible and can greatly reduce CO emissions on natural gas-fueled boilers.

The two units were retired in January 2012, but temporarily brought out of retirement due to leaks experienced at Southern California Edison’s San Onofre nuclear units.  Ultimately they must be retired because of offset required by modern projects proposed by AES and Edison Mission Energy.  
Link to AES California News .

Conclusion from the RACT/BACT/LAER Clearinghouse

Clearly, very low CO BACT limits or Ox-cat requirements for small to medium sized natural gas-fueled electric utility boilers exist only under very unusual permitting conditions (e.g. consent orders, LAER, power emergencies).  The only large natural gas-fueled electric utility boiler comparable with Anclote Units 3 and 4 is the 523 MW Cleco Power Rodemacher Unit 2.  The applicable CO BACT limit for that project is equal to the Department’s determination of 0.15 lb/MMBtu.

- DISCUSSION OF ECONOMIC FEASIBILITY OF OX-CAT FOR THIS PROJECT

In the present CO BACT determination, a number of factors will affect the economic feasibility analysis.  These include:

- Units 1 and 2 have remaining life through 2024 per the filing with the Florida Public Service Commission regarding the project.  Link to PSC Filing ;

- Units 1 and 2 are very large and existing units which would require much more work and cost to retrofit with Ox-cat compared with smaller units or incorporation of Ox-cat on units still on the drawing boards;

- The units will likely achieve less CO emissions than projected (e.g. like Possum Point Units 3 and 4);

- If the applicant had actually collected baseline CO emissions throughout the full operating range of the units as presently operated, then PSD for CO would likely not have been triggered;

- Good combustion practices are already required, including natural gas firing and close coupled overfire air (CCOFA);

- The project reduces the potential to emit SO2 by approximately 120,000 tons/year;

- The project reduces impacts on regional haze at the Chassahowitzka National Wildlife Area (NWA) to the point that the Anclote Plant now models out of any requirement to conduct a best available retrofit technology (BART) determination; and

- Further CO reductions (other than by Ox-cat) may come at the expense of NOX.

In the preliminary determination the Department noted that Department and EPA do not actually have “bright line thresholds for cost-effectiveness”.  If it is conservatively assumed that CO emissions will actually be 0.15 lb/MMBtu, then 90% CO reduction by Ox-cat will reduce emissions to 0.015 lb/MMBtu.  If it is very conservatively assumed that the units will operate at 100% annual capacity factor, then CO emissions will be reduced by 7,806 tons/year.

The Department accessed a report prepared by URS for the Pulp and Paper industry that included costs of oxidation catalyst for control of hazardous air pollutants from boilers.  Link to MACT Pulp and Paper .  The capital cost estimate for combustion improvements or Ox-cat for CO control is given as $3,000,000 for a boiler with a heat input rating of 250 MMBtu/hour.  Anclote Units 1 and 2 are each 22 times the size of such a model boiler.  Using a standard 0.6 exponent for scaling up the size of a typical piece of equipment yields a cost estimate of ($3,000,000/unit)x(22)0.6 = $19.2 million/unit or $38.4 million.

The estimated cost of the natural gas conversion project is $79,000,000 and it will result in massive reductions in SO2 and substantial reduction in PM, NOX, GHG and metal HAP.  After conversion to natural gas, there will be practically no organic HAP emissions and the only pollutant that could be reduced by Ox-cat is CO (e.g. in contrast to organic HAP from biomass units).  The Department does not consider an additional expenditure of $38,400,000 to be cost effective.  If put on the basis of cost per ton of CO removed, the Department estimates that the cost-effectiveness is approximately $900 to $1,000/ton.

The tendency of many applicants and agencies is to try to show that the cost-effectiveness of Ox-cat control for CO is greater than (or alternatively, less than) a cost-effectiveness value of the same order of magnitude characteristic of other criteria pollutants, like NOX and SO2.  Control of the NOX, VOC, SO2 and fine PM at costs in the thousands of dollars/ton avoids the externalities (costs) that are (depending on the part of the country), theoretically also worth thousands of dollars/ton in environmental damage from haze, health costs, water body acidification, fine particle formation, ozone formation, effects on monuments, effects on biota, etc.)

A few agencies have studied the matter in greater depth and used more realistic cost-effectiveness thresholds for control of CO.  For example, the San Diego Air Pollution Control District (APCD) uses a threshold of $12,000/ton of NOX or VOC removed to determine cost-effectiveness.  When considering CO control, San Diego APCD references the San Joaquin Valley APCD value of $300/ton.  The South Coast AQMD uses a value of $400/ton for the attainment areas (notwithstanding that cost is not a consideration in parts of the district that are non-attainment for CO).  Link to San Diego BACT .

Per the preliminary determination document, the estimated maximum 1-hour and 8-hour CO impacts from the 500-foot stack serving Units 1 and 2 are estimated at 164 and 31 micrograms per cubic meter (µg/m3), respectively.  These values equal 0.14 and 0.03 parts per million (ppm).

The highest 1-hour and 8-hour CO values measured at nearby monitoring stations were 1.5 and 1 ppm, respectively.  For reference, the 1-hour and 8-hour National Ambient Air Quality Standards (NAAQS) are 35 and 9 ppm, respectively.  In other words, the project maximum ground-level impacts of the project are less than 0.5% of the NAAQS.

Gaseous CO does not participate in ozone or fine PM formation and does not persist in the ambient air – ultimately oxidizing to CO2 (the same product of catalytic oxidation).  No PSD increments have been specified for CO to avoid significant deterioration in Class 1 or Class 2 areas.

CO emitted from a plant that easily complies with the NAAQS has virtually no externalities requiring a large investment to avoid.  When not masking or acting as a surrogate for other pollutants (like organic HAP, VOC or soot), CO emitted from a tall stack has minimal environmental impact.

For reference, natural gas-fueled electric generating units (in contrast to coal and oil-fueled electric generating units) are not subject to the Utility NESHAP, Subpart UUUUU including the CO limitations applicable to such units.

The Department provided a clear rationale in reducing the proposed limit to 0.15 lb/MMBtu, consistent with its recent determinations for large existing units.  Add-on control of CO by Ox-cat for this project would not bring any other tangible benefits than CO reductions.  The Department does not consider Ox-cat to be cost-effective at $900 to 1,000/ton CO removed for large utility boilers converting to natural gas and reiterates its previous conclusion.  This determination does not establish a “bright line” for acceptance or rejection of CO control technologies.  Department reserves its authority to issue BACT determinations on a case-by-case basis considering all of the circumstances of each project.

- CONCLUSION

The applicant, the Department and Region 4 air management staff were all motivated to insure that this permit is issued promptly.  This allows the public and the environment to realize the manifold benefits (including lower electric bills) of the project while complying with multiple federal rules at the earliest possible date.

The final action of the Department is to issue the permit with changes as indicated above.