Permittee

| City of St. Petersburg 635 3rd Avenue North St. Petersburg, Florida 33713 Authorized Representative: Mr. Steve Leavitt, P.E., Director | Air Permit No. 1030558-001-AC Permit Expires: January 1, 2017 Minor Air Construction Permit Southwest Water Resource Facility Biosolids Improvement Project |
| --- | --- |

Project

This is the final air construction permit, which authorizes the City of St. Petersburg’s (City) to consolidate their biosolids operations from all of their treatment plants to the Southwest Water Resource Facility (SWWRF) to capture the digester gas and clean it up to natural gas standards to fuel the City’s sanitation vehicle fleet and provide electricity to the City’s SWWRF.  The proposed work will be conducted at existing SWWRF, which is an existing domestic wastewater treatment plant categorized under Standard Industrial Classification Code No. 4952.  The existing SWWRF is located in Pinellas County at 3800 54th Avenue South in St. Petersburg, Florida.  The UTM coordinates are Zone 17, 333.8 kilometers (km) East, and 3067.2 km North.

This final permit is organized into the following sections:  Section 1 (General Information); Section 2 (Administrative Requirements); Section 3 (Emissions Unit Specific Conditions); and Section 4 (Appendices).  Because of the technical nature of the project, the permit contains numerous acronyms and abbreviations, which are defined in Appendix A of Section 4 of this permit.

Statement of Basis

This air pollution construction permit is issued under the provisions of:  Chapter 403 of the Florida Statutes (F.S.) and Chapters 62-4, 62-204, 62-210, 62-212, 62-296 and 62-297 of the Florida Administrative Code (F.A.C.).  The permittee is authorized to conduct the proposed work in accordance with the conditions of this permit.  This project is subject to the general preconstruction review requirements in Rule 62-212.300, F.A.C. and is not subject to the preconstruction review requirements for major stationary sources in Rule 62-212.400, F.A.C. for the Prevention of Significant Deterioration (PSD) of Air Quality.

Upon issuance of this final permit, any party to this order has the right to seek judicial review of it under Section 120.68 of the Florida Statutes by filing a notice of appeal under Rule 9.110 of the Florida Rules of Appellate Procedure with the clerk of the Department of Environmental Protection in the Office of General Counsel (Mail Station #35, 3900 Commonwealth Boulevard, Tallahassee, Florida, 32399-3000) and by filing a copy of the notice of appeal accompanied by the applicable filing fees with the appropriate District Court of Appeal.  The notice must be filed within 30 days after this order is filed with the clerk of the Department.

Executed in Tallahassee, Florida

(DRAFT)

for	Jeffery F. Koerner, Program Administrator

Office of Permitting and Compliance

Division of Air Resource Management

## CERTIFICATE OF SERVICE

The undersigned duly designated deputy agency clerk hereby certifies that this Air Permit package was sent by electronic mail, or a link to these documents made available electronically on a publicly accessible server, with received receipt requested before the close of business on the date indicated below to the following persons.

# Mr. Steve Leavitt, P.E., Director, City of St. Pete:  steve.leavitt@stpete.org

# Mr. Steve Marshall, Project Manager, City of St. Pete:  sdmarsha@stpete.org

# Mr. Andrew Westfall, P.E., Black & Veatch:  westfallAA@bv.com

# Mr. George (Ken) Wise, Operator, SWWRF:  george.wise@st.pete.org

# Ms. Kelley Boatwright, Administrator, SWD:  kelley.m.boatwright@dep.state.fl.us

# Ms. Heather Ceron, US EPA Region 4:  ceron.heather@epa.gov

# Ms. Lorinda Shepherd, EPA Region 4:  shephard.lorinda@epa.gov

# Ms. Lynn Scearce, DEP OPC:  lynn.scearce@dep.state.fl.us

# Clerk Stamp

# FILING AND ACKNOWLEDGMENT FILED, on this date, pursuant to Section 120.52(7), Florida Statutes, with the designated agency clerk, receipt of which is hereby acknowledged.

(DRAFT)

Facility Description

City of St Petersburg, SWWRF, is an existing domestic wastewater treatment plant, which is categorized under Standard Industrial Classification Code No. 4952.  The existing facility is a 20 million gallon per day (MMGD) annual average daily flow, Type I complete mix activated sludge domestic wastewater treatment plant.  The plant is a dual train facility with wastewater entering the plant by both force main and gravity lines.  The force main influent flows directly to the head-works structure while the gravity line flows first to the 40 MMGD influent pump station, the head-works has two mechanically cleaned fine bar screens and a manually cleaned by-pass bar screen prior to grit removal, one influent pump station with four 10 MMGD submersible pumps, two rectangular aeration basins, equipped with fine bubble diffusers, with a total volume of 4.03 million gallons, three clarifiers providing a total capacity of 3.85 million gallons with a total surface area of 42,942 square feet; a transfer pumping station; four manually backwashed deep bed dual media filters providing a total surface area of 5,624 square feet; and a dual channel chlorine contact chamber of 474,591 gallons, using a liquid sodium hypochlorite system.

The biosolids treatment system consists of: one gravity belt thickener; two anaerobic digesters with a total volume of 2.6 million gallons operated in series; and two belt filter presses. Filtrate from the process is returned to the head-works of the treatment plant.  After dewatering by the filter press, biosolids stabilization by the Bioset process to a Class AA is completed.  Lime and acid are added to the solids and pumped through a plug flow reactor and allowed to rise in temperature and pH, to release ammonia. The Class AA material is then transported off-site for land application or commercial sales.

Reclaimed water storage is provided in one 5 million gallon ground storage tank and in one 10 million gallon ground storage tank.  Reclaimed water will be directed to the St. Petersburg Master Reuse System.  Reclaimed water can also be routed to the aquifer storage and recovery well and to the injection well system if necessary.  Reject water is stored in a 15 million gallon ground storage tank.  Reject water may be directed to the 5 million gallon and 10 million gallon ground storage tanks in an emergency.  After normal plant operations resumes, reject water is directed to the filters for re-treatment.

Backup power is provided by four, on-site standby diesel powered generators.

PROPOSED PROJECT

The City of St. Petersburg proposes to construct and operate a biosolids-to-energy plant at their existing SWWRF.  The facility will consolidate the City’s biosolids operations for all their treatment plants at SWWRF to capture the digester gas and clean it to natural gas standards to fuel for the City’s sanitation vehicles, boilers and for electrical energy production.  The City operates four water reclamation facilities (SWWRF, Northeast WRF, Albert Whitted WRF, and Northwest WRF).  The biosolids improvement project is comprised of:

- Biosolids-to-Energy Project:  Upgrading and installing new clarification systems, new anaerobic digesters and improvements to an existing digester, new sludge handling equipment, new digester gas handling facilities, new Biosolids upgrade systems (BUS), and new odor control facilities.  Emission sources associated with this project includes: four flares; and two carbon scrubbers to control odor emissions from the primary clarifiers, the sludge storage tank, and the thickening facilities.

- Biosolids Dewatering Project:  Expanding the sludge thickening process and upgrading of the sludge dewatering system.  Emission sources associated with this project includes: a cooling tower; two 6.38 million British thermal units per hour (MMBtu/hour) boilers firing natural gas and cleaned digester BUS gas; and a carbon scrubber to control odor emissions from the sludge dewatering and truck loading areas.

- Generator and Electrical Improvements Project:  Construct a new combined heat and power facility coupled with an expanded emergency backup power system.  Emission sources associated with this project includes: two 1.1 megawatt (MW) reciprocating internal combustion engine (RICE)/electrical generator sets firing natural gas and cleaned digester BUS gas; and two diesel fired emergency generators (2,347 horse power (HP) and 2,682 HP).

Liquid wastewater will undergo a pre-treatment process to remove contaminants and moisture.  Waste activated sludge is sent through a sludge thickening process where fats, oils and grease is added prior to entering three continuously stirred tank reactor digesters.  The digesters will break down the organics and convert them primarily into methane (CH4) and carbon dioxide (CO2).  Two flares will be used to combust excess gas from the digesters.  After the digestion process, the gas is cooled through a process using, in part, cooling water from the cooling tower and the moisture is removed prior to the digester gas passing through the BUS.  The BUS is designed to process raw digester gas to pipeline natural gas quality.  A thermal oxidizer will be used to combust waste gas from the bus and a candlestick startup flare will be used to combust BUS product gas (cleaned digester gas).  The cleaned digester BUS gas will either be sent to the onsite engine-generators or sent to the compressed natural gas (CNG) fueling system for further compression.  The final compression and CNG fueling system compresses the cleaned digester BUS gas to high pressure for tube-trailer fueling or onsite high pressure storage.  Two natural gas and cleaned digester BUS gas fired boilers will also be used to heat water for use throughout the process.

Construction is scheduled to commence in 2014 and be completed in 2018.  The two 1.1 MW RICE/electrical generator sets will be installed and operating for a period of 2 or 3 years prior to the cleaned digester BUS gas being available for the engines.  During this period, the engines/generators will fire exclusively pipeline natural gas.

{Permitting Note:  Flares 1, 2 and 4 are exempt from permitting based on the provisions under Rule 62-210.300(3)(b), F.A.C., Generic and Temporary Exemptions.  Two 9,000 gallon (34.069 cm) diesel storage tanks used to store fuel for the two emergency diesel generators are well below the vapor pressure specified in NSPS Subpart Kb.  Therefore, the tanks are not subject to any unit-specific limitation or requirement.}

This project consists of the following emissions units (EU).

| EU No. | Description |
| --- | --- |
| 001 & 002 | Two nominal 1.1 MW Spark Ignition RICE/generator sets (1,517 HP, each) |
| 003 & 004 | Two Boilers (6.38 MMBtu/hour, each) |
| 005 | Flare #3, Thermal Oxidizer (140 scfm) |
| 006 | Odor Control Systems |
| 007 | Cooling Tower |
| 008 | Diesel Fired Emergency Generator (2,347 HP) |
| 009 | Diesel Fired Emergency Generator (2,682 HP) |

Facility Regulatory Classification

- The facility is not a major source of hazardous air pollutants (HAP).

- The facility does not operate units subject to the acid rain provisions of the Clean Air Act (CAA).

- The facility is not a Title V major source of air pollution in accordance with Chapter 62-213, F.A.C.

- The facility is not a major stationary source in accordance with Rule 62-212.400(PSD), F.A.C.

- The facility does operate units subject to the New Source Performance Standards (NSPS) of 40 CFR 60.

- The facility does operate units subject to the National Emissions Standards for Hazardous Air Pollutants (NESHAP) of 40 CFR 63.

- Permitting Authority:  The permitting authority for this project is the Office of Permitting and Compliance in the Division of Air Resource Management of the Department of Environmental Protection (Department).  The Office of Permitting and Compliance mailing address is 2600 Blairstone Road (MS #5505), Tallahassee, Florida  32399-2400.

- Compliance Authority:  All documents related to compliance activities such as reports, tests, and notifications shall be submitted to the Southwest District Office at:  13051 North Telecom Parkway, Temple Terrace, Florida  33637-0926.

- Appendices:  The following Appendices are attached as a part of this permit:  Appendix A (Citation Formats and Glossary of Common Terms); Appendix B (General Conditions); Appendix C (Common Conditions); Appendix D (Common Testing Requirements); Appendix E (NSPS Subpart A); Appendix F (NSPS Subpart IIII); Appendix G (NSPS Subpart JJJJ); Appendix H (NESHAP A); and Appendix I (NESHAP ZZZZ).

- Applicable Regulations, Forms and Application Procedures:   Unless otherwise specified in this permit, the construction and operation of the subject emissions units shall be in accordance with the capacities and specifications stated in the application.  The facility is subject to all applicable provisions of: Chapter 403, F.S.; and Chapters 62-4, 62-204, 62-210, 62-212, 62-213, 62-296 and 62-297, F.A.C.  Issuance of this permit does not relieve the permittee from compliance with any applicable federal, state, or local permitting or regulations.

- New or Additional Conditions:  For good cause shown and after notice and an administrative hearing, if requested, the Department may require the permittee to conform to new or additional conditions.  The Department shall allow the permittee a reasonable time to conform to the new or additional conditions, and on application of the permittee, the Department may grant additional time.  [Rule 62-4.080, F.A.C.]

- Modifications:  The permittee shall notify the Compliance Authority upon commencement of construction.  No new emissions unit shall be constructed and no existing emissions unit shall be modified without obtaining an air construction permit from the Department.  Such permit shall be obtained prior to beginning construction or modification.  [Rules 62-210.300(1) and 62-212.300(1)(a), F.A.C.]

- Construction and Expiration.  The expiration date shown on the first page of this permit provides time to complete the physical construction activities authorized by this permit, complete any necessary compliance testing, and obtain an operation permit.  Notwithstanding this expiration date, all specific emissions limitations and operating requirements established by this permit shall remain in effect until the facility or emissions unit is permanently shut down.  For good cause, the permittee may request that that a permit be extended.  Pursuant to Rule 62-4.080(3), F.A.C., such a request shall be submitted to the Permitting Authority in writing before the permit expires.  [Rules 62-4.070(4), 62-4.080 & 62-210.300(1), F.A.C.]

- Objectionable Odors Prohibited:  No person shall cause, suffer, allow or permit the discharge of air pollutants which cause or contribute to an objectionable odor.  [Rule 62-296.320(2), F.A.C.]

{Note:  An objectionable odor is defined in Rule 62-210.200(Definitions), F.A.C., as any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance.}

- Source Obligation:

- Authorization to construct shall expire if construction is not commenced within 18 months after receipt of the permit, if construction is discontinued for a period of 18 months or more, or if construction is not completed within a reasonable time. This provision does not apply to the time period between construction of the approved phases of a phased construction project except that each phase must commence construction within 18 months of the commencement date established by the Department in the permit.

- At such time that a particular source or modification becomes a major stationary source or major modification (as these terms were defined at the time the source obtained the enforceable limitation) solely by virtue of a relaxation in any enforceable limitation which was established after August 7, 1980, on the capacity of the source or modification otherwise to emit a pollutant, such as a restriction on hours of operation, then the requirements of subsections 62-212.400(4) through (12), F.A.C., shall apply to the source or modification as though construction had not yet commenced on the source or modification.

- At such time that a particular source or modification becomes a major stationary source or major modification (as these terms were defined at the time the source obtained the enforceable limitation) solely by exceeding its projected actual emissions, then the requirements of subsections 62-212.400(4) through (12), F.A.C., shall apply to the source or modification as though construction had not yet commenced on the source or modification.

[Rule 62-212.400(12), F.A.C.]

- Application for Air Operation Permit:  This permit authorizes construction of the permitted emissions units and initial operation to determine compliance with Department rules.  An air operation permit is required for regular operation of the permitted emissions units.  The permittee shall apply for an air operation permit at least 90 days prior to expiration of this permit, but no later than 180 days after commencing operation.  To apply for a operation permit, the applicant shall submit the appropriate application form, compliance test results, and such additional information as the Department may by law require.  The application shall be submitted to the appropriate Permitting Authority with copies to the Compliance Authority.  [Rules 62-4.030, 62-4.050, and 62-4.220, F.A.C.]

This section of the permit addresses the following emissions units.

| EU No. | Emission Unit Description |
| --- | --- |
| 001 & 002 | Two nominal 1.1 MW Spark Ignition RICE/generator sets (1,517 HP, each) |
| 003 & 004 | Two Boilers (6.38 MMBtu/hour, each) |

Equipment

- The permittee is authorized to install and operate the following processes and equipment:

- Biosolids Process, including:  primary clarification systems with waste sludge collection; anaerobic digesters; biosolids batch tanks, fats, oils and grease storage tank; and sludge handling equipment including waste activated sludge storage tank, thickening facilities, dewatering building; and supporting heat exchangers, pumps, piping and instrumentation.

- Digester Gas, Power Generation and Heat Recovery Process, including:  biogas storage, Biogas Upgrade System; four flares (760 standard cubic feet per minute (scfm), 600 scfm, 200 scfm, and 140 scfm); two natural gas and cleaned digester BUS gas fired engine/generator sets (1,517 HP, each) and boilers (6.8 MMBtu/hour, each); two diesel-fueled emergency generators; two 9,000 gallon fuel storage tanks; and supporting heat exchangers, pumps, piping and instrumentation.

- Odor Removal Process, including:  collection ductwork and two new odor control systems (biotrickling filters/carbon scrubbers) with supporting blowers, electric pumps and chemical feed systems.

[Design, Application No. 1030558-001-AC]

- Engine/Generator Sets:  The permittee is authorized to install and operate two spark-ignited RICE/generator sets (Cummins Model C1100 N6C, or equivalent) that will fire natural gas and cleaned digester BUS gas with the following nominal design specifications per engine:  a maximum engine rating of 1,517 HP at 100% load; a nominal electrical generator rating of 1.1 MW; and a heat input rate of approximately 18.2 MMBtu/hour from cleaned digester BUS gas.  Each engine shall be equipped with:

- An air-to-fuel ratio controller and ignition timing to maintain efficient fuel combustion.

- An automatic fail-safe block valve, which must be designed to stop the flow of natural gas and cleaned digester BUS gas in the event of an engine failure.

- A non-resettable elapsed time meter to indicate the elapsed engine operating time in cumulative hours.

- A gas flow meter to monitor the actual natural gas and cleaned digester BUS gas flow rate to each engine.

{Permitting Note:  The heat input rate is based on 100% load (1,517 bhp), a nominal natural gas and cleaned digester BUS gas heating value of 1,020 Btu/scf and 990 Btu/scf and an approximate natural gas firing rate of 156.7 scfm and cleaned digester BUS gas firing rate of 161.7 scfm, respectively per engine.}  
[Design, Application No. 1030558-001-AC]

- Heating Boilers:  The permittee is authorized to install and operate two heating water boilers (HURST Series 45, or equivalent) that will fire natural gas and cleaned digester BUS gas to provide supplemental heating to the biosolids improvement project with a design heat input rate of 6.38 MMBtu/hour, each.  Each boiler shall be equipped with a gas flow meter to monitor the actual natural gas and digester gas flow rate to each boiler.  [Design, Application No. 1030558-001-AC]

Performance Restrictions

- Permitted Capacity:  Each engine/generator set has a maximum engine power rating of 1,517 HP at 100% load (approximately 990 MMBtu/hour for cleaned digester BUS gas and 1,020 MMBtu/hour for natural gas) with an electrical generator rating 1.1 MW, nominal.  [Design, Application No. 1030558-001-AC, and Rule 62-210.200(PTE), F.A.C.]

- Authorized Fuel:  Only natural gas and cleaned digester BUS gas shall be fired in the boilers and engine/generator sets.  Prior to firing cleaned digester BUS gas in these engines, the permittee shall submit to the compliance authority the engine manufacturers’ certifications stating that these engines will meet the emission limits in Specific Conditions 10 through 13 when firing cleaned digester BUS gas or the engines shall be subject to the requirements in Specific Condition 22.  [Design, Application No. 1030558-001-AC; and, Rule 62-210.200(PTE), F.A.C.]

- Hours of Operation:  Operation of the new engine/generator sets and boilers are not limited (8,760 hours/year).  [Design, Application No. 1030558-001-AC; and, Rule 62-210.200(PTE), F.A.C.]

Applicable Requirements

- Applicable NSPS Provisions:  The natural gas and cleaned digester BUS gas fired engines are subject to, and shall comply with, the applicable provisions in NSPS Subpart A (General Provisions) and NSPS Subpart JJJJ (Stationary Spark Ignition Internal Combustion Engines) of 40 CFR 60, which are identified in Appendix E and G of this permit, respectively.  [Rule 62-204.800, F.A.C.; and, NSPS Subparts A and JJJJ in 40 CFR 60]

- Applicable NESHAP Provisions:  The natural gas and cleaned digester BUS gas fired engines are subject to, and shall comply with, the applicable provisions in NESHAP Subpart A (General Provisions) and NESHAP Subpart ZZZZ (Reciprocating Internal Combustion Engines) of 40 CFR 63, which are identified in Appendix H and I of this permit, respectively.  Pursuant to §63.6590 of this subpart, the requirements of NESHAP Subpart ZZZZ are met by complying with the requirements of NSPS Subpart JJJJ.  [Rule 62-204.800, F.A.C.; and, NESHAP Subparts A and ZZZZ of 40 CFR 63]

- Operating Requirements.

- Engine Certification Requirements.  The permittee shall operate and maintain the engines according to the manufacturer's written instructions or procedures developed by the owner or operator that are approved by the engine manufacturer.  In addition, owners and operators may only change those settings that are permitted by the manufacturer.  These engines/generators must be maintained and operated to meet the emissions limits over the entire life of the engines.

- Loss of Certification Requirements.  The permittee shall set the air-to-fuel ratio for each engine based on the most recent emissions tests demonstrating compliance with the standards specified in this permit and other operating conditions identified in NSPS Subpart JJJJ of 40 CFR 60.

[Rules 62-4.070(3) and 62-204.800(8)(b)81, F.A.C.; and, NSPS Subpart JJJJ of 40 CFR 60]

##### Emissions Standards

{Permitting Note:  To avoid Title V status, the applicant requested NOX, CO and VOC natural gas standards when the engines/generator are firing cleaned digester BUS gas.}

- Engine NOx Emissions:  The emissions of nitrogen oxide (NOX) from each engine/generator set shall not exceed 1.0 grams/horsepower-hour (g/HP-hour, equivalent to 3.34 lb/hour).  [Rules 62-4.070(1)&(3) and 62-204.800(8)(b)81, F.A.C.; and, NSPS Subpart JJJJ of 40 CFR 60]

- Engine CO Emissions:  The emissions of carbon monoxide (CO) from each engine/generator set shall not exceed 2.0 g/HP-hour (equivalent 6.69 lb/hour).  [Rules 62-4.070(1)&(3) and 62-204.800(8)(b)81, F.A.C.; and, NSPS Subpart JJJJ of 40 CFR 60]

- Engine VOC Emissions:  The emissions of volatile organic compounds (VOC) from each engine/generator set shall not exceed 0.7 g/HP-hour (equivalent to 2.34 lb/hour).  When calculating emission of VOC, emissions of formaldehyde should not be included.  [Rules 62-4.070(1)&(3) and 62-204.800(8)(b)81, F.A.C.; and, NSPS Subpart JJJJ of 40 CFR 60]

- Engine PM Emissions:  The emissions of particulate matter (PM) from each engine/generator set shall be minimized by firing natural gas and cleaned digester BUS gas meeting the characteristics of pipeline quality natural gas, or equivalent there to.  Compliance with SO2 emissions shall be demonstrated by the sampling and analysis of the cleaned digester BUS gas.  [Design, Application No. 1030558-001-AC; and, Rule 62-210.200(PTE), F.A.C.]

- Boiler SO2 Emissions:  The emissions of sulfur dioxide (SO2) from the boilers shall be minimized by firing natural gas and cleaned digester BUS gas meeting the characteristics of pipeline quality natural gas, or equivalent there to.  Compliance with SO2 emissions shall be demonstrated by the sampling and analysis of the cleaned digester BUS gas.  [Rule 62-296.406(3)(BACT), F.A.C.]

- Boiler PM Emissions:  The emission of particulate matter (PM) from the each boiler shall be demonstrated by the visible emissions limitation, which serves as an indicator of good combustion.  
[Rule 62-296.406(2)(BACT), F.A.C.]

- Boiler Visible Emissions:  Visible emission from the each boiler shall not exceed 20% opacity except for one 6-minute period per 1-hour period during which opacity shall not exceed 27%.  [Rule 62-296.406(1), F.A.C.]

##### Testing Requirements

- Test Requirements:  The permittee shall notify the Compliance Authority in writing at least 15 days prior to any required tests.  Tests shall be conducted in accordance with the applicable requirements specified in Appendix D (Common Testing Requirements) of this permit.  [Rule 62-297.310(7)(a)9, F.A.C.]

- Test Methods:  Required tests shall be performed in accordance with the following reference methods.

| Method | Description of Method and Comments |
| --- | --- |
| 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| 7E | Determination of NOx Emissions from Stationary Sources |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |
| 10 | Determination of CO Emissions from Stationary Sources (based on continuous sampling train) |
| 18 | Measurement of Gaseous Organic Compound Emissions by Gas Chromatography |
| 25A | Method for Determining Gaseous Organic Concentrations (Flame Ionization) |
| 320 | Measurement of Vapor Phase Organic and Inorganic Emissions by Extractive Fourier Transform Infrared (FTIR) Spectroscopy |

The above methods are described in Appendix A of 40 CFR 60 and are adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Rules 62-204.800 and 62-297.100, F.A.C.; and Appendix A of 40 CFR 60]

- Initial Compliance Tests:  Each boiler shall be tested to demonstrate initial compliance with opacity.  The initial tests shall be conducted within 60 days after achieving permitted capacity, but not later than 180 days after initial operation of the unit.  [Rules 62-4.070(3) and 62-297.310(7)(a)1, F.A.C.]

- Annual Compliance Tests:  During each federal fiscal year (October 1st to September 30th), each boiler shall be tested to demonstrate compliance with opacity.  [Rule 62-297.310(7)(a)4, F.A.C.]

- Engine Certification Requirements.  The permittee shall comply with the emissions standards specified above by having purchased an engine certified by the manufacturer to meet those limits.  The engine must have been installed and configured according to the manufacturer’s emission-related specifications.  No performance testing is required.  [Rule 62-204.800(8)(b)81, F.A.C.; and, NSPS Subpart JJJJ of 40 CFR 60.4243]

- Loss of Certification.  If you do not install, configure, operate, and maintain your engine and control device according to the manufacturer's emission-related written instructions, or you change emission-related settings in a way that is not permitted by the manufacturer, your engine will be considered a non-certified engine.

- Initial Compliance Tests for Non-Certified Engines:  Each engine/generator shall be tested to demonstrate initial compliance with the emissions standards for CO, NOX, and VOC.  The initial tests shall be conducted within 1-year after the engines and control devices are no longer installed, configured, operated, and maintained in accordance with the manufacturer's emission-related written instructions, or within 1-year after you change emission-related settings in a way that is not permitted by the manufacturer.  If the engines lose their certification due to the firing of cleaned digester BUS gas, an initial performance test shall be conducted for CO, NOX and VOC emissions within 60 days after the engines/generators start firing cleaned digester BUS gas.

- Periodic Compliance Tests for Non-Certified Engines:  Every 8,760 engine hours or at least once every three years, whichever comes first, each engine/generator set shall be tested to demonstrate compliance with the emissions standards for CO, NOX and VOC.

[Rules 62-4.070(3), 62-204.800(8)(b)81, 62-297.310(7), F.A.C.; and, NSPS Subpart JJJJ of 40 CFR 60.4243]

Monitoring Requirements

- Digester Gas Sampling/Analysis:  Within 30 days after the engines/generators start firing cleaned digester BUS gas, the permittee shall obtain representative samples of the digester gas.  Each gas sample shall be collected under normal operating conditions with the appropriate canister (e.g., SUMMA®, Bottle-Vac Sampler, or equivalent).  Each sample shall have an analysis conducted to determine the characteristics of the digester gas, including the hydrogen sulfide (H2S) concentration.  If the analysis shows the digester gas meets or is equivalent to the following characteristics of pipeline natural gas, no additional sampling is required.

- Higher heating value of 990 Btu/scf;

- Methane - 98% by volume, dry;

- Carbon Dioxide (CO2) – 2% by volume, dry;

- Oxygen (O2) – 0.1% by volume, dry;

- H2S – 1 parts per million (ppm) by volume

- CO2, NOX and O2, combined – 2% by volume; and

- Siloxanes, ammonia and other VOC – Non-detectable parts per billion (ppb) by volume.

If the analysis shows the digester gas does not meet natural gas standards, the permittee shall provide the Department with new calculations for all PSD pollutants and HAPs resulting from this project as well as facility-wide emissions to determine PSD applicability and Title V status.

[Design, Application No. 1030558-001-AC; and Rules 62-4.070(1)-(3), 62-210.200(PTE), and 62-296.406(3)(BACT), F.A.C.]

Records and Reports

- Engines/Generator Records:

    - All notifications submitted and supporting documentation.

    - Maintenance conducted on the engine.

    - Certified engines, documentation from the manufacturer that the engine is certified to meet the emission standards and information as required in 40 CFR Parts 90, 1048, 1054, and 1060, as applicable.

    - Non-certified engines or certified engines operating in a non-certified manner and subject to §60.4243(a)(2), documentation that the engine meets the emission standards.

[Rule 62-204.800(8)(b)81, F.A.C.; and, NSPS Subpart JJJJ of 40 CFR 60.4245]

- Maintenance Records for Certified Engines.  To demonstrate conformance with the manufacturer’s written instructions for maintaining the certified engine and to document when compliance testing must be performed pursuant to Specific Condition 22, the owner or operator must keep the following records:

- Engine manufacturer documentation and certification indicating compliance with the standards.

- A copy of the manufacturer’s written instructions for operation and maintenance of the certified engine.

- A written maintenance log detailing the date and type of maintenance performed on the engine, as well as any deviations from the manufacturer’s written instructions.

[Rule 62-204.800(8)(b)81, F.A.C.; and, NSPS Subpart JJJJ of 40 CFR 60.4243]

- Maintenance Plan for Non-Certified Engines:  The permittee shall keep a maintenance plan and records of conducted maintenance and must, to the extent practicable, maintain and operate the engine in a manner consistent with good air pollution control practice for minimizing emissions.  
[Rule 62-204.800(8)(b)81 and 62-213.440(1), F.A.C.; and, NSPS Subpart JJJJ of 40 CFR 60.4243]

- Test Reports:  The required test report shall be filed with the Department, as soon as practical, but no later than 45 days after the last sampling run of each test is completed.  The test report shall provide sufficient detail on the emissions unit tested and the test procedures used to allow the Department to determine if the test was properly conducted.  In addition to the information identified in Rule 62-297.310(8)(c), F.A.C., the test report shall also indicate the engine power (HP) during the test and the cleaned digester BUS gas heating value.  [Rule 62-297.310(8), F.A.C.]

This section of the permit addresses the following emissions units.

| EU No. | Emission Unit Description |
| --- | --- |
| 005 | Flare #3, Thermal Oxidizer (140 scfm) |
| 006 | Odor Control Systems |
| 007 | Cooling Tower |

Equipment

- Thermal Oxidizer, Flare No. 3:  The permittee is authorized to install and operate a thermal oxidizer/flare when low‐pressure waste gas is generated by the BUS with the following specifications:

- Maximum design flow rate of 140 scfm for the thermal oxidizer.

- The combustion stack assembly is capable of using natural gas and BUS gas as the pilot gas.

- The thermal oxidizer is designed for an overall 99.9% destruction efficiency of methane.

[Design, Application No. 1030558-001-AC]

- Odor Control System:  The permittee is authorized to install and operate two odor control systems to control the ventilation exhaust from the two primary clarifiers, WAS holding tank, splitter box and gravity belt thickener hoods.  For high H2S concentration (> 50 ppm), each control system will consist of a biotrickling filter followed by a carbon scrubber.  The gravity room will be treated by the activated carbon units only.  Each system will include a 12,000 cubic feet per minute (cfm) fan that will be used to maintain the flow rate while maintaining a negative pressure in the tanks.  An additional fan and an activated carbon unit will be installed and available for backup.  The general design specifications for the odor control systems are:

- Biotrickling Filter Design:

- Gas velocity of 80 feet per minute (fpm);

- Flow rate of 9,000 cfm;

- 99% removal of H2S, typical; and

- 40 to 50% removal of organic odors.

- Activated Carbon System Design:

- Treats H2S and organic sulfides odors;

- Gas velocity of 53 fpm;

- Flow rate of 12,000 cfm;

- Influent H2S concentration – up to 5 ppm; and

- 99.9% removal of H2S.

An air flow measuring device shall be installed to monitor and maintain the air flow from each system.  H2S levels downstream of the biotrickling filter shall be monitored to ensure the biotrickling filter is operating sufficiently.

[Design, Application No. 1030558-001-AC]

- Cooling Tower:  The permittee is authorized to install and operate a cooling tower (Marley Model MHF7105QAEBN, or equivalent) used to facilitate requisite cooling of the mesophilic digesters and the digester gas prior to entering the BUS with the following nominal design specifications:  2-cells with cooling fans; an air exit temperature of 85°F; a circulating water flow rate of 650 gallons per minute; and a drift rate of no more than 0.005% of the recirculating water flow rate.  [Design, Application No. 1030558-001-AC]

Performance Restrictions

- Authorized Fuel:  Only digester gas shall be fired in the thermal oxidizer/flare.  
[Application No. 1050558-001-AC; and Rule 62-210.200(PTE), F.A.C.]

- Hours of Operation:  The hours of operation for EU 005 – EU 007 are not limited (8,760 hours/year).  
[Rules 62-4.070(3) and 62-210.200(PTE), F.A.C.]

##### Emissions Standards

- Visible Emissions:  Visible emissions from the thermal oxidizer/flare shall not exceed 5% opacity.  
[Rules 62-4.070(3) and 62-210.200(PTE), F.A.C.]

##### Testing Requirements

- Initial Compliance Tests:  The thermal oxidizer/flare shall be tested to demonstrate initial compliance with opacity.  The initial tests shall be conducted within 60 days after achieving permitted capacity, but not later than 180 days after initial operation of the unit.  [Rules 62-4.070(3) and 62-297.310(7)(a)1, F.A.C.]

- Annual Compliance Tests:  During each federal fiscal year (October 1st to September 30th), the thermal oxidizer/flare shall be tested to demonstrate compliance with opacity.  [Rule 62-297.310(7)(a)4, F.A.C.]

- Test Requirements:  The permittee shall notify the Compliance Authority in writing at least 15 days prior to any required tests.  Tests shall be conducted in accordance with the applicable requirements specified in Appendix D (Common Testing Requirements) of this permit.  [Rule 62-297.310(7)(a)9, F.A.C.]

- Test Methods:  Required tests shall be performed in accordance with the following reference methods.

| Method | Description of Method and Comments |
| --- | --- |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |

The above methods are described in Appendix A of 40 CFR 60 and are adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Rules 62-204.800 and 62-297.100, F.A.C.; and Appendix A of 40 CFR 60]

Monitoring Requirements

- Odor Control Systems Design:  Within 60 days of commencing operation of the odor control systems, the permittee shall submit to the compliance authority the final design specifications for the odor control system including the designed H2S control efficiency.  [Design; Application No. 1030558-001-AC; and Rule 62-4.070(3), F.A.C.]

- Cooling Tower Design Drift Rate:  The cooling tower shall be designed with a maximum droplet drift rate of no more than 0.005% of the recirculating water flow rate.  Within 60 days of commencing operation, the permittee shall submit to the compliance authority the final design specifications for the cooling tower including a maximum designed droplet drift rate of 0.005%.  [Design; Application No. 1030558-001-AC; and Rule 62-4.070(3), F.A.C.]

Records and Reports

- Test Reports:  The permittee shall prepare and submit reports for all required tests in accordance with the requirements specified in Appendix D (Common Testing Requirements) of this permit.  
[Rule 62-297.310(8), F.A.C.]

This section of the permit addresses the following emissions unit.

| EU No. | Emission Unit Description |
| --- | --- |
| 008 | Emergency Diesel Generator (2,682 HP) |

Equipment

- Emergency Diesel Generator:  The permittee is authorized to install and operate an emergency diesel engine (CAT 3516C) with a maximum engine rating of 2,682 HP at 100% load with a nominal power rating of 2,000 kilowatts (kW) manufactured August 31, 2010.

The following table provides important details for the engine regulated as EU 008:

| Engine Identification | Engine Brake HP | Date of Construction | Model Year | Displacement liters/cylinder (l/c) | Engine Manufacturer | Model No. |
| --- | --- | --- | --- | --- | --- | --- |
| Emergency Diesel Engine | 2,682 (2000 kW) | 2015 | 2010 | <10 | Caterpillar | 3516C |

{Permitting Note:  This compression ignition (CI) RICE is regulated under 40 CFR 63, Subpart ZZZZ, NESHAP for Stationary RICE and 40 CFR 60, Subpart IIII, NSPS for Stationary CI RICE, adopted in Rules 62.204.800(11)(b) & (8)(b), F.A.C., respectively.  This RICE is not used as a fire pump.  This permit section addresses engines that commence construction after July 11, 2005, that is located at an area source of HAP and that was manufactured after April 1, 2006.  In accordance with provisions of 40 CFR 63.6590(c)(6), meeting the requirements of 40 CFR 60, Subpart IIII, satisfies compliance with the requirements of Subpart ZZZZ.}

Applicable Requirements

- Applicable NSPS Provisions:  The is subject to, and shall comply with, the applicable provisions in NSPS Subpart A (General Provisions) and NSPS Subpart IIII (Standards of Performance for Stationary Compression Ignition Internal Combustion Engines) of 40 CFR 60, which are identified in Appendix E and F of this permit, respectively.  [Rule 62-204.800, F.A.C.; and, NSPS Subparts A and IIII in 40 CFR 60]

- Applicable NESHAP Provisions:  The natural gas and cleaned digester BUS gas fired engines are subject to, and shall comply with, the applicable provisions in NESHAP Subpart A (General Provisions) and NESHAP Subpart ZZZZ (Reciprocating Internal Combustion Engines) of 40 CFR 63, which are identified in Appendix H and I of this permit, respectively.  Pursuant to §63.6590 of this subpart, the requirements of NESHAP Subpart ZZZZ are met by complying with the requirements of NSPS Subpart IIII.  [Rule 62-204.800, F.A.C.; and, NESHAP Subparts A and ZZZZ of 40 CFR 63]

Essential PTE Parameters

- Authorized Fuel:  This Stationary RICE must use diesel fuel that meets the following requirements for non-road diesel fuel:

- Sulfur Content.  The sulfur content shall not exceed = 15 ppm = 0.0015% by weight (ultra-low sulfur) for non-road fuel.

- Cetane and Aromatic.  The fuel must have a minimum cetane index of 40 or must have a maximum aromatic content of 35 volume percent.

- Use of Existing Fuel.  Any existing diesel fuel purchased (or otherwise obtained) prior to October 1, 2010, may be used until depleted.

[Rule 62-204.800, F.A.C.; and, 40 CFR 60.4207(b), 80.510(c), 80.510(f)(2) and 80.510(f)(7)]

- Restricted Hours of Operation:

- Maintenance and Testing.  These engines are authorized to operate for the purpose of maintenance checks and readiness testing, provided that the tests are recommended by federal, state, or local government, the manufacturer, the vendor, or the insurance company associated with the engine.  Maintenance checks and readiness testing of such units is limited to 100 hours/year.

- Emergency Situations.  There is no time limit on the use of emergency stationary RICE in emergency situations.

- Non-emergency Situations.  These engines may operate up to 50 hours/year in non-emergency situations, but those 50 hours are counted towards the 100 hours/year provided for maintenance and testing.

- Other Situations.  These engines cannot be used for peak shaving or to generate income for a facility to supply power to an electric grid or otherwise supply non-emergency power as part of a financial arrangement with another entity.

[Rule 62-204.800(8)(b)80, F.A.C.; and, 40 CFR 60.4211(f)]

- Operation and Maintenance:  The owner or operator must operate and maintain the stationary CI internal combustion engines according to the manufacturer's written instructions or procedures developed by the owner or operator that are approved by the engine manufacturer.  In addition, owners and operators may only change those settings that are permitted by the manufacturer.  This RICE must be maintained and operated to meet the emissions limits in Specific Conditions 5 through 7 over the entire life of the engine.  
[Rule 62-204.800(8)(b)80, F.A.C.; and, 40 CFR 60.4206, 4211(a)(1), (2) & (3)]

Emissions Standards

- NOX + NMHC Emissions:  Emissions of NOX plus non-methane hydrocarbons (NMHC) shall not exceed 6.4 grams per kilowatt hour (g/kW-hour) (4.8 g/HP-hour).  [40 CFR 60.4205(b) and 89.112 (Table 1)]

- CO Emissions:  CO emissions shall not exceed 3.5 g/kW-hour (2.6 g/HP-hour).  [40 CFR 60.4205(b) and 89.112 (Table 1)]

- PM Emissions:  PM emissions shall not exceed 0.2 g/kW-hour (0.15 g/HP-hour).  [40 CFR 60.4205(b) and 89.112 (Table 1)]

Testing and Compliance Requirements

- Engine Certification Requirements:  The owner or operator must comply with the emissions standards specified above by having purchased an engine certified by the manufacturer to meet those limits.  The engine must have been installed and configured according to the manufacturer’s emission-related specifications, except as permitted in Specific Condition 9.  [Rule 62-204.800(8)(b)80, F.A.C.; and, 40 CFR 60.4211(b)]

- Compliance Requirements Due to Loss of Certification:  If you do not install, configure, operate, and maintain your engine and control device according to the manufacturer's emission-related written instructions, or you change emission-related settings in a way that is not permitted by the manufacturer, you must keep a maintenance plan and records of conducted maintenance and must, to the extent practicable, maintain and operate the engine in a manner consistent with good air pollution control practice for minimizing emissions.  In addition, you must conduct an initial performance test to demonstrate compliance with the applicable emission standards within 1-year of startup, or within 1-year after an engine and control device is no longer installed, configured, operated, and maintained in accordance with the manufacturer's emission-related written instructions, or within 1-year after you change emission-related settings in a way that is not permitted by the manufacturer.  You must conduct subsequent performance testing every 8,760 hours of engine operation or 3-years, whichever comes first, thereafter to demonstrate compliance with the applicable emission standards.  [Rule 62-204.800(8)(b)80, F.A.C.; and, 40 CFR 60.4211(g)(3)]

- Testing Requirements:  In the event performance tests are required pursuant to Specific Condition 9, the following requirements shall be met:

  - Testing Procedures.  The performance test must be conducted according to the in-use testing procedures in 40 CFR Part 1039, Subpart F.  Link to Subpart F

  - NTE Standards.  Exhaust emissions from this engine must not exceed the not-to-exceed (NTE) standards for the same model year and maximum engine power in 40 CFR Part 1039, Subpart B as required in 40 CFR 1039.101(e) and 40 CFR 1039.102(g)(1), except as specified in 40 CFR 1039.104(d).  This requirement starts when NTE requirements take effect for non-road diesel engines under 40 CFR Part 1039, Subpart B.  Link to Subpart B

[Rule 62-204.800(8)(b)80, F.A.C.; and, 40 CFR 60.4212(a) & (b)]

- Common Testing Requirements:  Unless otherwise specified and if required, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

Monitoring Requirements

- Hour Meter:  The owner or operator must install a non-resettable hour meter if one is not already installed.  [Rule 62-204.800(8)(b)80, F.A.C.; and, 40 CFR 60.4209(a)]

Records and Reports

- Hours of Operation Records:  The owner or operator must keep records of the operation of the engine in emergency and non-emergency services that are recorded through the non-resettable hour meter.  The owner or operator must record the time of operation of the engine and the reason the engine was in operation during that time.  [Rule 62-204.800(8)(b)80, F.A.C.; and, 40 CFR 60.4214(b)]

- Maintenance Records:  To demonstrate conformance with the manufacturer’s written instructions for maintaining the certified engine and to document when compliance testing must be performed pursuant to Specific Condition 9, the owner or operator must keep the following records:

  - Engine manufacturer documentation and certification indicating compliance with the standards.

  - A copy of the manufacturer’s written instructions for operation and maintenance of the certified engine.

  - A written maintenance log detailing the date and type of maintenance performed on the engine, as well as any deviations from the manufacturer’s written instructions.

[Rule 62-4.070(3), F.A.C., F.A.C.]

- Testing Notification:  At such time that the requirements of Specific Condition 9 become applicable, the owner or operator shall notify the compliance authority of the date by which the initial compliance test must be performed.  [Rule 62-4.070(3), F.A.C.]

This section of the permit addresses the following emissions unit.

| EU No. | Emission Unit Description |
| --- | --- |
| 009 | Emergency Diesel Generator (2,347 HP) |

Equipment

- Emergency Diesel Generator:  The permittee is authorized to install and operate an emergency diesel engine (CAT D3516) with a maximum engine rating of 2,682 HP at 100% load with a nominal power rating of 1,750 kW manufactured August 3, 1999.

The following table provides important details for the engine regulated as EU 009:

| Engine Identification | Engine Brake HP | Date of Construction | Model Year | Displacement liters/cylinder (l/c) | Engine Manufacturer | Model No. |
| --- | --- | --- | --- | --- | --- | --- |
| Emergency Diesel Engine | 2,347 (1,750 kW) | 2000 | 1999 | <10 | Caterpillar | D3516 |

{Permitting Note:  This CI RICE is regulated under 40 CFR 63, Subpart ZZZZ, NESHAP for Stationary RICE adopted in Rule 62.204.800(11)(b), F.A.C.  This RICE is not used for fire pumps.  This RICE is exempted from regulations under 40 CFR 60, Subpart IIII - New Source Performance for Stationary ICE based on the manufacturer date.  This is an “existing” stationary CI RICE with a site rating of more than 500 HP, with a displacement of less than 10 liters per cylinder that is located at an area source of HAP and has not been modified or reconstructed after 6/12/2006.}

Essential Potential to Emit (PTE) Parameters

- Hours of Operation:

  - Emergency Situations.  There is no time limit on the use of emergency stationary RICE in emergency situations.  [Rule 62-204.800(11)(b)82, F.A.C.; and 40 CFR 63.6640(f)(1)]

  - Other Situations.  You may operate your emergency stationary RICE for any combination of the purposes specified in paragraphs 2.b.(1) through (3) for a maximum of 100 hours per calendar year.  Any operation for non-emergency situations as allowed by paragraphs 2.c. of this section counts as part of the 100 hours per calendar year allowed by this paragraph 2.b.

- Maintenance and Testing.  Each RICE is authorized to operate for the purpose of maintenance checks and readiness testing, provided that the tests are recommended by federal, state or local government, the manufacturer, the vendor, or the insurance company associated with the engine.  Maintenance checks and readiness testing of such units is limited to 100 hours/year.  The owner or operator may petition the Administrator for approval of additional hours to be used for maintenance checks and readiness testing, but a petition is not required if the owner or operator maintains records indicating that Federal, State, or local standards require maintenance and testing of emergency RICE beyond 100 hours/year.  [Rule 62-204.800(11)(b)82, F.A.C.; and 40 CFR 63.6640(f)(2)(i)]

- Emergency Demand Response.  Each RICE may be operated for emergency demand response for periods in which the Reliability Coordinator under the North American Electric Reliability Corporation (NERC) Reliability Standard EOP-002-3, Capacity and Energy Emergencies (incorporated by reference, see 40 CFR 63.14), or other authorized entity as determined by the Reliability Coordinator, has declared an Energy Emergency Alert Level 2 as defined in the NERC Reliability Standard EOP-002-3.  [Rule 62-204.800(11)(b)82, F.A.C.; and 40 CFR 63.6640(f)(2)(ii)]

- Voltage or Frequency Deviations.  Emergency stationary RICE may be operated for periods where there is a deviation of voltage or frequency of 5% or greater below standard voltage or frequency.  [Rule 62-204.800(11)(b)82, F.A.C.; and 40 CFR 63.6640(f)(2)(iii)]

  - Non-emergency Situations.  These RICE may be operated for up to 50 hours per calendar year in nonemergency situations.  The 50 hours of operation in non-emergency situations are counted as part of the 100 hours per calendar year for maintenance and testing and emergency demand response provided in paragraph b., above.  The 50 hours/year for non-emergency situations cannot be used for peak shaving or non-emergency demand response, or to generate income for a facility to supply power to an electric grid or otherwise supply power as part of a financial arrangement with another entity.  
[Rule 62-204.800(11)(b)82, F.A.C.; and 40 CFR 63.6640(f)(3)]

- Work or Management Practice Standards:

  - Oil.  Change oil and filter every 500 hours of operation or annually, whichever comes first.  
[Rule 62-204.800(11)(b)82, F.A.C.; and 40 CFR 63.6603 & Table 2d.4.a.]

  - Air Cleaner.  Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first and replace as necessary.  [Rule 62-204.800(11)(b)82, F.A.C.; and 40 CFR 63.6603 & Table 2d.4.b.]

  - Hoses and Belts.  Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary.  [Rule 62-204.800(11)(b)82, F.A.C.; and 40 CFR 63.6603 & Table 25.4.c.]

  - Operation and Maintenance.  Operate and maintain the stationary RICE according to the manufacturer's emission-related operation and maintenance instructions or develop and follow your own maintenance plan which must provide, to the extent practicable for the maintenance and operation of the engine in a manner consistent with good air pollution, control practice for minimizing emissions.  
[Rule 62-204.800(11)(b)82, F.A.C.; and 40 CFR 63.6625(e), 63.6640(a) & Table 6.9.a.]

  - Engine Startup.  During periods of startup the owner or operator must minimize the engine's time spent at idle during startup and minimize the engine's startup time to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes.  [Rule 62-204.800(11)(b)82, F.A.C.; and 40 CFR 63.6625(h)]

  - Oil Analysis.  The owner or operator has the option of using an oil analysis program to extend the oil change requirement.  The oil analysis must be performed at the same frequency specified for changing the oil in paragraph a., above.  The analysis program must at a minimum analyze the following three parameters:  Total Base Number, viscosity, and percent water content.  The condemning limits for these parameters are as follows:  Total Base Number is less than 30% of the Total Base Number of the oil when new; viscosity of the oil has changed by more than 20% from the viscosity of the oil when new; or percent water content (by volume) is greater than 0.5.  If all of these condemning limits are not exceeded, the engine owner or operator is not required to change the oil.  If any of the limits are exceeded, the engine owner or operator must change the oil within 2 days of receiving the results of the analysis; if the engine is not in operation when the results of the analysis are received, the engine owner or operator must change the oil within 2 days or before commencing operation, whichever is later.  The owner or operator must keep records of the parameters that are analyzed as part of the program, the results of the analysis, and the oil changes for the engine.  The analysis program must be part of the maintenance plan for the engine.  [Rule 62-204.800(11)(b)82, F.A.C.; and 40 CFR 63.6625(i)]

Monitoring of Operations

- Hour Meter:  The owner or operator must install a non-resettable hour meter if one is not already installed.  [Rule 62-204.800(11)(b)82, F.A.C.; and 40 CFR 63.6625(f)]

Compliance

- Continuous Compliance:  Each unit shall be in compliance with the emission limitations and operating standards in this section at all times.  [Rule 62-204.800(11)(b)82, F.A.C.; and 40 CFR 63.6605(a)]

- Operation and Maintenance of Equipment:  At all times the owner or operator must operate and maintain, any affected source, including associated air pollution control equipment and monitoring equipment, in a manner consistent with safety and good air pollution control practices for minimizing emissions.  Determination of whether such operation and maintenance procedures are being used will be based on information available to the compliance authority which may include, but is not limited to, monitoring results, review of operation and maintenance procedures, review of operation and maintenance records, and inspection of the source.  [Rule 62-204.800(11)(b)82, F.A.C.; and 40 CFR 63.6605(b)]

Recordkeeping Requirements

- Notification, Performance and Compliance Records:  The owner or operator must keep:

  - A copy of each notification and report that the owner or operator submitted to comply with this section, including all documentation supporting any Initial Notification or Notification of Compliance Status that the owner or operator submitted.

  - Records of the occurrence and duration of each malfunction of operation.

  - Records of all required maintenance performed on the hour meter.

  - Records of actions taken during periods of malfunction to minimize emissions in accordance with Specific Condition 6, including corrective actions to restore malfunctioning process and monitoring equipment to its normal or usual manner of operation.

  - Records of the actions required in Specific Condition 3.d to show continuous compliance with each emission limitation or operating requirement.

  - Records of the Work or Management Practice Standards specified in Specific Condition 3.

  - Records of the maintenance conducted in order to demonstrate that the RICE was operated and maintained according to your own maintenance plan.

  - Records of the hours of operation of the engine that is recorded through the non-resettable hour meter.  The owner or operator must document how many hours are spent for emergency operation including what classified the operation as emergency and how many hours are spent for non-emergency operation.  If the engines are used for emergency demand response operation or for periods of voltage or frequency deviations, the owner or operator must keep records of the notification of the emergency situation, and the time of engine operation for these purposes.

[Rule 62-204.800(11)(b)82, F.A.C.; and 40 CFR 63.6655]

- Record Retention:

  - The owner or operator must keep records in a suitable and readily available form for expeditious reviews.

  - The owner or operator must keep each record readily accessible in hard copy or electronic form for at least 5 years after the date of each occurrence, measurement, maintenance, corrective action, report, or record.

[Rule 62-204.800(11), F.A.C.; and 40 CFR 63.6660 and 40 CFR 63.10(b)(1)]

Reporting Requirements

- Delay of Performing Work Practice Requirements:  If an emergency engine is operating during an emergency and it is not possible to shut down the engine in order to perform the work practice requirements on the schedule required in Specific Condition 2, or if performing the work practice on the required schedule would otherwise pose an unacceptable risk under federal, state, or local law, the work practice can be delayed until the emergency is over or the unacceptable risk under federal, state, or local law has abated.  The work practice should be performed as soon as practicable after the emergency has ended or the unacceptable risk under federal, state, or local law has abated.  Sources must report any failure to perform the work practice on the schedule required and the federal, state or local law under which the risk was deemed unacceptable.  
[Rule 62-204.800(11)(b)82, F.A.C.; and 40 CFR 63, Subpart ZZZZ, Table 2d, footnote 2]