TECHNICAL EVALUATION

&

PRELIMINARY DETERMINATION

APPLICANT

City of St. Petersburg

3800 54th Avenue South

St. Petersburg, Florida  33711

St. Petersburg Southwest Water Resource Facility

Facility ID No. 1030558

PROJECT

Project No. 1030558-001-AC

Application for Minor Source Air Construction Permit

Biosolids Improvement Project

COUNTY

Pinellas County, Florida

PERMITTING AUTHORITY

Florida Department of Environmental Protection

Division of Air Resource Management

Office of Permitting and Compliance

2600 Blairstone Road, MS#5505

Tallahassee, Florida  32399-2400

December 30, 2014

- General Project INFORMATION

                - Air Pollution Regulations

Projects at stationary sources with the potential to emit (PTE) air pollution are subject to the applicable environmental laws specified in Section 403 of the Florida Statutes (F.S.).  The statutes authorize the Department of Environmental Protection (Department) to establish regulations regarding air quality as part of the Florida Administrative Code (F.A.C.), which includes the following applicable chapters:  62-4 (Permits); 62-204 (Air Pollution Control – General Provisions); 62-210 (Stationary Sources – General Requirements); 62-212 (Stationary Sources – Preconstruction Review); 62-213 (Operation Permits for Major Sources of Air Pollution); 62-296 (Stationary Sources - Emission Standards); and 62-297 (Stationary Sources – Emissions Monitoring).  Specifically, air construction permits are required pursuant to Chapters 62-4, 62-210 and 62-212, F.A.C.

In addition, the U. S. Environmental Protection Agency (EPA) establishes air quality regulations in Title 40 of the Code of Federal Regulations (CFR).  Part 60 specifies New Source Performance Standards (NSPS) for numerous industrial categories.  Part 61 specifies National Emission Standards for Hazardous Air Pollutants (NESHAP) based on specific pollutants.  Part 63 specifies NESHAP based on the Maximum Achievable Control Technology (MACT) for numerous industrial categories.  The Department adopts these federal regulations in Rule 62-204.800, F.A.C.

                - Glossary of Common Terms

Because of the technical nature of the project, the permit contains numerous acronyms and abbreviations, which are defined in Appendix A of this permit.

                - Facility Description and Location

City of St Petersburg Southwest Water Resource Facility (SWWRF) is an existing domestic wastewater treatment plant, which is categorized under Standard Industrial Classification Code No. 4952.  The existing facility is a 20 million gallon per day (MGD) annual average daily flow, Type I complete mix activated sludge domestic wastewater treatment plant.  The plant is a dual train facility with wastewater entering the plant by both force main and gravity lines.  The force main influent flows directly to the head-works structure while the gravity line flows first to the 40 MGD influent pump station, the head-works has two mechanically cleaned fine bar screens and a manually cleaned by-pass bar screen prior to grit removal, one influent pump station with four 10 MGD submersible pumps, two rectangular aeration basins, equipped with fine bubble diffusers, with a total volume of 4.03 million gallons, three clarifiers providing a total capacity of 3.85 million gallons with a total surface area of 42,942 square feet; a transfer pumping station; four manually backwashed deep bed dual media filters providing a total surface area of 5,624 square feet; and a dual channel chlorine contact chamber of 474,591 gallons, using a liquid sodium hypochlorite system.

The biosolids treatment system consists of: one gravity belt thickener; two anaerobic digesters with a total volume of 2.6 million gallons operated in series; and two belt filter presses. Filtrate from the process is returned to the head-works of the treatment plant.  After dewatering by the filter press, biosolid stabilization by the Bioset process to a Class AA is completed.  Lime and acid are added to the solids and pumped through a plug flow reactor and allowed to rise in temperature and pH, to release ammonia. The Class AA material is then transported off-site for land application or commercial sales.

Reclaimed water storage is provided in one 5.0 million gallon ground storage tank and in one 10.0 million gallon ground storage tank.  Reclaimed water will be directed to the St. Petersburg Master Reuse System.  Reclaimed water can also be routed to the ASR well and to the injection well system if necessary.  Reject water is stored in a 15.0 million gallon ground storage tank.  Reject water may be directed to the 5.0 million gallon and 10.0 million gallon ground storage tanks in an emergency.  After normal plant operations resumes, reject water is directed to the filters for re-treatment.

Backup power is provided by four, on-site standby diesel powered generators.

The existing Southwest Water Resource Facility is located in Pinellas County at 3800 54th Avenue South in St. Petersburg, Florida.  The UTM coordinates of the existing facility are Zone 17, 333.8 kilometers (km) East, and 3067.2 km North.  The location of the facility is shown in Figure 1 while an aerial view of the facility is shown in Figure 2.

Figure 1.  Location of St. Petersburg SWWRF.	Figure 2. Aerial View of St. Petersburg SWWRF.

This site is in an area that is in attainment (or designated as unclassifiable) for all air pollutants subject to Ambient Air Quality Standards (AAQS).

                - Facility Regulatory Categories

- The facility is not a major source of hazardous air pollutants (HAP).

- The facility does not operate units subject to the acid rain provisions of the Clean Air Act.

- The facility is not a Title V major source of air pollution in accordance with Chapter 62-213, F.A.C.

- The facility is not a major stationary source in accordance with Rule 62-212.400, F.A.C. for the Prevention of Significant Deterioration (PSD) of Air Quality.

- The facility does operate units subject to the NSPS of 40 CFR 60.

- The facility does operate units subject to the NESHAP of 40 CFR 63.

                - Project Description

On May 9, 2014, the Department received an application from the City of St. Petersburg (City) to construct and operate a biosolids-to-energy plant at their existing SWWRF.  The facility will consolidate the City’s biosolids operations for all their treatment plants at SWWRF to capture the digester gas and clean it to natural gas standards to fuel for the City’s sanitation vehicles, boilers and for electrical energy production.  The City operates four water reclamation facilities (SWWRF, Northeast WRF, Albert Whitted WRF, and Northwest WRF).  The biosolids improvement project is comprised of:

- Biosolids-to-Energy Project:  Upgrading and installing new clarification systems, new anaerobic digesters and improvements to an existing digester; new sludge handling equipment; new digester gas handling facilities; a new biosolids upgrade systems (BUS); and new odor control facilities.  Emission sources associated with this project includes: four flares; and two carbon scrubbers to control odor emissions from the primary clarifiers, the sludge storage tank, and the thickening facilities.

- Biosolids Dewatering Project:  Expanding the sludge thickening process and upgrading of the sludge dewatering system.  Emission sources associated with this project includes: a cooling tower; two 6.38 million British thermal units per hour (MMBtu/hour) boilers firing natural gas and cleaned digester gas; and a carbon scrubber to control odor emissions from the sludge dewatering and truck loading areas.

- Generator and Electrical Improvements Project:  Construct a new combined heat and power facility coupled with an expanded emergency backup power system.  Emission sources associated with this project includes: two 1.1 megawatt (MW) reciprocating internal combustion engine/electrical generator sets firing natural gas and cleaned digester gas; and two diesel fired emergency generators (2,347 horse power (HP) and 2,682 HP).

Liquid wastewater will undergo a pre-treatment process to remove contaminants and moisture.  Waste activated sludge is sent through a sludge thickening process where fats, oils and grease is added prior to entering three continuously stirred tank reactor digesters.  The digesters will break down the organics and convert them primarily into methane (CH4) and carbon dioxide (CO2).  Two flares will be used to combust excess gas from the digesters.  After the digestion process, moisture is removed prior to the digester gas passing through the BUS.  The BUS is designed to process raw digester gas to pipeline natural gas quality.  A thermal oxidizer will be used to combust waste gas from the BUS and a candlestick flare will be used to combust BUS product gas during startup.  The product gas will either be sent to the onsite engine-generators or sent to the compressed natural gas (CNG) fueling system for further compression.  The final compression and CNG fueling system compresses the BUS product gas to high pressure for tube-trailer fueling or onsite high pressure storage.  The two boilers used to heat water for use in the facility will fire BUS product gas and natural gas.

Construction is scheduled to commence in 2014 and be completed in 2018.  The two 1.1 MW reciprocating internal combustion engine/electrical generator sets will be installed and operating for a period of 2 or 3 years prior to the cleaned digester gas (BUS product gas) being available for the engines.  During this period, the engines/generators will fire exclusively on pipeline natural gas.

- This project consists of the emissions units (EU) given in Table 1.

Table 1 – list of emission units.

| EU No. | Description |
| --- | --- |
| 001 & 002 | Two nominal 1.1 MW Spark Ignition RICE/generator sets (1,517 HP, each) |
| 003 & 004 | Two Boilers (6.38 MMBtu/hour, each) |
| 005 | Flare #3, Thermal Oxidizer (140 scfm) |
| 006 | Odor Control Systems |
| 007 | Cooling Tower |
| 008 | Diesel Fired Emergency Generator (2,347 HP) |
| 009 | Diesel Fired Emergency Generator (2,682 HP) |

                - Processing Schedule

- 05/09/2014	Received the application for a minor source air pollution construction permit.

- 06/05/2014	Requested additional information.

- 08/22/2014	Received additional information; application incomplete.

- 09/10/2014	Requested additional information.

- 10/17/2014	Received additional information; application complete.

- PSD Applicability

- General PSD Applicability

The Department regulates major stationary sources in accordance with Florida’s PSD program pursuant to Rule 62-212.400, F.A.C.  PSD preconstruction review is required in areas that are currently in attainment with the state and federal Ambient Air Quality Standards (AAQS) or areas designated as “unclassifiable” for these regulated pollutants.  Commonly addressed PSD pollutants for IC engines firing digester gas include: carbon monoxide (CO); nitrogen oxide (NOX); sulfur dioxide (SO2); particulate matter (PM); PM smaller than 10 micrometers (PM10); PM2.5; VOC; and hydrogen sulfide (H2S);

Additional PSD pollutants that are more common to certain other industries include:  lead (Pb); mercury (Hg); fluorides (F); sulfuric acid mist (SAM); total reduced sulfur (TRS), including H2S; reduced sulfur compounds, including H2S; municipal waste combustor (MWC) organics measured as total tetra- through octa-chlorinated dibenzo-p-dioxins and dibenzofurans; MWC metals measured as PM; and MWC acid gases measured as SO2; hydrogen chloride (HCl); and municipal solid waste (MSW) landfills emissions measured as non-methane organic compounds (NMOC).

As defined in Rule 62-210.200(174), F.A.C., a stationary source is a “major stationary source” (major PSD source) if it emits or has the potential to emit (PTE):

- 250 tons per year (TPY) or more of any PSD pollutant; or

- 100 TPY or more of any PSD pollutant and the facility belongs to one of the 28 listed PSD major facility categories.

- For the special case of greenhouse gases (GHGs), the facility must first be shown to emit or have a PTE of 100,000 tons/year of GHGs as carbon dioxide equivalent (CO2e) to (possibly) be subject to regulation.

The list given in the citation does not include the category of “wastewater treatment plants” or “digester gas-fired electric plants.”  Therefore, the City of St. Petersburg Southwest WRF major stationary source threshold is 250 TPY or more of any PSD pollutant.  The proposed biosolids improvement project is a minor stationary source based on the potential to emit less than 250 TPY or more of any PSD pollutant.

If emissions of GHGs expressed as CO2e emissions are greater than 100,000 tons/year, then the total (unweighted) GHGs mass emissions are compared with the 100 and 250 tons/year thresholds to determine whether the source is a major stationary source.

# For major stationary sources, PSD applicability is based on emissions thresholds known as the significant emission rates (SER) as defined in Rule 62-210.200 (Definitions), F.A.C.  For each PSD pollutant that exceeds the corresponding SER, BACT must be employed to control emissions and an air quality impact analysis must be conducted if the PSD pollutant has a defined AAQS.  SER also means any emissions rate or any net emissions increase of a PSD pollutant associated with a major stationary source or major modification which would construct within 10 km of a Class I area and have an impact on such area equal to or greater than 1 gram per cubic meter (g/cm3), 24-hour average.

# Although a facility may be “major” (i.e. emits or has the PTE 100 or 250 TPY as applicable) for only one PSD pollutant, a project must include BACT controls for any PSD pollutant that exceeds the corresponding SER given in Table 2 below.

Table 2 - List of SER by PSD-Pollutant. 1

| Pollutant | SER (tons/year) | Pollutant | SER (tons/year) 4 |
| --- | --- | --- | --- |
| CO | 100 | NOX | 40 |
| PM/PM10/PM2.5 | 25/15/10 | Ozone (VOC) 2 | 40 |
| PM2.5 (NOX) | 40 | PM2.5 (SO2) | 40 |
| Ozone (NOX) 2 | 40 | SAM | 7 |
| SO2 | 40 | Pb | 0.6 |
| Hg | 0.1 | GHGs | > 75,000 (CO2e) and > 0 (mass) 3 |
| - Excluding fluoride and pollutants specific to the Pulp and Paper industry, MWCs, MSW landfills. - Ozone (O3) is regulated by its precursors (VOC and NOX). PSD for PM2.5 can be triggered by its precursors (NOX and SO2). - Pursuant to 40 CFR 52.21(b)(23)(ii), pollutants with no SER listed at 40 CFR 52.21(b)(23)(i) have a SER of zero (0) tons/year. - SER also means any emissions rate or any net emissions increase associated with a major stationary source or major modification which would construct within 10 km of a Class I area and have an impact on such area equal to or greater than 1 μg/m3, 24-hour average. |  |  |  |

- PSD Applicability for Project

The project will be located in Pinellas County, which is in an area that is currently in attainment with the AAQS or otherwise designated as unclassifiable.  Table 3 summarizes the annual emissions from the project as defined in the application.  The table compares these emissions to the PSD significant emission rates.

Table 3 - Summary of the Applicant’s PSD Applicability Analysis.

| Pollutant | Annual Emissions, Tons/Year |  | Subject to PSD? |
| --- | --- | --- | --- |
|  | Potential Emissions | Significant Emissions Rate |  |
| NOX | 38.6 | 250 | No |
| CO | 66.7 | 250 | No |
| PM | 1.4 | 250 | No |
| PM10 | 2.6 | 250 | No |
| PM2.5 | 2.5 | 250 | No |
| SO2 | 40.0 | 250 | No |
| VOC | 22 | 250 | No |
| H2S | 1.5 | 250 | No |
| GHG (CO2e) | 21,899 | 100,000 | No |
| - The potential emissions are based on the worst-case scenario operating the engines, boiler, flares, scrubbers, and cooling tower 8,760 hours/year. - The applicant estimated potential NOX, CO and VOC annual emissions for the engines based on firing natural gas in New Source Performance Standard in Subpart JJJJ of 40 CFR 60. The applicant contends that the cleaned digester BUS gas will be cleaned to meet the natural gas standards. |  |  |  |

As shown in the Table 3, total project emissions will not exceed the PSD significant emissions rates; therefore, the project is not subject to PSD preconstruction review.

- Departments project review

Figure 3 shows a biosolids improvements project process flow diagram.

Figure 3.  Biosolids Improvements Project Process Flow Diagram.

The Biosolids Improvement Project is comprised of a Biosolids-to-Energy Project, a Biosolids Dewatering Project and a Generator and Electrical Improvements Project.  Emission sources associated with this project include two 1.1 MW Cummins Model C1100 N6C RICE/electrical generator sets, two open “candlestick-type” flares (200 standard cubic feet per minute (scfm) and 600 scfm), an enclosed flare (760 scfm), flare - thermal oxidizer (140 scfm), two 6.38 MMBtu/hour boilers, cooling tower, two emergency generators, and three odor control system (carbon scrubbers) to control potential odor causing pollutants.

- Process Description

- Biosolids Process

Raw sewage enters the treatment plant at the headworks where large inorganics are removed such as sticks, stones, grit and sand from the wastewater stream.  An existing odor control system (i.e. carbon scrubber) is used to control odor from the headwork’s process.  Liquid wastewater is then pumped to the primary clarifier to further remove solids that passed through the headworks and grit equipment before it enters the aeration basins.  The wastewater then undergoes biological treatment in the aeration basins.  Air is injected into the wastewater to promote the growth of microorganisms that feed on organic materials in the sewage.  Wastewater is pumped into the secondary clarifier to separate the water from the solids.  The suspended heavier materials settle to the bottom of the clarifiers as a thin mud (sludge).  Waste activated sludge (WAS) is sent through a sludge thickening process where fats, oils and grease is added prior to entering three continuously stirred digesters.  The digester tanks will maximize organics destruction and biogas/methane generation while minimizing digestion volume and residual digestate production requiring dewatering and disposal.  The digesters will break down the organics and convert them primarily into methane (CH4) and carbon dioxide (CO2).  As shown in Figure 4 below, the anaerobic digesters allow the organic matter to decompose in a contained environment to create a digester gas with a methane content of approximately 57%.

| - Organic Matter - “Waste” |  | - Acid Forming Bacteria |  | - Organic Acids - (Acetic Acid) - CH3COOH |  | - Methane Forming Bacteria |
| --- | --- | --- | --- | --- | --- | --- |
| - CH4 + CO2 + Heat + Water |  |  |  |  |  |  |
| - 57% 43% |  |  |  |  |  |  |

Figure 4.  Anaerobic Decomposition Process.

Fare Nos. 1 and 2 will be used to combust excess gas from the digesters.  A new odor control system will be used to treat foul air generated by the primary clarifiers, sludge storage tank, and thickening facilities.

Upgrades to the biosolids processing facility will include a new and upgraded clarification systems, new anaerobic digesters and improvements to an existing digester, new sludge handling equipment, new digester gas handling facilities, new digester gas upgrade systems, and new odor control facilities.

- Digester Gas Pretreatment

The gas cleaning process begins with raw digester gas being saturated with liquid water emanating from an upstream condensing process.  Water accounts for 8.5% of the digester gas mass flow at the characteristic temperatures of the digester gas.  Prior to entering the BUS, moisture is removed from the digester gas utilizing an in-line type gas separator with filter elements and a mist eliminator.  The gas will be cooled to a temperature of about 40 degrees Fahrenheit (°F) (via a process utilizing, in part, cooling water from the cooling tower) and the water will be separated out.  Water removal is required for the BUS which requires a maximum dew point of 100°F.  The gas separator will be specified to require the removal of moisture and 98% of all solid particles five microns and larger.  Once moisture is removed, the dehydrated gas is precooled in order to promote energy efficiency in the downstream compression process.

- Biogas Upgrade System Process

Following the precooling process, the gas will enter the BUS where other unwanted constituents will be removed. The BUS system will be manufactured by Guild Associates, Inc. and will utilize a Vacuum Pressure Swing Adsorption (PSA) process.  The BUS consists of the following five basic unit operations:

- Feed Gas Compression System.  The feed gas compression skid includes an inlet separator, compressor, oil separator, post-compression cooler, condensate separator, and gas re-heat heat exchanger.  This operation compresses the gas to a pressure of approximately 100 pounds per square inch (psi).  The compressed gas is fed into one of three PSA vessels.

- PSA System.  A PSA skid includes an inlet separator, three PSA vessels, and pneumatically actuated valves for PSA vessel process cycling.  The three pressure vessels are filled with a solid adsorbent (Molecular Gate).  Under high pressure, the unwanted gases tend to be attracted to solid surfaces, or “adsorbed”.  The solid adsorbent material restricts the adsorption of relatively large methane molecules while allowing the adsorption of unwanted smaller constituents.  The gas cleaning operation is rotated between the three PSA vessels.  Following the PSA vessels, the product gas is conveyed to a gas chromatograph analyzer to ensure that it meets quality specifications and then to final compression prior to being fired in the generators, boilers and vehicles.

- Vacuum Pump.  A vacuum pump is used to depressurize the PSA vessel to release and collect unwanted waste gases (CO2, H2S, siloxanes, nitrogen (N), ammonia, VOC, and water vapor) from the adsorbent.  The methane content is approximately 15% to support combustion in the thermal oxidizer (Flare 3). This waste gas is conveyed to Flare 3 where it is oxidized.

- Thermal Oxidizer.  Flare 3 is an assisted combustion device designed for low-Btu (low methane content) waste gas.

- Buffer Vessels.  As part of the PSA system, buffer vessels with pneumatically actuated valves are used to smooth out pressures and flows during the cyclical process.

The BUS cleans the gas to the specification listed in Table 4.  The BUS is designed to remove 99% of H2S and 99% or more of siloxanes and VOC relative to the raw digester gas.

Table 4 - Comparison of Raw Digester Gas, BUS Product Gas and Natural Gas Standards.

| Digester Gas Characteristics | Units | Approximate Value or Range |  |  |
| --- | --- | --- | --- | --- |
|  |  | Raw Digester Gas2 | BUS Product | Natural Gas |
| Higher Heating Value | Btu/scf, min | 600 - 700 | 990 | 1020 |
| Methane | % by volume, dry | 60 - 65 | 98 | 96 |
| CO2 | % by volume, dry | 35 – 40 | 2 | 1 |
| N | % by volume, dry | 0 – 0.5 | --- | --- |
| O2 | % by volume, max | --- | 0.1 | --- |
| O2 | ppmv | 0 - 50 | --- | --- |
| CO2, N and O2, Total | % by volume, max | --- | 2 | --- |
| CO2 and N, Total | % by volume, max | --- | --- | 3 |
| H2S | ppmv, max | 100 – 3,000 | 1 | 4 |
| Siloxanes | ppbv, max | 0 - 5 | Non-Detectable | --- |
| Ammonia | ppbv, max | 0 - 100 | Non-Detectable | --- |
| VOC | ppbv, max | 0 - 100 | Non-Detectable | --- |
| - Part per million by volume (ppmv); parts per billion by volume (ppbv); minimum (min); and maximum (max). - Typically, concentrations of HCl, formaldehyde, metals, chlorine, and fluorine in raw digester gas are either at non-detect levels or nil. Additionally, sulfur compounds, aside from H2S, are typically insignificant. |  |  |  |  |

As shown in Table 4, the minimum amount of methane found in the BUS product gas is 2% percent higher than in the natural gas quality standards and 28% higher than the raw digester gas.  The maximum H2S content is 3 ppmv lower in the BUS product gas than the natural gas and 2,999 ppmv lower than raw digester gas.  Additionally, the minimum heat content for the BUS product gas is within 1% of the natural gas, whereas, the raw digester gas is within 40% of the natural gas standard.

Pipeline natural gas is defined as … pipeline natural gas must either be composed of at least 70% methane by volume or have a gross calorific value between 950 and 1100 Btu/scf.

As can be seen in Table 4, the BUS product gas meets the definition of pipeline natural gas as defined by the EPA.  The BUS product gas will be used to fuel the City’s vehicles and combusted (along with utility natural gas) in the spark ignition engines, the heating water system boilers, and occasionally in the BUS start-up flare (Flare 4).

- Project Emission Sources

- Engines/Generator Sets

- The cleaned digester gas (BUS product gas) and natural gas combusted in the two identical Cummins Model C1100 N6C engine/generator sets (or equivalent) for the production of electricity for the plant and to supplement emergency backup power.  The engine/generators will have the following specifications:

- Each engine will be fired with pipeline natural gas and cleaned digester BUS gas generated at SWWRF.

- Each engine will fire a maximum of approximately 156.7 scfm of pipeline natural gas and 161.7 scfm of cleaned digester BUS gas.

- Each engine will have a maximum engine rating of 1,517 HP at 100% load with a nominal power rating of 1,100 kilowatts (kW).

- Each engine will be connected to an electrical generator rated at 1.1 MW, nominal.

- Each engine will have a maximum heat input rate of 9.6 MMBtu/hour.

- With both engines operating, the proposed biosolids-to-energy plant will have a total electrical generating capacity of 2.2 MW, nominal.  Emissions produced by the combustion of natural gas and cleaned digester BUS gas in each engine will be exhausted to ambient air through individual stacks connected to the engine exhaust manifolds.  Each engine exhaust stack is 1.33 feet in diameter and 25 feet in height with a volumetric flow rate of 6,650 actual cubic feet per minute (acfm).

- NSPS Provisions for the Engines

The cleaned digester BUS gas/natural gas fired engines and generator sets are subject to applicable NSPS provisions in 40 CFR 60 for Subpart A (General Provisions) and Subpart JJJJ (Standards of Performance for Stationary Spark Ignition Internal Combustion Engines).  These regulations establish operating limitations and emissions standards for CO, NOX and VOC (see Table 5).

Table 5- Subpart JJJJJ and Cummins C1100 N6C Emission Standards and Proposed Emission Limits

| Pollutant | Subpart JJJJ Standards | Cummins C1100 N6C Standard | Proposed Emission Limits |
| --- | --- | --- | --- |
| CO | 2.0 g/bhp-hour | 1.6 g/bhp-hour | 2.0 g/bhp-hour |
| NOX | 1.0 g/bhp-hour | 1.0 g/bhp-hour | 1.0 g/bhp-hour |
| VOC | 0.7 g/bhp-hour | 0.5 g/bhp-hour | 0.7 g/bhp-hour |

Technical data sheets (Cummins Model C1100 N6C) show that the engines will meet the emission limits established in NSPS Subpart JJJJ shown below in Table 4 for spark-ignited engines when firing natural gas with a capacity of more than 500 HP.  The applicants contends that the clean digester BUS gas will meet the characteristics of pipeline natural gas standards and requests emissions limits for these engines to be established for natural gas fired engines for either fuels fired in the engines.  However, the applicant has not provided the manufacturer’s guarantee that the natural gas emission factors are representative when firing cleaned digester BUS gas and that these engines will not lose their natural gas certification when firing cleaned digester BUS gas.  As requested by the applicant, if the engine/generator sets certifications are lost due to the firing of cleaned digester gas, these engines must be tested to demonstrate compliance with the natural gas emissions standards.

- NESHAP Provisions for the Engines

The engines/generator sets are subject to applicable NESHAP provisions in 40 CFR 63 for Subpart A (General Provisions) and Subpart ZZZZ (Reciprocating Internal Combustion Engines).  Hazardous air pollutants as specified in Rule 62-210.200(155), F.A.C are produced during the combustion of natural gas and digester gas used as fuel by the internal combustion engines since HAP compounds are present in the gas and when the fuel combustion process is not 100% complete and a small portion of the HAPs pass through the fuel combustion system.  In addition, when the gas is combusted, methane compounds present in gas can form formaldehyde (CH2O), which is a regulated HAP.

The engine technical data sheet provided by Cummins was used to estimate the total potential HAP content of the natural gas and cleaned digester gas that will be fired in the engines.  The applicant estimated total annual HAP emissions (engines only) to be 6.07 tons/year, which is below the 10 tons/year threshold to be considered a major source of HAP.  Pursuant to §63.6590 of this subpart, NESHAP Subpart ZZZZ are met by complying with the requirements of NSPS Subpart JJJJ.

- Heating Water System Boilers.

A primary heating water system will provide heated water throughout the process.  Primary heating water pumps will circulate heating water through the natural gas and cleaned digester BUS gas fueled engine generator heat recovery system to two heating water boilers, which will provide supplemental heating.  The heating water will be fed to the new digester facility being designed and constructed as part of this project.  The two heating water boilers will have a maximum 6.38 MMBtu/hour each.

- NSPS Provisions for the Boilers

NSPS Subpart Dc (Small Industrial‐Commercial‐Institutional Steam Generating Units) of 40 CFR 60 apply to units that have a maximum design heat input of less than 100 MMBtu/hour, and greater than 10 MMBtu/hour. The primary heating water system boilers have a maximum heat input of 6.38 MMBtu/hour each. Therefore, the requirements of Subpart Dc do not apply to the boilers.

- NESHAP Provisions for the Boilers

NESHAP Subpart JJJJJJ, (Industrial, Commercial, and Institutional Boilers Area Sources) of 40 CFR 63 exempts gas fired boilers.  As defined in 40 CFR 63.11237, a gas‐fired boiler includes any boiler that burns gaseous fuels not combined with any solid fuels and burns liquid fuel only during periods of gas curtailment, gas supply interruption, startups, or periodic testing on liquid fuel.

- State Rule Provisions for the Boilers

The City requested an exemption pursuant to Rule 62-210.300(3)(a)(34)(f), F.A.C.

If burning more than one (1) type of fuel, the equivalent annual amount of each fuel burned by the unit shall not exceed the maximum annual amount of such fuel, shall not exceed 150 million scf of natural gas, one million gallons of propane, one million gallons of fuel oil with a sulfur content not exceeding 0.05%, by weight, 290,000 gallons of fuel oil with a sulfur content not exceeding 0.5%, by weight, or 145,000 gallons of fuel oil with a sulfur content not exceeding 1%, by weight., multiplied by a fuel percentage. The fuel percentage is the percentage ratio of the total annual amount of the fuel burned by the unit to the total annual amount of such fuel allowed to be burned by the unit. The sum of the fuel percentages for all fuels burned by the unit must be less than or equal to 100%.

This exemption does not include the firing of digester gas in the boilers; therefore, this exemption does not apply to the boilers.

Rule 62-296.406, F.A.C. (Fossil Fuel Steam Generators with Less Than 250 MMBtu/hour Heat Input, New and Existing Emissions Units) applies to the boilers, which requires a visible emissions test and particulate matter PM and SO2 BACT.  Specifically, visible emissions from the each boiler shall not exceed 20% opacity except for one 6-minute period per 1-hour period during which opacity shall not exceed 27% and emissions of PM and SO2 from the boilers shall be minimized by firing natural gas and cleaned digester BUS gas meeting the characteristics of pipeline quality natural gas, or equivalent there to.  The emissions of particulate matter (PM) from the each boiler shall be demonstrated by the visible emissions limitation, which serves as an indicator of good combustion.

- Flares 1 through 4.

Temperature‐Controlled Enclosed Biogas Flare (Flare 1).

Flare 1 will operate when digester gas is generated by the SWWRF new anaerobic digesters (Digester Nos. 1 and 2) or during emergency situations.  The digester gas will contain particulate materials and greasy oils.  The applicant proposes to install and operate the enclosed flare with the following specifications:

- Maximum design flow rate of 760 scfm enclosed ground flare with automatic ignition and designed to burn low pressure digester gas.

- Digester gas temperatures are expected to range between 40 to 125°F and contain 40 to 70% methane and the remainder composed of 30- 40% CO2, trace quantities of nitrogen and hydrogen, and up to 3,000 ppm of H2S.

- Based on the digester gas heat content of 645 Btu/scf and a maximum annual throughput rate of 9.44 MMscf/year, the maximum heat input rate is 6,085.6 MMBtu/year of digester gas burned in the flare.

- Natural gas will be supplied for the burner’s pilot burner at pressures between 1 and 5 psig.

- The maximum annual throughput rate of natural gas was estimated to be 0.44 MMscf/year.

Waste Gas Burner (Flare 2).

Flare 2 will operate when digester gas is generated by SWWRF Digester No. 3.  The digester gas will contain particulate materials and greasy oils.  The applicant proposes to install and operate the open-candlestick-type flare with the following specifications:

- Maximum design flow rate of 600 scfm open-candlestick type flare with automatic ignition and designed to burn low pressure digester gas.

- Digester gas temperatures are expected to range between 40 to 125°F and contain 40 to 70% methane and the remainder composed of 30- 40% CO2, trace quantities of nitrogen and hydrogen, and up to 3,000 ppm of H2S.

- Based on the digester gas heat content of 186 Btu/scf and a maximum annual throughput rate of 3.6 MMscf/year, the maximum heat input rate is 664.1 MMBtu/year of digester gas burned in the flare.

- Natural gas will be supplied for the burner’s pilot burner at pressures between 1 and 5 psig.

- The maximum annual throughput rate of natural gas was estimated to be 0.44 MMscf/year.

Low‐Btu Waste Gas Burner or Thermal Oxidizer (Flare 3).

Flare 3, thermal oxidizer, will operate when low‐pressure waste gas is generated by the BUS.  The applicant proposes to install and operate the thermal oxidizer with the following specifications:

- Maximum design flow rate of 140 scfm for the thermal oxidizer.

- The combustion stack assembly is capable of using natural gas and BUS gas as the pilot gas.

- The waste gas is expected to contain 79 to 82% CO2 and the remainder composed of 15 to 18% methane, and trace quantities of H2S.

- Based on the waste gas heat content of 186 Btu/scf and a maximum annual throughput rate of 73.6 MMscf/year, the maximum heat input rate is 13,686.6 MMBtu/year of waste gas burned in the thermal oxidizer.

- The maximum annual throughput rate of the natural gas was estimated to be 0.88 MMscf/year.

- The thermal oxidizer is designed for an overall 99.9% destruction efficiency of methane.

BUS Startup Flare (Flare 4).

Flare 4 will operate when excess product gas is generated by the BUS.  Gas produced from the BUS will be wasted and combusted during its normal startup process and occasionally during normal operation for pressure control.  The applicant proposes to install and operate an open-candlestick type flare with the following specifications:

- Maximum design flow rate of 200 scfm open-candlestick type flare with automatic ignition.

- BUS product gas is expected to contain 98% methane and the remainder composed of CO2, trace quantities of nitrogen and hydrogen, and less than 50 ppm of H2S.

- The product gas temperature is expected to be between 50 and 150°F with a gas pressure of 0.5 to 1.0 psig.

- Based on the BUS product gas heat content of 990 Btu/scf and a maximum annual throughput rate of 6,088 scf/year, the maximum heat input rate is 6.0 MMBtu/year of product gas burned in the flare.

- Natural gas will be supplied for the burner’s pilot burner at pressures between 45 and 55 psig.

- The maximum annual throughput rate of the natural gas was estimated to be 0.22 MMscf/year.

- State Rule Provisions for the Flares

The City requested an exemption from permitting for Flares 1, 2 and 4 based on the provisions under Rule 62-210.300(3)(b)(1), F.A.C., Generic and Temporary Exemptions:

- The flares are not subject to any unit-specific limitation or requirement.

- Emissions from the flares, in combination with the emissions of other units and activities at the facility, does not cause the facility to emit or have the potential to emit (PTE) any pollutant in such amount as to create a Title V source.

- The flares would neither emit nor have the PTE 500 lb/year or more of lead, 1,000 lb/year or more of any HAP, 2,500 lb/year or more of total HAP, or 5 TPY or more of any other regulated air pollutant.

- Emissions from the new flares or in combination with the emissions of any other new or modified units and activities at the existing facility does not result in a modification subject to PSD preconstruction review.

- The new flares would not constitute a modification of any existing non-exempt emissions unit at a non-Title V source or any existing non-insignificant emissions unit at a Title V source.

Based on the application, Flares 1, 2 and 4 meet the exemption; therefore, the flares are not included in the permit.  If it is determined that the cleaned digester BUS gas does not meet the characteristics of pipeline quality natural gas (or equivalent) and new calculations are required, the exemption for the flares will be reevaluated based on new findings.

- Odor Control Systems – Carbon Scrubbers.

Odor control systems will be installed to treat foul air generated by two primary clarifiers, WAS holding tank, splitter box and gravity belt thickener hoods.  For high H2S concentration (> 50 ppm), each control system will consist of a biotrickling filter followed by a carbon scrubber.  The gravity room will be treated by the activated carbon units only.  Each system will include a 12,000 cfm fan that will be used to maintain the flow rate while maintaining a negative pressure in the tanks.  An additional fan and an activated carbon unit will be installed and available for backup.  The general design specifications for the odor control systems are:

- Biotrickling Filter Design:

- Vessel diameter of 12 feet, bed depth of 16 feet and a media volume of 1,800 cubic feet;

- Detention time of 12 seconds;

- Gas velocity of 80 feet per minute (fpm);

- Flow rate of 9,000 cfm;

- 99% removal of H2S, typical; and

- 40 to 50% removal of organic odors.

- Activated Carbon System Design:

- Treats H2S and organic sulfides odors;

- Bed depth of 3 feet;

- Detention time of 3.39 seconds;

- Gas velocity of 53 fpm;

- Flow rate of 12,000 cfm;

- Influent H2S concentration – up to 5 ppm;

- Pressure drop across carbon bed is 2 inches per foot of media;

- 99.9% removal of H2S.

- State Rule Provisions for the Odor Control Systems

The City requested an exemption from permitting for the odor control systems based on the provisions under Rule 62-210.300(3)(b)(1), F.A.C., Generic and Temporary Exemptions as described for the flares in Section 3.2.3.1.  Based on the application, the odor control systems meet the exemption.  However, the applicant shall submit to the Department the final design specifications for the odor control systems including the designed H2S control efficiency.

- Cooling Tower

A cooling tower (Marley Model MHF7105QAEBN, or equivalent) will be used to facilitate requisite cooling of the mesophilic digesters and the digester gas prior to entering the BUS with the following nominal design specifications:  2-cells with cooling fans; an air exit temperature of 85°F; a circulating water flow rate of 650 gallons/minute; and a drift rate of no more than 0.005% of the recirculating water flow rate.

- State Rule Provisions for the Cooling Tower

The City requested an exemption from permitting for the cooling tower based on the provisions under Rule 62-210.300(3)(b)(1), F.A.C., Generic and Temporary Exemptions as described for the flares in Section 3.2.3.1.  Based on the application, the cooling tower meets the exemption.  However, the applicant shall submit to the Department the final design specifications for the cooling tower including a maximum designed droplet drift rate of 0.005%.

- Project Emissions

Based on the information provide in the application, pollutant emissions from the project did not constitute major source for PSD of air quality in accordance with Rule 62-212.400, F.A.C. and the potential and HAP emissions (facility-wide) did not constitute the facility to be a major Title V source in accordance with Rule 62-213, F.A.C.

- Engines/Generators (EU 001 and EU 002)

The applicant proposes the following maximum emission rates for the 1.1 MW spark ignitions RICE/generator sets with a maximum engine rating of 1,157 HP at 100% load with a nominal power rating of 1,100 kW.

- NOX:  1.0 g/HP-hour

- 3.34 lb/hour and 14.65 TPY per engine and 29.3 TPY for both engines

- CO:  2.0 g/HP-hour

- 6.69 lb/hour and 29.3 TPY per engine and 58.6 TPY for both engines

- VOC:  0.7 g/HP-hour

- 2.34 lb/hour and 10.25 TPY per engine and 20.5 TPY for both engines

- PM/PM10/PM2.5:  0.03 g/HP-hour

- 0.10 lb/hour and 0.44 TPY per engine and 0.88 TPY for both engines

- SO2:  0.000588 lb/MMBtu

- 0.002 lb/hour and 0.009 per engine and 0.017 TPY for both engines

- Potential NOX, CO and VOC emissions were based on the emission standards for the engines firing natural gas specified in NSPS Subpart JJJJ of 40 CFR 60.  SO2 emissions were based on an emission factor obtained from AP-42 for the engines firing natural gas.  PM emissions were based on engine vendor data.

- Site-specific emissions testing in Florida for these engines firing cleaned digester BUS gas have not been done.  However, several previous projects using the similar engines (CAT 3520C) firing landfill gas, digester gas or biogas have been installed and are in operation.  Based on actual test data from these facilities emissions of NOX ranged from 0.28 to 0.48 g/HP-hour, emissions from CO ranged between 1.9 to 2.66 g/HP-hour, and emission of VOC ranged from 0.23 to 0.64 g/HP-hour.  The wide range of emissions from these engines are due to the various characteristics of the gas such as the methane, CO2, N, oxygen (O2), H2S content and the heat content of the gas.  Contaminants found in waste gas include VOC, siloxanes, ammonia, hydrogen chloride, formaldehyde, metals, chlorine and fluorine.  The type of process used to clean the waste gas will alter the characteristics of the gas by increasing the methane and heating content of the gas, reduce CO2, N, O2, and other contaminants.

- After the waste gases are cleaned, the characteristics of the gas may still contain siloxanes which affects the performance of the engines over time.  Siloxane deposits degrade the performance of the engine and extensive maintenance is required to restore the combustion equipment to proper operation.  As the engine performance degrades, it is difficult to maintain the engine tuned for low CO and NOX emissions.  SO2 emissions can be produced during the combustion of these gases since it contains sulfur-bearing compounds (such as H2S) that are oxidized at normal engine operating temperatures.  The applicant estimates an H2S concentration of 3,000 ppmv for the digester gas upstream of the BUS and 50 ppmv in the cleaned digester BUS gas.  The applicant contends that the BUS used to clean the digester gas removes 99% of H2S, 99% or more of siloxanes and VOC and cleans the digester gas to natural gas standards.

Based on the information provided in the application, the Department will establish NOX, CO and VOC emission limits based on firing natural gas.  The draft permit will specify prior to firing the cleaned digester BUS gas in the engines, the permittee will provide the Department with the following:

- Manufacturers guarantee stating these engines will not lose their certification when firing cleaned digester BUS gas.

- If the engines lose their certification due to the firing of cleaned digester BUS gas, these engines shall be tested to demonstrate compliance with the natural gas emissions standards for NOX, CO and VOC (applicant request).

- Digester gas sampling and analysis shall be performed on the cleaned digester BUS gas demonstrating the gas meets or is equivalent to natural gas standards.

- If the analysis shows the digester gas does not meet natural gas standards, the permittee shall provide the Department with new calculations for all PSD pollutants and HAPs resulting from this project as well as facility-wide emissions to determine PSD applicability and Title V status.

- Boilers (EU 003 and EU 004)

The two 6.38 MMBtu/hour boilers will primarily be used to provide heated water to the digests as well as supplemental heated water throughout the process.  Natural gas and cleaned digester BUS gas will be fired in the boilers.  The following emission associated with the boilers were based on firing natural gas:

As shown in Table 6, the potential emissions produced from the boilers are minimal based on the natural gas emissions factors used for firing both natural gas and cleaned digester BUS gas.  To provide reasonable assurance that the fuel fired in the boilers will meet potential emissions provided in the application, the draft permit will require the digester gas to be sampled and an analysis provided demonstrating the gas meets natural gas standards.

Table 6 - Boiler Potential Emissions.

| Emission Source | Annual Emissions (TPY) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | CO | NOX | SO2 | PM/PM10/PM2.5 | VOC |
| Boilers, combined | 4.61 | 5.48 | 0.03 | 0.1/0.42/0.42 | 0.3 |

- Flares 1 – 4

The flares will be operating under the following scenarios:

- Flare 1 will operate when digester gas is generated by the SWWRF new anaerobic digesters (Digester Nos. 1 and 2) or during emergency situations.  Estimated gas throughput of 9,435,039 scf/year with a heat content of 645 Btu/scf.

- Flare 2 will operate when digester gas is generated by SWWRF Digester No. 3.  Estimated gas throughput of 3,570,459 scf/year with a heat content of 186 Btu/scf.

- Flare 3, thermal oxidizer, will operate when low‐pressure waste gas is generated by the BUS.  Estimated gas throughput of 74,000,000 scf/year with a heat content of 186 Btu/scf.

- Flare 4 will operate when excess product gas is generated by the BUS.  Estimated gas throughput of 6,088 scf/year with a heat content of 990 Btu/scf.

Proposed emissions from the flares are summarized in Table 7.  Emissions were estimated based on the heat content of the gas and the estimated throughput of the gas to the flare and pilot.

Table 7 - Potential emission from the Flares.

| Emission Source | Annual Emissions (TPY) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | CO | NOX | SO2 | PM/PM10/PM2.5 | VOC |
| Flare 1 | 0.54 | .2 | 2.29 | 0.28/0.28/0.28 | 0.27 |
| Flare 2 | 0.51 | 0.09 | 0.87 | --- | 0.19 |
| Flare 3 | 2.22 | 0.44 | 36.79 | --- | 0.61 |
| Flare 4 | 0.042 | 0.0078 | 0.00018 | --- | 0.0161 |

As shown in Table 7, the potential emissions produced from the flares 1, 2 and 4 are minimal and meet the exemption requirement pursuant to Rule 62-210.300, F.A.C.  Flare 4 (EU 005) emissions of SO2 were estimated to be higher due to the low-pressure waste gas being flared.  To provide reasonable assurance emissions from the flare will meet the estimated emissions provided in the application, the draft permit requires a visible emissions test for Flare No. 4.

- Odor Control Systems (EU 006)

Odor control systems will be installed to treat foul air generated by two primary clarifiers, WAS holding tank, splitter box and gravity belt thickener hoods.  For high H2S concentration (> 50 ppm), each control system will consist of a biotrickling filter followed by a carbon scrubber.  The gravity room will be treated by the activated carbon units only.

Proposed emissions from the odor control systems are summarized in Table 8.  Emissions were estimated based on the H2S concentration in the foul air from the headworks, primary clarifiers, gravity belt thickening building and the dewatering building.

Table 8 - Potential emission from the Odor Control Systems.

| Emission Source | H2S Concentration (ppmvd) | Control Efficiency | H2S (TPY) |
| --- | --- | --- | --- |
| Headworks (existing Scrubber) | 275 | 95% | 1.183 |
| Primary Clarifiers, Gravity Belt Thickening | 10 | 95% | 0.278 |
| Dewatering Building | 45 | 95% | 1.26 |

As shown in Table 8, the potential emissions produced from the odor control systems are minimal and meet the exemption requirement pursuant to Rule 62-210.300, F.A.C.  However, to provide reasonable assurance that the scrubbers are designed to meet the 95% control efficiency, the draft permit requires the applicant to provide the final design specifications for the scrubbers including the designed H2S control efficiency.

- Cooling Tower (EU 007)

A cooling tower will be used to assist in the cooling of the mesophilic digesters and the digester gas prior to entering the BUS.  Emissions were estimated based on a circulating water flow rate of 650 gallons/minute and a drift rate of 0.005%.

Proposed PM/PM10/PM2.5 emissions from the cooling tower were estimated to be 0.11/0.11/0.06 TPY.  The potential emissions produced from the cooling tower are minimal and meet the exemption requirement pursuant to Rule 62-210.300, F.A.C.  However, to provide reasonable assurance that the cooling tower is designed to with a drift rate of 0.005%, the draft permit requires the applicant to provide the final design specifications showing a 0.005% drift rate for the cooling tower

- Title V Major Source Applicability

- Hazardous Air Pollutants

Hazardous Air Pollutants as specified in Rule 62-210.200(160), F.A.C are produced during the combustion of digester gas to be used as fuel by the engines since the fuel combustion process is not 100% complete and a small portion of the HAPs pass through the fuel combustion system.  The presence of methane and elevated temperatures (700°F – 900°F) in the engine exhaust produces formaldehyde (CH2O, a regulated HAP).  Engines typically reduce halogenated species by 93% and non-halogenated species by 86.1%.  Based on 100% design capacity of the engines, the applicant estimates total annual HAP emissions from both engines to be 6.07 TPY.  The applicant estimated the total annual HAP emissions from the project as well as facility-wide to be 6.18 TPY.

Based on the application, the proposed emission sources at the facility will not emit or have the potential to emit 100 TPY of any regulated pollutant, 10 TPY or more of a single HAP, as well as 25 TPY or more of any combination of HAPs.  Therefore, the Department identifies this facility to be an area source of HAP and not a Title V major source of air pollution.

- Preliminary Determination

The Department makes a preliminary determination that the proposed project will comply with all applicable state and federal air pollution regulations as conditioned by the draft permit.  This determination is based on a technical review of the complete application, reasonable assurances provided by the applicant, and the conditions specified in the draft permit.  No air quality modeling analysis is required because the project does not result in a significant increase in emissions.  Tammy McWade is the project engineer responsible for reviewing the application and drafting the permit.  Additional details of this analysis may be obtained by contacting the project engineer at the Department’s Office of Permitting and Compliance at Mail Station #5505, 2600 Blair Stone Road, Tallahassee, Florida  32399-2400.

In making this calculation, the values listed in 40 CFR 98, Subpart A, Table A-1 are used to weight emissions by their respective Global Warming Potential (GWP).  For example, the current GWP factors for four of the GHGs are:  CO2 = 1; CH4 = 25; N2O = 298 and SF6 = 22,800.

This procedure was held to be invalid at the federal level due to a U.S. Supreme Court opinion dated June 23, 2014.  
Link to Supreme Court Opinion  The Department is reviewing the effects of the decision on its own rules.  EPA issued guidance regarding implementation of the decision on July 24, 2014.  Link to EPA Guidance