### TECHNICAL EVALUATION

&

PRELIMINARY DETERMINATION

#### APPLICANT

Georgia-Pacific Consumer Operations, LLC

Post Office Box 919

Palatka, Florida  32178

Palatka Mill

Facility ID No. 1070005

#### PROJECT

# Project No. 1070005-080-AC

Application for Minor Source Air Construction Permit

No. 4 Recovery Boiler Conversion of Oil Burners to Natural Gas Burners

#### COUNTY

Putnam County, Florida

PERMITTING AUTHORITY

Florida Department of Environmental Protection

Division of Air Resource Management

Office of Permitting and Compliance

2600 Blair Stone Road, MS#5505

Tallahassee, Florida  32399-2400

May 16, 2013

1.  General Project INFORMATION

Air Pollution Regulations

Projects at stationary sources with the potential to emit air pollution are subject to the applicable environmental laws specified in Section 403 of the Florida Statutes (F.S.).  The statutes authorize the Department of Environmental Protection (Department) to establish regulations regarding air quality as part of the Florida Administrative Code (F.A.C.), which includes the following applicable chapters:  62-4 (Permits); 62-204 (Air Pollution Control – General Provisions); 62-210 (Stationary Sources – General Requirements); 62-212 (Stationary Sources – Preconstruction Review); 62-213 (Operation Permits for Major Sources of Air Pollution); 62-296 (Stationary Sources - Emission Standards); and 62-297 (Stationary Sources – Emissions Monitoring).  Specifically, air construction permits are required pursuant to Chapters 62-4, 62-210 and 62-212, F.A.C.

In addition, the U. S. Environmental Protection Agency (EPA) establishes air quality regulations in Title 40 of the Code of Federal Regulations (CFR).  Part 60 specifies New Source Performance Standards (NSPS) for numerous industrial categories.  Part 61 specifies National Emission Standards for Hazardous Air Pollutants (NESHAP) based on specific pollutants.  Part 63 specifies NESHAP based on the Maximum Achievable Control Technology (MACT) for numerous industrial categories.  The Department adopts these federal regulations in Rule 62-204.800, F.A.C.

Glossary of Common Terms

Because of the technical nature of the project, the permit contains numerous acronyms and abbreviations, which are defined in Appendix A of this permit.

Facility Description and Location

Georgia-Pacific Consumer Operations, LLC (Georgia-Pacific) operates the existing Palatka Mill, which is a Kraft pulp and paper mill that consists of major activities areas such as: chip handling, pulping, bleaching, chemical recovery, utilities, paper machines, converting, and turpentine and tall oil production.  Refer to Figures 1 and 2.  The existing Palatka Mill is located in Putnam County at 215 County Road 216 in Palatka, Florida.

The pulp and paper mill is categorized under Standard Industrial Classification (SIC) Code Nos. 2611 and 2621.  The UTM coordinates of the existing facility are Zone 17, 434.0 kilometers (km) East, and 3283.4 km North.  This site is in an area that is in attainment (or designated as unclassifiable) for all air pollutants subject to Ambient Air Quality Standards (AAQS).

Palatka Mill ▲

Putnam County

Figure 1 – Location of Putnam County, Florida	Figure 2 – Location of Palatka Mill

- Process Description

- The existing mill uses the Kraft sulfate process in which the digesting liquor (white liquor) is a solution of sodium hydroxide and sodium sulfide that is mixed with wood chips and cooked under pressure (Figure 3).  Black liquor is a by-product from the digestion of wood chips.  Weak black liquor is concentrated and introduced into a special boiler known as a black liquor recovery boiler.  The organic fraction is burned in stages and the energy is recovered for steam production.

- The inorganic fraction containing the spent cooking chemicals (primarily sodium carbonate and sodium sulfide) is recovered as smelt from a bed of char that forms on the floor of the boiler (Figure 4).  The smelt drains, cools and is then diluted with water to make green liquor.  The green liquor is causticized with lime to make the white liquor for use in the digestion of wood chips.

- Figure 3 – Chemical, Energy Recovery	Figure 4 – Char/Smelt Bed

Facility Regulatory Categories

- The facility is a major source of hazardous air pollutants (HAP).

- The facility does not operate units subject to the acid rain provisions of the Clean Air Act.

- The facility is a Title V major source of air pollution in accordance with Chapter 62-213, F.A.C.

- The facility is a major stationary source in accordance with Rule 62-212.400, F.A.C. for the Prevention of Significant Deterioration (PSD) of Air Quality.

- The existing No. 4 Recovery Boiler is subject to the applicable federal National Emissions Standards for Hazardous Air Pollutants (NESHAP) provisions in Subparts A (General Provisions) and MM (National Emission Standards for Hazardous Air Pollutants for Chemical Recovery Combustion Sources at Kraft, Soda, Sulfite, and Stand-Alone Semichemical Pulp Mills) of 40 CFR 63.

State Provisions

The existing No. 4 Recovery Boiler is subject to Rules 62-296.404 (Kraft (Sulfate) Pulp Mills and Tall Oil Plants), 62-212.400 (BACT Determination for CO, NOX, PM, and VOC emissions), F.A.C.  The existing facility has met the applicable requirements of these rules.  The reporting and monitoring of actual emissions of NOX for 5 years following the project will ensure the PSD BACT determinations will be met.

NSPS Provisions

The existing Palatka Mill is not currently subject to NSPS Subpart BB (Standards of Performance for Kraft Pulp Mills) or Subpart Db (Standards of Performance for Industrial-Commercial-Institutional Steam generators) in 40 CFR 60.  An existing source can become subject to NSPS Subpart Db and NSPS Subpart BB if the existing facility is “modified” or “reconstructed”.

Modification is defined as any physical or operational change to an existing facility which results in an increase in the emission rate to the atmosphere of any pollutant to which a standard applies shall be considered a modification.  …..use the following to determine emission rate:  Emission factors as specified in the latest issue of “Compilation of Air Pollutant Emission Factors,” EPA Publication No. AP-42.... where utilization of emission factors demonstrates that the emission level resulting from the physical or operational change will either clearly increase or clearly not increase.

Reconstruction is defined as the replacement of components of an existing facility to such an extent that the fixed capital cost of the new components exceeds 50 percent of the fixed capital cost that would be required to construct a comparable entirely new facility, and it is technologically and economically feasible to meet the applicable standards set forth in this part.

NSPS Subpart BB of 40 CFR 60

NSPS Subpart BB regulates emission of PM and TRS.  The replacement of the fuel oil burners with natural gas burners represents a physical change in the No. 4 Recovery Boiler.  However, according to the applicant, the change will not cause an increase in emissions of either PM or TRS on a maximum hourly basis.  Emissions of TRS are expected to be less since natural gas has less sulfur than No. 6 fuel oil.  Therefore, the proposed project will not be considered a modification to the No. 4 Recovery Boiler.  Additionally, the cost of the proposed component replacements to the No. 4 Recovery Boiler will be minimal, less than 50% of the cost of replacing the recovery boiler.  Therefore, the proposed project will not constitute reconstruction.  For these reasons, the proposed project will not result in the No. 4 Recovery Boiler being subject to the applicable requirements of NSPS Subpart BB.

NSPS Subpart Db of 40 CFR 60

NSPS Subpart Db regulates emission of NOX, SO2 and PM.  The addition of the natural gas burners does represent a physical change in the No. 4 Recovery Boiler.  However, according to the applicant, the change will not cause an increase in emissions of NOX, SO2 and PM on a maximum hourly basis.  Therefore, the proposed project will not be considered a modification to the No. 4 Recovery Boiler.  Additionally, the cost of the proposed component replacements to the No. 4 Recovery Boiler will be minimal, less than 50% of the cost of replacing the recovery boiler.  Therefore, the proposed project will not constitute reconstruction.  For these reasons, the proposed project will not result in the No. 4 Recovery Boiler being subject to the applicable requirements of NSPS Subpart Db.

NESHAP Provisions

The existing No. 4 Recovery Boiler is subject to the following applicable NESHAP provisions:  Subparts A (General Provisions) and MM (National Emission Standards for Hazardous Air Pollutants for Chemical Recovery Combustion Sources at Kraft, Soda, Sulfite, and Stand-Alone Semichemical Pulp Mills) in 40 CFR 63.  The existing facility has met the applicable requirements of these subparts.

Project Description

- The applicant, Georgia-Pacific, is requesting to install new burners and associated equipment that will allow the No. 4 Recovery Boiler, which is emission unit 018 (EU 018) at the facility, to burn natural gas instead of fuel oil as a supplemental fuel.  The applicant is proposing the following changes to the boiler:

- Replace the existing residual oil load burners with burners designed to burn natural gas alone.

- Replace the existing residual oil starter burners with natural gas starter burners.

- Replace the flame scanners on all burners with class 1 igniters with flame rods.

- Install new Programmable Logic solver (PLC)-based burner management system controls.

- Install fuel trains, piping and hardware to support the addition of natural gas as a permitted fuel.

- According to the applicant, the proposed project may result in an increase in the utilization of the No. 4 Recovery Boiler due to the difference in efficiencies of burning natural gas in the No. 4 Recovery Boiler versus the No. 7 Package Boiler.  The conversion to natural gas is not intended to increase the overall annual steam production rate or emissions at the mill.  The proposed project is scheduled to begin in July 2013 and continue through the annual outage in October 2013.

2.  PSD Applicability

General PSD Applicability

The Department regulates major stationary sources in accordance with Florida’s PSD program pursuant to Rule 62-212.400, F.A.C.  PSD preconstruction review is required in areas that are currently in attainment with the state and federal ambient air quality standards (AAQS) or areas designated as “unclassifiable” for these regulated pollutants.  Commonly addressed PSD pollutants for Kraft pulp mills such as the Palatka Mill include: carbon monoxide (CO), nitrogen oxide (NOX), PM, PM with a mean diameter of 10 microns or less (PM10), PM with a mean diameter of 2.5 microns or less (PM2.5), sulfur dioxide (SO2), volatile organic compounds (VOC) and sulfuric acid mist (SAM).

Additional PSD pollutants that are more common to certain other industries include: lead (Pb), mercury (Hg), hydrogen sulfide (H2S), TRS including H2S, reduced sulfur compounds (RSC) including H2S, municipal waste combustor (MWC) organics measured as total tetra- through octa-chlorinated dibenzo-p-dioxins and dibenzofurans (dioxin/furan), MWC metals measured as PM; MWC acid gases measured as SO2 and HCl, and municipal solid waste (MSW) landfill emissions as non-methane organic compounds (NMOC).

As defined in Rule 62-210.200(Definitions), F.A.C., a stationary source is a “major stationary source” (major PSD source) if it emits or has the potential to emit (PTE):

- 250 tons per year (tons/year) or more of any PSD pollutant; or

- 100 tons/year or more of any PSD pollutant and the facility belongs to one of the 28 listed PSD major facility categories.

The list given in the citation includes the category of “Kraft pulp mills”.  The given category applies to the facility before and after the proposed project.  The Palatka Mill is a major stationary source based on actual emissions of and potential to emit 100 tons/year or more of several individual PSD pollutants.

For major stationary sources such as the Palatka Mill, PSD applicability for modification projects is based on thresholds known as the significant emission rates (SER) as defined in Rule 62-210.200(Definitions), F.A.C.  Any “net emissions increase” as defined in Rule 62-210.200(Definitions), F.A.C. of a PSD pollutant from the project that equals or exceeds the respective SER is considered “significant”.  SER also means any emissions rate or any net emissions increase of a PSD pollutant associated with a major stationary source or major modification which would construct within 10 km of a Class I area and have an impact on such area equal to or greater than 1 gram per cubic meter, 24-hour average.

Although a facility may be “major” (i.e. emits or has the potential to emit 100 or 250 tons/year (TPY) as applicable) for only one PSD pollutant, a project must include Best Available Control Technology (BACT) controls for any PSD pollutant that exceeds the corresponding significant emission rates given in the Table 1 below.

Table 1 - List of SER by PSD-Pollutant. 1, 3

| Pollutant | SER (TPY) | Pollutant | SER (TPY) |
| --- | --- | --- | --- |
| CO | 100 | NOX | 40 |
| PM/PM10/PM2.5 | 25/15/10 | Ozone (VOC) 2 | 40 |
| PM2.5 (NOX) | 40 | PM2.5 (SO2) | 40 |
| Ozone (NOX) 2 | 40 | SAM | 7 |
| SO2 | 40 | Pb | 0.6 |
| Hg | 0.1 | GHG (CO2e) | 75,000 3 |
| - Excluding fluoride and those pollutants defined for Pulp and Paper, MWC, MSW landfills. - Ozone (O3) is regulated by its precursors (VOC and NOX). PSD for PM2.5 can be triggered by its precursors (NOX and SO2). - Federal SER of 75,000 TPY for GHG (as CO2e) for PSD sources and has not been incorporated into Department rules. |  |  |  |

According to 40 CFR 52.21, six greenhouse gases (GHG), are also be subject to regulation at new stationary sources that will emit or have the potential to emit 100,000 tons/year (SER equal to 75,000 tons/year) expressed as the carbon dioxide equivalent emissions (CO2e).  This requirement has not been incorporated into Department rules but is a separate requirement of the EPA.

PSD Applicability for Project

The project is located in Putnam County which is in an area that is currently in attainment with the AAQS or is otherwise designated as unclassifiable.  As provided in the application, Table 2 below summarizes potential emissions and PSD applicability for the project.

Table 2.  Summary of the Applicant’s PSD Applicability Analysis

| Pollutant | Annual Emissions, Tons/Year |  |  |  | Subject to PSD? |
| --- | --- | --- | --- | --- | --- |
|  | Baseline Actual a | Projected Actual b | Increase c | Significant Emissions Rate |  |
| CO | 1,225.28 | 1,265.04 | 39.76 | 100 | No |
| NOX | 472.18 | 507.97 | 35.79 | 40 | No |
| PM | 97.88 | 84.80 | -13.08 | 25 | No |
| PM10 | 94.97 | 90.07 | -4.90 | 15 | No |
| PM2.5 | 73.92 | 72.08 | -1.84 | 10 | No |
| SO2 | 78.75 | 39.78 | -38.97 | 40 | No |
| VOC | 20.53 | 34.83 | 14.30 | 40 | No |
| TRS | 8.15 | 6.05 | -2.1 | 10 | No |
| SAM | 3.40 | 1.11 | -2.29 | 7 | No |
| Lead | 0.00565 | 0.00433 | -0.00132 | 0.6 | No |
| Mercury | 0.00142 | 0.00154 | 0.00012 | 0.1 | No |
| GHG | 36,975 | 69,233 | 32,258 | 75,000 | No |
| CO2e | 56,077 | 92,067 | 35,990 | 75,000 | No |
| - Baseline actual emissions were calculated based on the following highest consecutive 2-year average: 1/2005 – 12/2006 (TRS, PM/PM10/PM2.5); 7/2005 – 6/2007 (NOX); 10/2006 – 9/2008 (CO, Hg); 12/2006 – 11/2008 (VOC); 2/2008 - 1/2010 (Lead); 6/2008 – 5/2010 (GHG); 10/2010 - 9/2012 (SAM); and 12/2010 – 11/2012 (SO2). - Projected actual emissions based on worst case heat input increases. The projected actual black liquor solids (BLS) processing rate for this project was determined to be 823,000 tons BLS/year. The total projected annual heat input rate of the BLS (9,629,100 Million British thermal units per year (MMBtu/year) and natural gas firing of 10% of the total permitted annual heat input rate (1,178,220 MMBtu/year) is 10,807,320 MMBtu/year. - The increase from the project is the difference between the projected and baseline actual emissions. |  |  |  |  |  |

As shown in the above table, total project emissions will not exceed the PSD significant emissions rates; therefore, the project is not subject to PSD preconstruction review.

The applicant provided a GHG and CO2e emissions PSD analysis to demonstrate that the proposed project would not trigger a PSD review per 40 CFR 52.21, i.e., the PSD Tailoring Rule.

3.  DEPARTMENT REVIEW

No. 4 Recovery Boiler

The No. 4 Recovery Boiler (EU 018) began operation in December of 1976.  The maximum operational rate of this emissions unit is 210,000 pounds per hour of black liquor solids (lb BLS/hour).  The boiler is designed and permitted to burn black liquor (BLS) to utilize its inherent energy and recover inorganic chemicals from the spent cooking liquor.  The recovery boiler is currently permitted to fire a total maximum heat input rate of 11,782,200 million British thermal units per hour (MMBtu/hour) of BLS, No. 6 fuel oil and on-specification used oil.  The annual fuel oil firing is limited to an annual capacity factor of less than 10% of the maximum permitted annual heat input rate, which is equivalent to 1,178,220 MMBtu/year of fuel oil.  On-specification used oil is limited to less than 10% of fuel oil on an annual basis.

The applicant is proposing to install new burners and associated equipment to convert the No. 4 Recovery Boiler from burning fuel oil to burning natural gas as a supplemental fuel.  The total heat input to the boiler from the combustion of natural gas in the startup and load burners combined will be 664 MMBtu/hour.  The applicant is requesting to limit the annual natural gas heat input to the current fuel oil limit of 1,178,220 MMBtu during any consecutive 12 months.  As part of this project, the applicant is proposing to use natural gas in the recovery boiler for more than just startup, shutdown or as a supplemental fuel.  The increase in usage depends on the efficiency of the No. 4 Recovery Boiler firing natural gas versus the No. 7 Package Boiler.

Emissions

Pipeline quality natural gas contains only trace amounts of ash, sulfur and other contaminants.  Therefore, emissions from firing natural gas in an equivalent amount based on heat input to currently used fuel oil in the No. 4 Recovery Boiler is not expected to exceed any significant emission rates.  However, the applicants PSD analysis showed an NOX emission increase of 35.79 tons/year, which is just below the PSD significant emissions rate of 40 tons/year.  To provide reasonable assurance that the project emissions will not exceed the PSD significant emissions rates, the Department estimated the difference in emissions by comparing the AP-42 emission factors for the combustion of fuel oil and natural gas.  The results are summarized in Table 3.

Table 3.  Estimated Emissions Data for the No. 4 Recovery Boiler firing Fuel Oil and Natural Gas

| Pollutant | Heat Input (MMBtu/Year)a | Fuel Oil Emissions |  | Natural Gas Emissions |  | Increase (Tons/Year) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Emission Factor (lb/MMBtu)b | Equivalent Emissions (Tons/Year) | Emission Factor (lb/MMBtu)c | Equivalent Emissions (Tons/Year) |  |
| CO | 1,178,220 | 0.033 | 19.64 | 0.084 | 49.48 | 29.84 |
| NOX | 1,178,220 | 0.313 | 184.59 | 0.28e | 164.95 | -19.64 |
| PMd | 1,178,220 | 0.165/0.01 | 97.46/5.89 | 0.0019/0.0057 | 1.12/3.36 | -96.34/-2.53 |
| SO2 | 1,178,220 | 2.46 | 1449.01 | 0.0006 | 0.35 | -1448.66 |
| VOC | 1,178,220 | 0.0019 | 1.10 | 0.0055 | 3.24 | 2.14 |
| SAMe | 1,178,220 | 0.09 | 52.61 | --- | --- | -52.61 |
| Lead | 1,178,220 | 0.1 x 104 | 0.006 | 0.5 x 106 | 0.0003 | -0.0057 |
| Mercury | 1,178,220 | 0.8 x 106 | 0.0004 | 0.26 x 106 | 0.0002 | -0.0002 |
| - The maximum permitted heat input rate to the No. 4 Recovery Boiler from firing oil or natural gas. - U.S. EPA AP-42, Chapter 1.3 emission factors for fuel oil combustion divided by the No. 6 fuel oil heating value of 150 MMBtu/103 gallons. - U.S. EPA AP-42, Chapter 1.4 emission factors for natural gas combustion divided by the natural gas heating value of 1000 MMBtu/106 standard cubic feet (scf). - Filterable/Condensable. All condensable PM is assumed to be less than 1.0 micron in diameter. - Determined as sulfur trioxide (SO3) in AP-42, Chapter 1.3 for combustion of fuel oil. No emission factor is given for natural gas combustion in AP-42, Chapter 1.4 for SO3. |  |  |  |  |  |  |

As shown in Table 3, the burning of natural gas alone will result in lower annual emissions of NOX, PM, SO2, SAM, lead and mercury.  CO and VOC showed an increase in annual emissions of 29.84 tons/year and 2.14 tons/year respectively, which is below the PSD significant emissions rates of 100 tons/year (CO) and 40 tons/year (VOC).

In determining NOX emissions, the Department used EPA’s AP-42 emission factors (Chapter 1.4, Table 1.4.1) that a pre-NSPS natural gas fired boiler would have for an uncontrolled NOX emission rate of approximately 280 pounds per million standard cubic feet (lb/MMscf) (equivalent to 0.28 lb NOX /MMBtu and 164.95 tons/year).  In comparison, the NOX emission factor guaranteed by the vendor of 150 lb/MMscf (equivalent to 0.15 lb NOX/MMBtu) would result in annual NOX emissions of 88.37 tons/year.  Based on the vendor guarantee, this project would show a reduction (184.59 tons/year – 88.37 tons/year) of NOX emissions of 96.22 tons/year.

The Department recognizes that emissions from the No. 4 Recovery Boiler will be relatively low due it’s to firing clean natural gas.  Emissions of NOX are controlled by a four-level overfire air system.  Natural gas is a gaseous fuel; therefore PM emissions are low.  The recovery boiler is also equipped with an electrostatic precipitator to control emissions of PM.  Sulfur is a significant component of fuel oils.  Natural gas contains only trace amounts of sulfur compounds; therefore, emissions of SO2 and SAM are expected to be significantly less than when firing fuel oil.  Emissions of CO and VOC are controlled by combustion design and good operating practices.  A continuous emission monitoring system (CEMS) is used to monitor emissions of NOX, SO2, CO and TRS from the No. 4 Recovery Boiler.  Visible emissions are monitored with a continuous opacity monitoring system (COMS).

PSD Applicability

In reviewing the submitted information provided by the applicant, the Department is aware that the emission increases for CO, NOX, VOC and mercury are predicted to be below the PSD significant emission rates.  The applicants PSD analysis compared baseline actual emissions with projected actual emissions.  The analysis shows the change in emissions from the No. 4 Recovery Boiler being converted from firing residual fuel oil to firing natural gas for startup and as a supplemental fuel.  Included in the analysis is the possible increase in the utilization of the recovery boiler while firing natural gas.

Baseline actual emissions for each pollutant were based on the highest 24- month annual average of the last 10 years (March 2003 – December 2012).  Actual emissions were determined based on operating data, available stack test data, CEMS data, and published emissions data.  Table 4-4 in the application, showed the maximum annual BLS burned in the No. 4 Recovery Boiler during this time period was 831,687 tons of BLS/year and the annual average was 732,550 tons of BLS/year.  Fuel oil usage data showed the maximum annual heat input to the recovery boiler was 527,510 MMBtu/year and the annual average was 240,265 MMBtu/year.

The potential emissions were estimated using emission factors developed by Georgia Pacific based on historical operating data, the company’s own representation, and the company expected business activity.  The applicant determined that the No. 4 Recovery Boiler will burn a maximum of 823,000 tons of BLS/year over the next 5 years.  The activity factor used for the combustion of natural gas was based on a maximum annual natural gas heat input of 1,178,220 MMBtu/year, which is equivalent to 10% of the annual heat input to the boiler.  However in actual operation, the annual heat input of firing fuel oil has never been greater than 5% of the annual heat input limit.  The proposed increase in burning natural gas will be based on the efficiency of burning natural gas in the No. 4 Recovery Boiler versus the No. 7 Package Boiler.  The project may result in lower utilization of the No. 7 Package Boiler, which would reduce its emissions.  The possibility of reduced emissions from the package boiler was not addressed in the application.  The recovery boiler will remain subject to all existing emissions standards.

The Department has determined that based on the increase in NOX emissions of 35.79 tons/year, which was just below the PSD significant emissions rate of 40 tons/year, the applicant, shall compute and report annual emissions for a period of 5 years following resumption of regular operations after the No. 4 Recovery Boiler has been converted to fire natural gas.  For this project, the permittee shall use data collected from the CEMS to determine and report the actual annual emissions of NOX for the No. 4 Recovery Boiler to show compliance with the established BACT emission limit included in Permit No. PSD-FL-380 (1070005-038-AC) and that the SER for NOX emissions has not been exceeded due to this project.

4.  Preliminary Determination

The Department makes a preliminary determination that the proposed project will comply with all applicable state and federal air pollution regulations as conditioned by the draft permit.  This determination is based on a technical review of the complete application, reasonable assurances provided by the applicant, and the conditions specified in the draft permit.  No air quality modeling analysis is required because the project does not result in a significant increase in emissions.  Tammy McWade is the project engineer responsible for reviewing the application and drafting the permit.  Additional details of this analysis may be obtained by contacting the project engineer at 850/717-9086 or by email tammy.mcwade@dep.state.fl.us at the Department’s Office of Permitting and Compliance at Mail Station #5505, 2600 Blair Stone Road, Tallahassee, Florida  32399-2400.