Oleander Power Project, L.P.

Oleander Power Project

# Facility ID No. 0090180

# Brevard County

#### Title V Air Operation Permit Renewal

#### Draft/Proposed Permit No. 0090180-008-AV

(Renewal of Title V Air Operation Permit No. 0090180-006-AV)

# Permitting Authority:

State of Florida

Department of Environmental Protection

Division of Air Resource Management

Office of Permitting and Compliance

2600 Blairstone Road

Mail Station #5505

Tallahassee, Florida  32399-2400

# Telephone:  (850) 717-9000

Fax:  (850) 717-9097

# Compliance Authority:

Department of Environmental Protection

Central District Office

3319 Maguire Boulevard

Suite 232

Orlando, FL 32803-3767

Telephone:  (407) 897-4100

Fax:  (850) 412-0455

Title V Air Operation Permit Renewal

Permit No. 0090180-008-AV

Table of Contents

Section	Page Number

Placard Page 	 1

I.	Facility Information.

A.	Facility Description. 	 2

B.	Summary of Emissions Units. 	 2

C.	Applicable Regulations. 	 2

II.	Facility-wide Conditions. 	 4

III.	Emissions Units and Conditions.

A.	Emissions Units -001, -002, -003, -004. 	 6

B.	Emissions Unit -005. 	 14

IV.	Acid Rain Part. 	 21

V.	Clean Air Interstate Rule Part. 	 26

VI.	Appendices. 	 32

Appendix A, Glossary.

Appendix I, List of Insignificant Emissions Units and/or Activities.

Appendix NSPS, Subpart A – General Provisions.

Appendix NSPS, Subpart GG – Standards of Performance for Stationary Gas Turbines.

Appendix NSPS, Subpart KKKK – Standards of Performance for Stationary Gas Turbines.

Appendix RR, Facility-wide Reporting Requirements.

Appendix TR, Facility-wide Testing Requirements.

Appendix TV, Title V General Conditions.

Appendix U, List of Unregulated Emissions Units and/or Activities.

Referenced Attachments. 	 At End

Figure 1, Summary Report-Gaseous and Opacity Excess Emission and

Monitoring System Performance (40 CFR 60, July, 1996).

Table H, Permit History.

Permittee:	Permit No. 0090180-008-AV

Oleander Power Project, L.P.	Oleander Power Project

555 Townsend Road	Facility ID No. 0090180

Cocoa, Florida 32926	Title V Air Operation Permit Renewal

The purpose of this permit is to renew the Title V air operation permit for the above referenced facility.  The existing Oleander Power Project is located at 555 Townsend Road, Cocoa, Brevard County.  UTM Coordinates are:  Zone 17, 520.12 km E, 3137.58 km N.  Latitude is:  280 21’ 51” North; and Longitude is:  800 47’ 41” West.

The Title V air operation permit is issued under the provisions of Chapter 403, Florida Statutes (F.S.), and Florida Administrative Code (F.A.C.) Chapters 62-4, 62-210, 62-213 and 62-214.  The above named permittee is hereby authorized to operate the facility in accordance with the terms and conditions of this permit.

Effective Date:  January 1, 2014

Renewal Application Due Date:  May 20, 2018

Expiration Date:  December 31, 2018

(Draft/Proposed)

JFK/sa/ejs

Subsection A.  Facility Description.

This facility consists of five, dual-fuel (natural gas and fuel oil), nominal 190 megawatt (MW) General Electric Frame 7FA simple-cycle combustion turbine-electrical generators with five 60-foot stacks, two 1.9-million gallon capacity fuel oil storage tanks, and one 900,000 gallon distillate fuel oil storage tank.  Emissions from the combustion turbine units are controlled by Dry Low NOX (DLN) combustors when operating on natural gas, and wet injection when firing fuel oil.  Inherently clean fuels and good combustion practices are employed to control all pollutants.

Subsection B.  Summary of Emissions Units.

| EU No. | ## Brief Description |
| --- | --- |
| Regulated Emissions Units |  |
| 001 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |
| 002 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |
| 003 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |
| 004 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |
| 005 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |
| Unregulated Emissions Units and Activities (see Appendix U, List of Unregulated Emissions Units and/or Activities) |  |
| 006 | Fuel Oil Storage Tank (1.9-million gallon) |
| 007 | Fuel Oil Storage Tank (1.9-million gallon) |
| 008 | One 900,000 gallon distillate fuel oil storage tank. |

Also included in this permit are miscellaneous insignificant emissions units and/or activities (see Appendix I, List of Insignificant Emissions Units and/or Activities).

Subsection C.  Applicable Regulations.

Based on the Title V air operation permit renewal application received May 14, 2013, this facility is not a major source of hazardous air pollutants (HAP).  The existing facility is a prevention of significant deterioration (PSD) major source of air pollutants in accordance with Rule 62-212.400, F.A.C.  A summary of applicable regulations is shown in the following table.

| Regulation | ## EU No(s). |
| --- | --- |
| Federal Rule Citations |  |
| 40 CFR 60, Subpart A, NSPS General Provisions | -001, -002, -003, -004, -005 |
| 40 CFR 60, Subpart GG, Standards of Performance for Stationary Gas Turbines | -001, -002, -003, -004 |
| 40 CFR 60, Subpart KKKK, Standards of Performance for Stationary Combustion Turbines | -005 |
| 40 CFR 72, 73, 75 Acid Rain Requirements | -001, -002, -003, -004, -005 |

| State Rule Citations |  |
| --- | --- |
| Rule 62-4, Florida Administrative Code (F.A.C.), Permitting Requirements | -001, -002, -003, -004, -005, -006, -007, -008 |
| Rule 62-204, F.A.C., Air Pollution Control-General Provisions | -001, -002, -003, -004, -005, -006, -007, -008 |
| Rule 62-210, F.A.C., Stationary Sources-General Requirements | -001, -002, -003, -004, -005, -006, -007, -008 |
| Rule 62-212, F.A.C., Stationary Sources-Preconstruction Review | -001, -002, -003, -004, -005, -006, -007, -008 |
| Rule 62-213, F.A.C., Operation Permits for Major Sources of Air Pollution | -001, -002, -003, -004, -005, -006, -007, -008 |
| Rule 62-214, F.A.C., Requirements for Sources Subject to the Federal Acid Rain Program | -001, -002, -003, -004, -005 |
| Rule 62-296, F.A.C., Stationary Sources Emissions Standards | -001, -002, -003, -004, -005 |
| Rule 62-297, F.A.C., Stationary Sources Emissions Monitoring | -001, -002, -003, -004, -005 |

The following conditions apply facility-wide to all emission units and activities:

- Appendices.  The permittee shall comply with all documents identified in Section VI, Appendices, listed in the Table of Contents.  Each document is an enforceable part of this permit unless otherwise indicated.  [Rule 62-213.440, F.A.C.]

Emissions and Controls

- Not federally Enforceable.  Objectionable Odor Prohibited.  No person shall cause, suffer, allow or permit the discharge of air pollutants, which cause or contribute to an objectionable odor.  An “objectionable odor” means any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance.  [Rule 62-296.320(2) and 62-210.200(Definitions), F.A.C.]

- General Volatile Organic Compounds (VOC) Emissions or Organic Solvents (OS) Emissions.  The permittee shall allow no person to store, pump, handle, process, load, unload or use in any process or installation, volatile organic compounds or organic solvents without applying known and existing vapor emission control devices or systems deemed necessary and ordered by the Department.  [Rule 62-296.320(1), F.A.C.]

{Permitting Note:  Nothing is deemed necessary and ordered at this time.}

- General Visible Emissions.  No person shall cause, let, permit, suffer or allow to be discharged into the atmosphere the emissions of air pollutants from any activity equal to or greater than 20% opacity.  This regulation does not impose a specific testing requirement.  [Rule 62-296.320(4)(b), F.A.C.]

- Unconfined Particulate Matter.  No person shall cause, let, permit, suffer or allow the emissions of unconfined particulate matter from any activity, including vehicular movement; transportation of materials; construction; alteration; demolition or wrecking; or industrially related activities such as loading, unloading, storing or handling; without taking reasonable precautions to prevent such emissions.  Reasonable precautions to prevent emissions of unconfined particulate matter at this facility include:

a.	Chemical or water application to unpaved roads and parking areas.

b.	Sweeping and general maintenance of paved roads and parking areas.

c.	Landscaping or planting of vegetation.

- Other techniques, as necessary.

[Rule 62-296.320(4)(c)2., F.A.C.; and, proposed by applicant in Title V air operation permit renewal application received May 14, 2013.]

Annual Reports and Fees

See Appendix RR, Facility-wide Reporting Requirements for additional details.

- Annual Operating Report.  The permittee shall submit an annual report that summarizes the actual operating rates and emissions from this facility.  Annual operating reports shall be submitted to the Compliance Authority by April 1st of each year.  [Rule 62-210.370(3), F.A.C.]

- Annual Emissions Fee Form and Fee.  The annual Title V emissions fees are due (postmarked) by April 1st of each year.  The completed form and calculated fee shall be submitted to:  Major Air Pollution Source Annual Emissions Fee, P.O. Box 3070, Tallahassee, Florida  32315-3070.  The forms are available for download by accessing the Title V Annual Emissions Fee On-line Information Center at the following Internet web site:  http://www.dep.state.fl.us/Air/permitting/tvfee.htm.  [Rule 62-213.205, F.A.C. and §403.0872(11), Florida Statutes (2013)]

{Permitting Note:  In addition to the change in the Title V fee submission from March 1st to April 1st, Chapter 403.0872(11)(a) has been revised to require that the annual fee be calculated based upon actual emissions rather than allowable emissions, as in the past.  The Department will be exploring the development of a revision to the electronic annual operating report (EAOR) application to automatically calculate the amount of the fee based upon actual emission information provided with the annual operating report.  When completed, the procedures for submitting the fee and/or the submission address may change.  Until further notice, the fees shall continue to be submitted to the address shown in Specific Condition FW7 and according to instructions posted on the Department’s fee information web page.  Be sure to check the Title V Annual Emissions Fee On-line Information Center (see above web site address) periodically for updates, especially before submitting future Title V fee payments.}

- Annual Statement of Compliance.  The permittee shall submit an annual statement of compliance to the compliance authority at the address shown on the cover of this permit within 60 days after the end of each calendar year during which the Title V permit was effective.  [Rules 62-213.440(3)(a)2. & 3. and (b), F.A.C.]

FW9.	Prevention of Accidental Releases (Section 112(r) of CAA).  If, and when, the facility becomes subject to 112(r), the permittee shall:

a.	Submit its Risk Management Plan (RMP) to the Chemical Emergency Preparedness and Prevention Office (CEPPO) RMP Reporting Center.  Any Risk Management Plans, original submittals, revisions or updates to submittals, should be sent electronically through EPA’s Central Data Exchange system at the following address:  https://cdx.epa.gov.  Information on electronically submitting risk management plans using the Central Data Exchange system is available at:  http://www.epa.gov/osweroe1/content/rmp/index.htm.  The RMP Reporting Center can be contacted at:  RMP Reporting Center, Post Office Box 10162, Fairfax, VA  22038, Telephone:  (703) 227-7650.

b.	Submit to the permitting authority Title V certification forms or a compliance schedule in accordance with Rule 62-213.440(2), F.A.C.

[40 CFR 68]

The specific conditions in this section apply to the following emissions units:

| EU No. | Brief Description |
| --- | --- |
| -001 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |
| -002 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |
| -003 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |
| -004 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |

These four emissions units are each comprised of a nominal 190 MW simple-cycle combustion turbine (General Electric Frame 7FA), with a 60-foot exhaust stack.  These emissions units began operations in 2002.  Natural gas is the primary fuel, with low-sulfur distillate fuel oil as the back-up fuel.  NOX emissions are controlled by dry low NOX (DLN) combustors when firing natural gas, and a water injection (WI) system for use when firing No. 2, or superior grade, distillate fuel oil.  All stationary combustion turbines, ducting, and stacks are designed so as to not preclude installation of SCR equipment and/or oxidation catalyst equipment in the event of a failure to achieve the NOX limits given in Specific Conditions A.7., and/or the carbon monoxide (CO) limits given in Specific Condition A.8.

{Permitting notes:  These emissions units are regulated under Acid Rain-Phase II, 40 CFR 60, Subpart GG, Standards of Performance for Stationary Gas Turbines, adopted by reference in Rule 62-204.800(8)(b), F.A.C., Rule 212.400, F.A.C., Prevention of Significant Deterioration (PSD), Best Available Control Technology (BACT), and Air Construction Permit PSD-FL-258 (0090180-001-AC).}

Essential Potential to Emit (PTE) Parameters

- Permitted Capacity.  The maximum allowable heat input rate rates, based on the lower heating value (LHV) of each fuel to each unit at ambient conditions of 59° F temperature, 60% relative humidity, 100% load, and 14.7 psi pressure shall not exceed as follows:

| Unit No. | MMBtu/hr Heat Input | Fuel Type |
| --- | --- | --- |
| 001, 002, 003, 004 | 1,722 million Btu per hour (MMBtu/hr) | Natural Gas |
|  | 1,919 MMBtu/hr | No. 2 or superior grade of distillate fuel oil |

These maximum heat input rates will vary depending upon ambient conditions and the combustion turbine characteristics.  Manufacturer’s curves, corrected for site conditions, or equations for correction to other ambient conditions, shall be provided to the Department of Environmental Protection (DEP) within 45 days of completing any compliance testing or combustor tuning that changes the curves.  [Rules 62-4.160(2), 62-204.800, 62-210.200(PTE), F.A.C.; and, Permit No. 0090180-001-AC.]

- Emissions Unit Operating Rate Limitation After Testing.  See the related testing provisions in Appendix TR, Facility-wide Testing Requirements.  [Rule 62-297.310(2), F.A.C.]

- Methods of Operation - Fuels.  Only pipeline natural gas containing a maximum of 1 grain of sulfur per 100 standard cubic feet or fuel oil containing a maximum of 0.05 percent sulfur, by weight, No. 2, or superior grade, of distillate fuel oil shall be fired in these units.

a.	Natural Gas.  Fuel usage as heat input, while burning natural gas at the site, shall not exceed 29.188 x 1012 Btu (LHV) per year, during any consecutive 12-month period.

b.	Fuel Oil.  Fuel usage as heat input, while burning fuel oil at the site, shall not exceed 9.595 x 1012 Btu (LHV) per year during any consecutive 12-month period.  Additionally, the amount of fuel oil burned at the site (in Btu’s) shall not exceed natural gas burned at the site (in Btu’s) during any consecutive 12-month period.

[Permit No. 0090180-001-AC, Specific Conditions 14. & 15.]

- Hours of Operation.  Each stationary gas turbine shall only operate up to 3390 hours during any calendar year.  [Rule 62-210.200, F.A.C. (Definitions - Potential Emissions); and 0090180-001-AC, Specific Condition 13.]

Control Technology

- DLN Systems.  The DLN systems shall each be tuned to optimize emissions reductions and shall be maintained to minimize NOX emissions and CO emissions.  Operation of the DLN systems in the diffusion-firing mode shall be minimized when firing natural gas.  [Rules 62-4.070, and 62-210.650, F.A.C.; and 0090180-001-AC, Specific Condition 19.]

Emission Limitations and Standards

Unless otherwise specified, the averaging times for Specific Conditions A.6. - A.10. are based on the specified averaging time of the applicable test method.

- Visible emissions (VE).  VE emissions shall not exceed 10 percent opacity when firing natural gas or No. 2 or superior grade of fuel oil, except for during startup and shutdown at which time emissions shall not exceed 20 percent opacity.  [Rule 62-296.320(4)(b), F.A.C.; and 0090180-001-AC, Specific Condition 24.]

- NOX Emissions.

a.	NOX CEMS Substitution Data.  When NOX monitoring data are not available, substitution for missing data shall be handled as required by Title IV (40 CFR 75) to calculate any specified average time.

b.	While firing Natural Gas.  The emission rate of NOX in the exhaust gas shall not exceed 62.6 lb/hr (at ISO conditions) on a 24-hr block average, as measured by the continuous emission monitoring system (CEMS).  In addition, NOX emissions calculated as NO2 (at ISO conditions) shall not exceed 9 ppmvd @15% O2 to be demonstrated by annual stack test.  Note:  Basis for lb/hr limit is 9 ppmvd @ 15% O2, full load.

c.	While firing Fuel oil.  The concentration of NOX in the exhaust gas shall not exceed 42 ppmvd at 15% O2 on the basis of a 3-hr average as measured by the continuous emission monitoring system (CEMS).  In addition, NOX emissions calculated as NO2 (at ISO conditions) shall not exceed 42 ppmvd @15% O2 to be demonstrated by stack test.

[Rule 62-212.400, F.A.C.; and 0090180-001-AC, Specific Condition 21.]

- Carbon Monoxide (CO).  The concentration of CO in the exhaust gas when firing natural gas shall not exceed 12 ppmvd when firing natural gas and 20 ppmvd when firing fuel oil, as measured by EPA Method 10.  CO emissions (at ISO conditions) shall not exceed 41.0 lb/hr (when firing natural gas) and 66.9 lb/hr (when firing fuel oil) as indicated by EPA Method 10.  [Rule 62-212.400, F.A.C.; and 0090180-001-AC, Specific Condition 22.]

- Sulfur Dioxide (SO2).  SO2 emissions (at ISO conditions) shall not exceed 5.5 pounds per hour when firing pipeline natural gas, and 103.4 pounds per hour when firing maximum 0.05 percent sulfur, by weight, No. 2 or superior grade distillate fuel oil, as measured by applicable compliance methods described below (see Specific Condition A.27.).  [Rule 62-212.400, F.A.C.; and 0090180-001-AC, Specific Condition 23.]

- Volatile Organic Compounds (VOC) Emissions.  The concentration of VOC in the exhaust gas when firing natural gas shall not exceed 3 ppmvd when firing natural gas and 6 ppmvd when firing fuel oil as assured by EPA Methods 18, and/or 25 A.  VOC emissions (at ISO conditions) shall not exceed 5.9 lb/hr (when firing natural gas) and 11.5 lb/hr (when firing fuel oil).  See Specific Condition A.29.  [Rule 62-212.400, F.A.C.; and 0090180-001-AC, Specific Condition 25.]

Excess Emissions

Rule 62-210.700 (Excess Emissions), F.A.C. cannot vary any requirement of an NSPS, NESHAP or Acid Rain program provision.

- Excess Emissions Allowed.  Excess emissions resulting from startup, shutdown, or malfunction shall be permitted provided that best operational practices are adhered to and the duration of excess emissions shall be minimized, but in no case exceed two hours in any 24-hour period for other reasons, unless specifically authorized by the Department for longer duration.  Operation below 50% output shall be limited to 2 hours per unit cycle (breaker closed to breaker open).  Excess emissions caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure that may reasonably be prevented during startup, shutdown or malfunction, shall be prohibited pursuant to Rule 62-210.700, F.A.C.  [Rule 62-210.700(1), F.A.C.; and 0090180-001-AC, Specific Condition 26.]

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C.]

Monitoring of Operations

- Operational Procedures.  At all times, including periods of startup, shutdown and 	malfunction, owners and operators shall, to the extent practicable, maintain and operate any affected facility including associated pollution control equipment in a manner consistent with good air pollution control practice for minimizing emissions.  Determination of whether acceptable operating and maintenance procedures are being used will be based on information available to the Administrator which may include, but is not limited to, monitoring results, opacity observations, review of operating and maintenance procedures, and inspection of the source.  [40 CFR 60.11(d)]

- Water-to-Fuel Monitoring.  The owner or operator of any stationary gas turbine subject to the provisions of 40 CFR 60, Subpart GG and using water injection to control NOX emissions shall install and operate a continuous monitoring system (CMS) to monitor and record the fuel consumption and the ratio of water to fuel being fired in the turbine.  This system shall be accurate to within +5.0 percent and shall be approved by the Administrator.  [40 CFR 60.334(a)]

- Fuel Content Monitoring.  The owner or operator of any stationary gas turbine subject to the provisions of 40 CFR 60, Subpart GG shall monitor sulfur content and nitrogen content of the fuel being fired in the turbine.  Please see Specific Conditions A.16. and A.17.  [40 CFR 60.334(b)]

- Fuel Oil Monitoring Schedule.  The following monitoring schedule for No. 2 or superior grade fuel oil shall be followed: For all bulk shipments of No. 2 or superior grade fuel oil received at the Oleander Power Project, an analysis which reports the sulfur content and nitrogen content of the fuel shall be provided by the fuel vendor.  The analysis shall also specify the methods by which the analyses were conducted and shall comply with the requirements of 40 CFR 60.335(d).  [0090180-001-AC, Specific Condition 44.]

- Natural Gas Monitoring Schedule.  The following custom monitoring schedule for natural gas is approved (pending EPA concurrence) in lieu of the daily sampling requirements of 40 CFR 60.334 (b)(2):

a.	The permittee shall apply for an Acid Rain permit in compliance with the deadlines specified in 40 CFR 72.30.  See Section IV, the Acid Rain Part of this permit.

b.	The permittee shall submit a monitoring plan, certified by signature of the Designated Representative that commits to using a primary fuel of pipeline-supplied natural gas (sulfur content less than 1 grain per 100 standard cubic feet, pursuant of 40 CFR 75.11 and 75 Appendix D.).  See Specific Condition A.9.

c.	Each unit shall be monitored for SO2 emissions using methods consistent with the requirements of 40 CFR 75 and certified by the USEPA.

d.		Oleander Power Project, L.P., shall notify DEP of any change in natural gas supply for reexamination of this monitoring schedule.  A substantial change in natural gas quality (i.e., sulfur content variation of greater than 1 grain per 100 standard cubic feet of natural gas) shall be considered as a change in the natural gas supply.  Sulfur content of the natural gas will be monitored weekly by the natural gas 	supplier during the interim period when this monitoring schedule is being reexamined.

[0090180-001-AC, Specific Condition 45.]

Continuous Emissions Monitoring Requirements

- Continuous Monitoring System.  The permittee shall install, calibrate, maintain, and operate a continuous emission monitor in the stack to measure and record the nitrogen oxides emissions from each CT unit.  Periods when NOX emissions are above the standards as listed in Specific Condition A.7. shall be reported to the DEP Central District Office pursuant to Rule 62-4.160(8), F.A.C.  Following the format of 40 CFR 60.7, periods of startup, shutdown, malfunction, and fuel switching shall be monitored, recorded, and reported as excess emissions when emission levels exceed the standards listed in Specific Condition A.7., except as noted in Specific Condition A.26.  [Rule 62-204.800; 40 CFR 60.7 (1997 version); and 0090180-001-AC, Specific Condition 41.]

- CEMS in lieu of Water to Fuel Ratio.  The NOX CEMS shall be used in lieu of the water/fuel monitoring system for reporting excess emissions in accordance with 40 CFR 60.334(c)(1), Subpart GG (1997 version).  The calibration of the water/fuel-monitoring device required in 40 CFR 60.335 (c)(2) (1997 version) will be replaced by the 40 CFR 75 certification tests of the NOX CEMS.  Upon request from DEP, the CEMS emission rates for NOX shall be corrected to ISO conditions to demonstrate compliance with the NOX standard established in 40 CFR 60.332.  [0090180-001-AC, Specific Condition 42.]

Test Methods and Procedures

- Test Methods.  Required tests shall be performed in accordance with the following reference methods:

| Method | Description of Method and Comments |
| --- | --- |
| 7E | Determination of Nitrogen Oxide Emissions from Stationary Sources (or RATA test data) |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |
| 10 | Determination of Carbon Monoxide Emissions from Stationary Sources |
| 18 | Measurement of Gaseous Organic Compound Emissions by Gas Chromatography |
| 25A | Method for Determining Gaseous Organic Concentrations (Flame Ionization) |

The above methods are described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [0090180-001-AC, Specific Condition 29.]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- Annual Compliance Tests.  During each federal fiscal year (October 1st to September 30th), each EU shall be tested to demonstrate compliance with the emissions standards for NOX, VE, and CO.  If normal operation on fuel oil is less than 400 hours per calendar year, then subsequent compliance testing (annual or renewal) on fuel oil is not required for that year.  If data collected from the reference method during the required CEMS quality assurance RATA test are substituted for annual or renewal compliance tests for NOX, then no separate annual or renewal compliance testing for the fuel fired while conducting the CEMS quality assurance RATA test shall be required.  Unless specifically requested by the Compliance Authority pursuant to Rule 62-297.310(7)(b), F.A.C., periodic opacity tests are not required when firing natural gas.  [Rule 62-297.310(7), F.A.C. and 0090180-007-AC.]

- Compliance Tests Prior To Permit Renewal.  The owner or operator shall conduct testing to demonstrate compliance with the emissions standards for NOX, VE, and CO emissions prior to renewal of the facility’s Title V Air Operation Permit.  See Specific Condition TR.7.  If normal operation on fuel oil is less than 400 hours per calendar year, then subsequent compliance testing (annual or renewal) on fuel oil is not required for that year.  If data collected from the reference method during the required CEMS quality assurance RATA test are substituted for annual or renewal compliance tests for NOX, then no separate annual or renewal compliance testing for the fuel fired while conducting the CEMS quality assurance RATA test shall be required.  [Rule 62-297.310(7), F.A.C. and 0090180-007-AC.]

{Permitting Note:  Tests which are only required once during the term of a permit prior to obtaining a renewed permit should be performed roughly five years from the previous test.}

- Computation of NOX Emissions.  To compute the nitrogen oxides emissions, the owner or operator shall use analytical methods and procedures that are accurate to within 5 percent and are approved by the Department to determine the nitrogen content of the fuel being fired.  [40 CFR 60.335(a)]

- For purposes of demonstrating compliance with NSPS - 40 CFR 60, Subpart GG.  The monitoring device of 40 CFR 60.334(a) shall be used to determine the fuel consumption and the water-to-fuel ratio necessary to comply with the permitted NOX standard at 30, 50, 75, and 100 percent of peak load or at four points in the normal operating range of the gas turbine, including the minimum point in the range and peak load.  All loads shall be corrected to ISO conditions using the appropriate equations supplied by the manufacturer.  [40 CFR 60.335(c)(2)]

- Continuous compliance with the NOX emission limits.  Continuous compliance with the NOX emission limits shall be demonstrated with the CEM system based on the applicable averaging time of 24-hr block average (DLN technology).  For the 24-hr block average (lb/hr) emissions may be determined via EPA Method 19 or equivalent EPA approved methods.  Based on CEMS data, a separate compliance determination shall be conducted at the end of each operating day and a new average emission rate shall be calculated from the arithmetic average of all valid hourly emission rates from the previous operating day.  Valid hourly emission rates shall not include periods of startup, shutdown, or malfunction as defined in Rule 62-210.200 F.A.C., where emissions exceed the applicable NOX standard.  These excess emissions periods shall be reported as required in Specific Conditions A.11. and A.37.  A valid hourly emission rate shall be calculated for each hour in which at least two NOX concentrations are obtained at least 15 minutes apart.  [Rules 62-4.070 and 62-210.700, F.A.C.; 40 CFR 75; and 090180-001-AC, Specific Condition 30.]

- Compliance with the SO2 and PM/PM10 emission limits.  Notwithstanding the requirements of Rule 62-297.310(7), F.A.C., the use of pipeline natural gas and No. 2 or superior grade distillate fuel oil with a maximum 0.05 percent sulfur, by weight, is the method for determining compliance for SO2 and PM10.  For the purposes of demonstrating compliance with the 40 CFR 60.333 SO2 standard and the 0.05% sulfur, by weight, limit, fuel oil analysis using ASTM D2880-941 or D4294-90 (or equivalent latest version) for the sulfur content of liquid fuels and D1072-80, D3031-81, D4084-82 or D3246-81 (or equivalent latest version) for sulfur content of gaseous fuel shall be utilized in accordance with the EPA-approved custom fuel monitoring schedule.  The applicant is responsible for ensuring that the procedures above are used for determination of fuel sulfur content.  Analysis may be performed by the owner or operator, a service contractor retained by the owner or operator, the fuel vendor, or any other qualified agency pursuant to 40 CFR 60.335(e) (1997 version).  [0090180-001-AC, Specific Condition 31.]

- Compliance with the CO emission limit.  Annual compliance testing for CO may be conducted concurrent with the annual RATA testing for NOX required pursuant to 40 CFR 75 and is required for gas only.  Such annual compliance test may be used for CO renewal test requirements, and is required for gas only.   [0090180-001-AC, Specific Condition 32. and 0090180-007-AC.]

- Compliance with the VOC emission limit.  The CO emission limit shall be employed as surrogate, and no annual or renewal testing for VOC is required.  [0090180-001-AC, Specific Condition 33. and 0090180-007-AC.]

Recordkeeping and Reporting Requirements

- Reporting Schedule.  The following reports and notifications shall be submitted to the Compliance Authority:

| Report | Reporting Deadline | Related Condition(s) |
| --- | --- | --- |
| Fuel Usage as heat input for natural gas and fuel oil at the site | Monthly | A.36.a |
| Fuel usage as heat input for natural gas and fuel oil at the site | Each consecutive 12 month period | A.36.b |
| Fuel usage as heat input for natural gas and fuel oil at the site | Each calendar year; submit along with the Annual Operating Report (AOR) | RR5, A.36.c |
| Hours of Operation for each combustion turbine | Each Calendar year; submit along with the AOR | RR5, A.36.d |

[0090180-001-AC, Specific Condition 40.]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440(1)(b), F.A.C.]

- Special Record Keeping Requirements.  The owner or operator shall obtain, make, and keep the following records related to fuel usage:

a.	Monthly Fuel usage as heat input, for natural gas and fuel oil at the site.

b.	Fuel usage as heat input, for natural gas and fuel oil at the site for each consecutive 12-month period.

c.	Fuel usage as heat input, for natural gas and fuel oil at the site during each calendar year shall be submitted with the Annual Operation Report (AOR).

d.	Hours of operation for each combustion turbine shall be reported during each calendar year with the Annual Operation Report (AOR).

[0090180-001-AC, Specific Condition 40.]

- Reporting Requirements.  The owner or operator required to install a continuous monitoring system (CMS) or monitoring device shall submit an excess emissions and monitoring systems performance report (excess emissions are defined in applicable subparts) and/or a summary report form [see 40 CFR 60.7(d)] to the Administrator semiannually, except when:  more frequent reporting is specifically required by an applicable subpart; or, the CMS data are to be used directly for compliance determination, in which case quarterly reports shall be submitted; or, the Administrator, on a case-by-case basis, determines that more frequent reporting is necessary to accurately assess the compliance status of the source.  All reports shall be postmarked by the 30th day following the end of each calendar half (or quarter, as appropriate).  Written reports of excess emissions shall include the following information:

a.	The magnitude of excess emissions computed in accordance with 40 CFR 60.13(h), any conversion factor(s) used, and the date and time of commencement and completion of each time period of excess emissions.  The process operating time during the reporting period.

b.	Specific identification of each period of excess emissions that occurs during startups, shutdowns, and malfunctions of the affected facility.  The nature and cause of any malfunction (if known), the corrective action taken or preventative measures adopted.

c.	The date and time identifying each period during which the continuous monitoring system was inoperative except for zero and span checks and the nature of the system repairs or adjustments.

d.	When no excess emissions have occurred or the continuous monitoring system(s) have not been inoperative, repaired, or adjusted, such information shall be stated in the report.

[40 CFR 60.7(c)(1), (2), (3), and (4).]

- Malfunction Reporting.  If excess emissions occur due to malfunction, the owner or operator shall notify DEP’s Central District Office within (1) working day of:  (A) the nature, extent, and duration of the excess emissions, (B) the cause of the excess emissions, and (C) the actions taken to correct the problem.  In addition, the Department may request a written summary report of the incident.  Pursuant to the New Source Performance Standards, excess emissions shall also be reported in accordance with 40 CFR 60.7, Subpart A.  [Rules 62-4.130 and 62-210.700(6), F.A.C.; and 0090180-001-AC, Specific Condition 27.]

- Excess Emissions Summary Report.  The summary report form shall contain the information and be in the format shown in Figure 1 Summary Report-Gaseous and Opacity Excess Emission and Monitoring System Performance (attached) unless otherwise specified by the Administrator.  One summary report form shall be submitted for each pollutant monitored at each affected facility.

a.	If the total duration of excess emissions for the reporting period is less than 1 percent of the total operating time for the reporting period and CMS downtime for the reporting period is less than 5 percent of the total operating time for the reporting period, only the summary report form shall be submitted and the excess emission report described in 40 CFR 60.7(c) need not be submitted unless requested by the Administrator.

b.	If the total duration of excess emissions for the reporting period is 1 percent or greater of the total operating time for the reporting period or the total CMS downtime for the reporting period is 5 percent or greater of the total operating time for the reporting period, the summary report form and the excess emission report described in 40 CFR 60.7(c) shall both be submitted.

[40 CFR 60.7(d)(1) and (2).]

- Excess Emissions Reports.

a.	Notwithstanding the frequency of reporting requirements specified in 40 CFR 60.7(c), an owner or operator who is required by an applicable subpart to submit excess emissions and monitoring systems performance reports (and summary reports) on a quarterly (or more frequent) basis may reduce the frequency of reporting for that standard to semiannual if the following conditions are met:

(1)	For 1 full year (e.g., 4 quarterly or 12 monthly reporting periods) the affected facility’s excess emissions and monitoring systems reports submitted to comply with a standard under this part continually demonstrate that the facility is in compliance with the applicable standard;

(2)	The owner or operator continues to comply with all recordkeeping and monitoring requirements specified in 40 CFR 60, Subpart A, and the applicable standard; and

(3)	The Administrator does not object to a reduced frequency of reporting for the affected facility, as provided in 40 CFR 60.7(e)(2).

b.	The frequency of reporting of excess emissions and monitoring systems performance (and summary) reports may be reduced only after the owner or operator notifies the Administrator in writing of his or her intention to make such a change and the Administrator does not object to the intended change.  In deciding whether to approve a reduced frequency of reporting, the Administrator may review information concerning the source’s entire previous performance history during the required recordkeeping period prior to the intended change, including performance test results, monitoring data, and evaluations of an owner or operator’s conformance with operation and maintenance requirements.  Such information may be used by the Administrator to make a judgment about the source’s potential for noncompliance in the future.  If the Administrator disapproves the owner or operator’s request to reduce the frequency of reporting, the Administrator will notify the owner or operator in writing within 45 days after receiving notice of the owner or operator’s intention.  The notification from the Administrator to the owner or operator will specify the grounds on which the disapproval is based.  In the absence of a notice of disapproval within 45 days, approval is automatically granted.

c.	As soon as monitoring data indicate that the affected facility is not in compliance with any emission limitation or operating parameter specified in the applicable standard, the frequency of reporting shall revert to the frequency specified in the applicable standard, and the owner or operator shall submit an excess emissions and monitoring systems performance report (and summary report, if required) at the next appropriate reporting period following the noncomplying event.  After demonstrating compliance with the applicable standard for another full year, the owner or operator may again request approval from the Administrator to reduce the frequency of reporting for that standard as provided for in 40 CFR 60.7(e)(1) and (e)(2).

[40 CFR 60.7(e).]

- Continuous Monitoring System Reports.  The monitoring devices shall comply with the certification and quality assurance, and any other applicable requirements of 40 CFR 60.13, including certification of each device in accordance with 40 CFR 60, Appendix B, Performance Specifications and 40 CFR 60.7(a)(5) or 40 CFR Part 75.  Quality assurance procedures must conform to all applicable sections of 40 CFR 60, Appendix F or 40 CFR 75.  Data on CEM equipment specifications, manufacturer, type, calibration and maintenance needs, and its proposed location shall be provided to the Department’s Central District Office for review at least 90 days prior to installation.  [0090180-001-AC, Specific Condition 43.]

- Record Retention.  Any owner or operator subject to the provisions of 40 CFR 60 shall maintain a file of all measurements, including continuous monitoring system, monitoring device, and performance testing measurements; all continuous monitoring system performance evaluations; all continuous monitoring system or monitoring device calibration checks; adjustments and maintenance performed on these systems or devices; and, all other information required by 40 CFR 60 recorded in a permanent form suitable for inspection.  The file shall be retained for at least 5 (five) years following the date of such measurements, maintenance, reports, and records.  [40 CFR 60.7(f); and Rule 62-213.440(1)(b)2.b., F.A.C.]

Other Requirements

- Operating Procedures.  Operating procedures shall include good operating practices and proper training of all operators and supervisors.  The good operating practices shall meet the guidelines and procedures as established by the equipment manufacturers.  All operators (including supervisors) of air pollution control devices shall be properly trained in plant specific equipment.  [0090180-001-AC, Specific Condition 11.]

- Compliance With NSPS Requirements.  These emission units are also subject to the terms and conditions contained in the attached Appendix NSPS, Subpart GG and NSPS, Subpart A.  Compliance with the requirements listed above will ensure compliance with the NSPS requirements.  [40 CFR 60.330 and Rule 62.213.440(1), F.A.C.]

The specific conditions in this section apply to the following emissions unit:

| EU No. | Brief Description |  |
| --- | --- | --- |
| -005 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |

This emissions unit is comprised of a nominal 190 MW simple-cycle combustion turbine General Electric PG7241 FA, with a 60-foot exhaust stack.  The emissions unit began operations in 2007.  The combustion turbine is equipped with GE’s DLN combustor, and an inlet air filtration system with evaporative coolers.  The combustion turbine is designed for operation in simple cycle mode and has dual-fuel capability.  Natural gas is the primary fuel, with low-sulfur distillate fuel oil as the back-up fuel.  NOX emissions are controlled by dry low NOX (DLN) combustors when firing natural gas, and a water injection (WI) system for use when firing No. 2, or superior grade, distillate fuel oil.

{Permitting note:  These emissions units are regulated under Acid Rain-Phase II, 40 CFR 60, Subpart KKKK, Standards of Performance for Stationary Gas Turbines, adopted by reference in Rule 62-204.800(8)(b), F.A.C., Rule 212.400, F.A.C., Prevention of Significant Deterioration (PSD), Best Available Control Technology (BACT), and Air Construction Permit PSD-FL-377 (0090180-003-AC).}

Essential Potential to Emit (PTE) Parameters

- Permitted Capacity.  The nominal heat input rates are as follows:

| Unit No. | MMBtu/hr Heat Input (or other regulated capacity) | Fuel Type |
| --- | --- | --- |
| 005 | 1,722 | Natural gas |
|  | 1,920 | Fuel oil |

Heat input rates will vary depending upon gas turbine characteristics, ambient conditions, alternate methods of operation, and evaporative cooling.  The permittee shall provide manufacturer’s performance curves (or equations) that correct for site conditions to the Permitting and Compliance Authorities within 45 days of completing any compliance testing or combustor tuning that changes the curves.  Operating data may be adjusted for the appropriate site conditions in accordance with the performance curves and/or equations on file with the Department.  [Rules 62-4.160(2), 62-204.800, 62-210.200(PTE) & 62-213.440(1), F.A.C.; and, Permit No. 0090180-003-AC.]

- Emissions Unit Operating Rate Limitation After Testing.  See the related testing provisions in Appendix TR, Facility-wide Testing Requirements.  [Rule 62-297.310(2), F.A.C.]

- Methods of Operation.

a.	Fuels.  The fuels that are allowed to be burned in this unit are natural gas as the primary fuel, which shall contain no more than 1.5 grains of sulfur per 100 standard cubic feet of natural gas.  As a restricted alternate fuel, the combustion turbine may fire low sulfur fuel oil containing no more than 0.05% sulfur by weight.  The gas turbine shall fire no more than 500 hours of fuel oil, during any calendar year.

b.	Simple Cycle, Intermittent Operation.  The turbine shall operate only in simple cycle mode not to exceed the permitted hours of operation allowed by this permit.  This restriction is based on the permittee’s request, which formed the basis of the PSD applicability and BACT determination and resulted in the emission standards specified in this permit.  For any request to convert this unit to combined cycle operation by installing/connecting to heat recovery steam generators, including changes to the fuel quality or quantity related to combined cycle conversion which may cause an increase in short or long-term emissions, the permittee may be required to submit a full PSD permit application complete with a new proposal of the best available control technology as if the unit had never been built.

[Permit No. 0090180-003-AC, Specific Conditions 8 and 9.]

- Hours of Operation.  The combustion turbine may operate no more than 3,390 hours per calendar year.  Restrictions on individual methods of operation are specified in separate conditions.  [Rule 62-210.200(PTE), F.A.C., Permit No. 0090180-003-AC, Specific Condition 6.]

Control Technology

- DLN Combustion.  The permittee shall operate and maintain the General Electric DLN 2.6 combustion system (or better) to control NOX emissions from the combustion turbine when firing natural gas.  The DLN combustors and automated gas turbine control system shall be maintained and tuned in accordance with the manufacturer’s recommendations or determined best practices to achieve the permitted levels for NOX.  [Permit No. 0090180-003-AC.]

Emission Limitations and Standards

Unless otherwise specified, the averaging times for Specific Conditions B.5. – B.8. are based on the specified averaging time of the applicable test method.

- Nitrogen Oxides (NOX).  Emissions of NOX from the CT shall not exceed the following standards on a continuous basis and as measured by the required CEMS for the averaging period specified, and as measured during the required stack tests.

  - While firing natural gas.  9.0 ppmvd @ 15% O2 on a 24-hour rolling average as measured by the required CEMS and defined by this permit.

- While firing fuel oil.  42.0 ppmvd @ 15% O2 on a 4-hr rolling average as measured by the required CEMS and defined by subpart KKKK attached as an Appendix to this permit.

[Rules 40 CFR 60.4380; and, 0090180-003-AC, Specific Condition 11. and 0090180-007-AC.]

- Sulfur Dioxide (SO2).

- While firing natural gas.  The fuel sulfur specifications, established in Specific Condition B.2. of this subsection, of 1.5 grains per 100 standard cubic feet effectively limit the potential emissions of SO2 from the combustion turbine while firing natural gas.

- While firing fuel oil.  The fuel sulfur specification, established in Specific Condition B.2. of this subsection, of 0.05 % sulfur by weight effectively limit the potential emissions of SO2 from the combustion turbine while firing fuel oil.

[Rules 62-4.070(3) and 62-212.400 (PSD Avoidance), F.A.C.]

- Particulate Matter (PM/PM10) Emissions.  The fuel sulfur specifications, established in Specific Condition B.2. of this subsection, combined with the efficient combustion, design, and operation of the combustion turbine represent BACT for PM/PM10 emissions.  Compliance with the fuel specifications and visible emissions standard shall serve as indicators of good combustion.  [Rules 62-4.070(3), 62-210.200 (BACT), 62-212.400(PSD)& 62-297.310(4)(a)2, F.A.C.; and, Permit No. 0090180-003-AC]

- Visible Emissions.  Visible emissions shall not exceed 10 % opacity as observed during the required 30-minute visible emissions tests.  [Rules 62-4.070(3), 62-210.200 (BACT), 62-212.400(PSD)& 62-297.310(4)(a)2, F.A.C.; and, Permit No. 0090180-003-AC.]

{Permitting Note:  In combination with the annual restriction on hours of operation, the above emissions standards effectively limit annual potential emissions from the combustion turbine to:  174.5 tons/year of NOX,, 34.5 tons/year of PM/PM10, and 37.1 tons/year of SO2.}

Excess Emissions

Rule 62-210.700 (Excess Emissions), F.A.C. cannot vary any requirement of an NSPS, NESHAP or Acid Rain program provision.

{Permitting Note:  The following conditions apply only to the SIP-based emissions standards of this subsection.}

- Definitions.

    - Startup is defined as the commencement of operation of any emissions unit which has shut down or ceased operation for a period of time sufficient to cause temperature, pressure, chemical or pollution control device imbalances, which result in excess emissions.

    - Shutdown is the cessation of the operation of an emissions unit for any purpose.

    - Malfunction is defined as any unavoidable mechanical and/or electrical failure of air pollution control equipment or process equipment or of a process resulting in operation in an abnormal or unusual manner.

[Rule 62-210.200(165, 242, and 258), F.A.C. and Permit No. 0090180-003-AC.]

- Excess Emissions Prohibited.  Excess emissions caused entirely or in part by poor maintenance, poor operation or any other equipment or process failure that may reasonably be prevented during startup, shutdown or malfunction shall be prohibited.  All such preventable emissions shall be included in any compliance determinations based on CEMS data.  [Rule 62-210.700(4), F.A.C. and Permit No. 0090180-003-AC.]

- Data Exclusion Procedures for SIP Compliance.  As per the procedures in this condition, limited amounts of CEMS emissions data, as specified in Specific Condition B.12., may be excluded from the corresponding SIP-based compliance demonstration, provided that best operational practices to minimize emissions are adhered to, the duration of data excluded is minimized, and the procedures for data exclusion listed below are followed.  As provided by the authority in Rule 62-210.700(5), F.A.C., these conditions replace the provisions in Rule 62-210.700(1), F.A.C.

- Limiting Data Exclusion.  If the compliance calculation using all valid CEMS emission data indicates that the emission unit is in compliance, then no CEMS data shall be excluded from the compliance demonstration.

- Event Driven Exclusion.  There must be an underlying event (startup, shutdown, malfunction, or fuel switching) in order to exclude data.  If there is no underlying event, then no data may be excluded.

- Continuous Exclusion.  Data shall be excluded on a continuous basis.  Data from discontinuous periods shall not be excluded for the same underlying event.

[Rule 62-210.700(5) F.A.C. and Permit No. 0090180-003-AC.]

- Allowable Data Exclusions.  The following data may be excluded from the corresponding SIP-based compliance demonstration for each of the events listed below in accordance with the Data Exclusion Procedures listed below:

- Startup.  Up to 30 minutes of CEMS data may be excluded for each combustion turbine startup.  For startups of less than 30 minutes in duration, only those minutes attributable to startup may be excluded.

- Shutdown.  Up to 30 minutes of CEMS data may be excluded for each combustion turbine shutdown.  For shutdowns of less than 30 minutes in duration, only those minutes attributable to shutdown may be excluded.

- Malfunction.  Up to two hours (in any operating day) of CEMS data may be excluded due to a documented malfunction.  A “documented malfunction” means a malfunction that is documented within one working day of detection by contacting the Compliance Authority by telephone, facsimile transmittal, or electronic email.

- DLN Tuning.  CEMS data collected during initial or other DLN tuning sessions may be excluded from the compliance demonstrations provided the tuning session is performed in accordance with the manufacturer’s specifications or determined best practices.  Prior to performing any tuning session, the permittee shall provide the Compliance Authority with an advance notice of at least one (1) day that details the activity and proposed tuning schedule.  The notice may be by telephone, facsimile transmittal, or electronic mail.  [Design; Rule 62-4.070(3), F.A.C.]

- Fuel Switching.  Up to 60 minutes of CEMS data may be excluded for each fuel switch.  For fuel switches of less than 60 minutes in duration, only those minutes attributable to fuel switching may be excluded.

All valid emissions data (including data collected during startup, shutdown, malfunction, DLN tuning, and fuel switching) shall be used to report emissions for the Annual Operating Report.

[Rules 62-210.200(BACT), 62-210.370, & 62-210.700, F.A.C.; and, Permit No. 0090180-003-AC.]

Continuous Emissions Monitoring Requirements

- CEM Systems.  Subject to the following, the permittee shall install, calibrate, operate, and maintain a continuous emission monitoring system (CEMS) to measure and record the emissions of NOX from the combustion turbine in terms of the applicable standards.  The monitoring system shall be installed, and functioning within the required performance specifications by the time of the initial compliance demonstration.

- NOX Monitor.  Each NOX monitor shall be certified pursuant to the specifications of 40 CFR 75.  Quality assurance procedures shall conform to the requirements of 40 CFR 75.  The annual and required RATA tests required for the NOX monitor shall be performed using EPA Method 20 or 7E in Appendix A of 40 CFR 60.

- Diluent Monitor.  The oxygen (O2) or carbon dioxide (CO2) content of the flue gas shall be monitored at the location where NOX is monitored to correct the measured emissions rates to 15% oxygen.  If a CO2 monitor is installed, the oxygen content of the flue gas shall be calculated using F-factors that are appropriate for the fuel fired.  Each monitor shall comply with the performance and quality assurance requirements of 40 CFR 75.

[Rules 62-4.070(3), 62-210.200(BACT), F.A.C.; 40 CFR 60, Subpart 75; and, Permit No. 0090180-003-AC.]

- Moisture Correction.  If necessary, the owner or operator shall determine the moisture content of the exhaust gas and develop an algorithm to enable correction of the monitoring results to a dry basis (0% moisture).  [Rules 62-4.070(3) & 62-210.200(BACT), F.A.C.; and, Permit No. 0090180-003-AC.]

- CEMS Data Requirements for BACT Standards.

{Permitting Note:  The following conditions apply only to the SIP-based NOX emissions standards of this section.  These requirements cannot vary or supersede any federal provision of the NSPS, or Acid Rain programs.  Additional reporting and monitoring may be required by the individual subparts.}

- Data Collection.  Except for continuous monitoring system breakdowns, repairs, calibration checks, and zero and span adjustments, emissions shall be monitored and recorded during all operation including startup, shutdown, and malfunction.

- Operating Hours and Operating Days.  An hour is the 60-minute period beginning at the top of each hour.  Any hour during which an emissions unit is in operation for more than 15 minutes is an operating hour for that emission unit.  A day is the 24-hour period from midnight to midnight.  Any day with at least one operating hour for an emissions unit is an operating day for that emission unit.

- Valid Hour.  Each CEMS shall be designed and operated to sample, analyze, and record data evenly spaced over the hour at a minimum of one measurement per minute.  All valid measurements collected during an hour shall be used to calculate a 1-hour block average that begins at the top of each hour.

  - Hours that are not operating hours are not valid hours.

  - For each operating hour, the 1-hour block average shall be computed from at least two data points separated by a minimum of 15 minutes.  If less than two such data points are available, there is insufficient data and the 1-hour block average is not valid.

  - During fuel switching an hour in which fuel oil is fired is attributed towards compliance with the permit standards for oil firing.

- Rolling 24-Hour Average.  Compliance shall be determined after each valid hourly average is obtained by calculating the arithmetic average of that valid hourly average and the preceding 23 valid hourly averages.

- Data Exclusion.  Each CEMS shall monitor and record emissions during all operations including episodes of startup, shutdown, malfunction, DLN tuning, and fuel switches.  Some of the CEMS emissions data recorded during these episodes may be excluded from the corresponding CEMS compliance demonstration subject to the provisions of Specific Conditions B.11. and B.12. of this subsection.

- Availability.  The quarterly excess emissions report shall identify monitor availability for each quarter in which the unit operated.  Monitor availability for the CEMS shall be 95% or greater in any calendar quarter in which the unit operated for more than 760 hours.  In the event the applicable availability is not achieved, the permittee shall provide the Department with a report identifying the problems in achieving the required availability and a plan of corrective actions that will be taken to achieve 95% availability.  The permittee shall implement the reported corrective actions within the next calendar quarter.  Failure to take corrective actions or continued failure to achieve the minimum monitor availability shall be violations of this permit, except as otherwise authorized by the Department’s Compliance Authority.

[Rules 62-4.070(3) & 62-210.200(BACT), F.A.C.; and, Permit No. 0090180-003-AC.]

- CEMS Annual Emissions Requirement.  The owner or operator shall use data from the NOX CEMS when calculating annual emissions for purposes of computing actual emissions, baseline actual emissions, and net emissions increase, as defined at Rule 62-210.200, F.A.C., and for purposes of computing emissions pursuant to the reporting requirements of Rule 62-210.370(3), F.A.C.  In computing the emissions of a pollutant, the owner or operator shall account for the emissions during periods of startup and shutdown of the emissions unit.  [Rules 62-210.200, and 62-210.370(3), F.A.C.]

- Continuous Compliance.  Continuous compliance with the permit standard for emissions of NOX shall be demonstrated with data collected from the required continuous monitoring system.  [0090180-003-AC, Specific Condition 19.]

Test Methods and Procedures

- Test Methods.  Required tests shall be performed in accordance with the following reference methods:

| Method | Description of Method and Comments |
| --- | --- |
| 7E | Determination of Nitrogen Oxide Emissions from Stationary Sources |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |
| 20 | Determination of Nitrogen Oxides, Sulfur Dioxide and Diluent Emissions from Stationary Gas Turbines |

The methods are described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used for compliance testing unless prior written approval is received from the administrator of the Department’s Emissions Monitoring Section in accordance with an alternate sampling procedure pursuant to 62-297.620, F.A.C.  [Rules 62-204.800, F.A.C.; 40 CFR 60, Appendix A]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- Annual Compliance Tests.  During each federal fiscal year (October 1st, to September 30th) the annual test shall be conducted between 90% and 100% of permitted capacity in accordance with the requirements of Rule 62-297.310(2), F.A.C..  Tests shall be conducted for each pollutant while firing each fuel in the CT.  If normal operation on fuel oil is less than 400 hours per calendar year, then subsequent compliance testing (annual or renewal) on fuel oil is not required for that year.  If normal operation on fuel oil exceeds 400 hours per year, the Department shall require compliance testing for NOX and visible emissions while firing fuel oil.  For each run during tests for visible emissions, emissions of NOX recorded by the CEMS shall also be reported.  Data collected from the reference method during the required CEMS quality assurance RATA tests may substitute for annual and renewal compliance tests for NOX, provided the owner or operator indicates this intent in the submitted test protocol, and obtains approval prior to testing.  If data collected from the reference method during the required CEMS quality assurance RATA test are substituted for annual or renewal compliance tests for NOX, then no separate annual or renewal compliance testing for the fuel fired while conducting the CEMS quality assurance RATA test shall be required.  If the RATA is conducted at less than permitted capacity, and the data is used for annual compliance, the requirements of 62-297.310(2) (Operating Rate During Testing) still apply.  [Rules 62-210.200(BACT), 62-4.070, 62-297.310(2) & (7)(a), F.A.C.; 40 CFR 60.8; and, Permit Nos. 0090180-003-AC and 0090180-007-AC.]

- Compliance Tests Prior To Permit Renewal.  The owner or operator shall conduct testing to demonstrate compliance with the emissions standards for VE and NOX emissions prior to renewal of the facility’s Title V Air Operation Permit.  See Specific Condition TR.7.  [Rule 62-297.310(7), F.A.C.]

{Permitting Note:  Tests which are only required once during the term of a permit prior to obtaining a renewed permit should be performed roughly five years from the previous test.}

Recordkeeping and Reporting Requirements

- Monitoring of Capacity.  The permittee shall monitor and record the operating rate of the combustion turbine on a daily average basis, considering the number of hours of operation during each day (including the times of startup, shutdown, malfunction, DLN tuning, and fuel switching).  Such monitoring shall be made by monitoring daily rates of consumption and heat content of each allowable fuel in accordance with the provisions of 40 CFR 75 Appendix D.  [Rules 62-4.070(3) & 62-210.200(BACT), F.A.C. ; and Permit No. 0090180-003-AC.]

- Monthly Operations Summary.  By the 15th calendar day of each month, the permittee shall record the following for each fuel in a written or electronic log for the combustion turbine for the previous month of operation: fuel consumption, hours of operation on each fuel, and the updated calendar year totals for each.  Information recorded and stored as an electronic file shall be available for inspection and printing within at least three days of a request by the Department.  The fuel consumption shall be monitored in accordance with the provisions of 40 CFR 75 Appendix D.  [Rules 62-4.070(3) & 62-210.200(BACT), F.A.C. ; and Permit No. 0090180-003-AC.]

- Fuel Sulfur Records.  The permittee shall demonstrate compliance with the fuel sulfur limits specified in this permit by maintaining the following records of the sulfur contents.

a.	Natural Gas Sulfur Limit.  Compliance with the fuel sulfur limit for natural gas shall be demonstrated by keeping reports obtained from the vendor indicating the average sulfur content of the natural gas being supplied from the pipeline for each month of operation.  Methods for determining the sulfur content of the natural gas shall be ASTM methods D4084-82, D4468-85, D5504-01, D6228-98 and D6667-01, D3246-81 or more recent versions.

b.	Distillate Fuel Oil Sulfur Limit.  Compliance with the distillate fuel oil sulfur limit shall be demonstrated by taking a sample, analyzing the sample for fuel sulfur, and reporting the results to each Compliance Authority before initial startup.  Sampling the fuel oil sulfur content shall be conducted in accordance with ASTM D4057-88, Standard Practice for Manual Sampling of Petroleum and Petroleum Products, and one of the following test methods for sulfur in petroleum products:  ASTM methods D5453-00, D129-91, D1552-90, D2622-94, or D4294-90.  More recent versions of these methods may be used.  For each subsequent fuel delivery, the permittee shall maintain a permanent file of the certified fuel sulfur analysis from the fuel vendor.  At the request of the Compliance Authority, the permittee shall perform additional sampling and analysis for the fuel sulfur content.

The above methods shall be used to determine the fuel sulfur content in conjunction with the provisions of 40 CFR 75 Appendix D.  [Rules 62-4.070(3) & 62-4.160(15), F.A.C.; and Permit No. 0090180-003-AC.]

- Excess Emissions Reporting.

a.	Malfunction Notification.  If emissions in excess of a standard (subject to the specified averaging period) occur due to malfunction, the permittee shall notify the Compliance Authority within (1) working day of:  the nature, extent, and duration of the excess emissions; the cause of the excess emissions; and the actions taken to correct the problem.  In addition, the Department may request a written summary report of the incident.

b.	SIP Quarterly Report.  Within 30 days following the end of each calendar-quarter, the permittee shall submit a report to the Compliance Authority summarizing periods of NOX emissions in excess of the BACT permit standard following the NSPS format in 40 CFR 60.7(c), Subpart A.  A summary of data excluded from SIP compliance calculations should also be provided.  In addition, the report shall summarize the NOX CEMS system monitor availability for the previous quarter.

c.	NSPS Reporting.  Within 30 days following the calendar quarter, the permittee shall submit the written reports required by 40 CFR 60 Subpart KKKK (Standards of Performance for Stationary Combustion Turbines) for the previous semi-annual period to the Compliance Authority.

{Note:  If there are no periods of excess emissions as defined in 40 CFR, Part 60, Subpart KKKK, a statement to that effect may be submitted with the SIP Quarterly Report to suffice for the NSPS Semi-Annual Report.}

[Rules 62-4.130, 62-204.800, 62-210.700(6) & 62-212.400(BACT), F.A.C.; 40 CFR 60.7 & 60.4375; and, Permit No. 0090180-003-AC.]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440(1)(b), F.A.C.]

Operated by:  Oleander Power Project, L.P.

ORIS Code:  55286

The emissions units listed below are regulated under Acid Rain, Phase II.

| E.U. ID No. | Brief Description |
| --- | --- |
| -001 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |
| -002 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |
| -003 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |
| -004 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |
| -005 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |

A.1.	The Phase II Acid Rain Part application submitted for this facility, as approved by the Department, is a part of this permit.  The owners and operators of these Phase II acid rain units must comply with the standard requirements and special provisions set forth in the application listed below:

a.	DEP Form No. 62-210.900(1)(a), dated 05/08/13, received 05/14/13.

[Chapter 62-213, F.A.C. and Rule 62-214.320, F.A.C.]

A.3.	Sulfur Dioxide (SO2) Emission Allowances.  SO2 emissions from sources subject to the Federal Acid Rain Program (Title IV) shall not exceed any allowances that the source lawfully holds under the Federal Acid Rain Program.  Allowances shall not be used to demonstrate compliance with a non-Title IV applicable requirement of the Act.

a.	No permit revision shall be required for increases in emissions that are authorized by allowances acquired pursuant to the Federal Acid Rain Program, provided that such increases do not require a permit revision pursuant to Rule 62-213.400(3), F.A.C.

b.	No limit shall be placed on the number of allowances held by the source under the Federal Acid Rain Program.

c.	Allowances shall be accounted for under the Federal Acid Rain Program.

[Rule 62-213.440(1)(c)1., 2. & 3., F.A.C.]

A.4.	Comments, Notes, and Justifications:  None.

Clean Air Interstate Rule (CAIR).

Operated by: Oleander Power Project

Plant: Oleander Power Project, L.P.

ORIS Code: 55286

The emissions units below are regulated under the Clean Air Interstate Rule.

| EU No. | EPA Unit ID# | Brief Description |
| --- | --- | --- |
| 001 | 0-1 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |
| 002 | 0-2 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |
| 003 | 0-3 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |
| 004 | 0-4 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |
| 005 | 0-5 | Simple-Cycle Combustion Turbine-Electrical Generator (nominal 190 megawatt) |

- Clean Air Interstate Rule Application.  The Clean Air Interstate Rule Part Form submitted for this facility is a part of this permit.  The owners and operators of these CAIR units as identified in this form must comply with the standard requirements and special provisions set forth in the CAIR Part Form (DEP Form No. 62-210.900(1)(b)) dated March 16, 2008, which is attached at the end of this section.  [Chapter 62-213, F.A.C. and Rule 62-210.200, F.A.C.]

Appendix A, Glossary.

Appendix I, List of Insignificant Emissions Units and/or Activities.

Appendix NSPS, Subpart A – General Provisions.

Appendix NSPS, Subpart GG – Standards of Performance for Stationary Gas Turbines.

Appendix NSPS, Subpart KKKK – Standards of Performance for Stationary Gas Turbines.

Appendix RR, Facility-wide Reporting Requirements.

Appendix TR, Facility-wide Testing Requirements.

Appendix TV, Title V General Conditions.

Appendix U, List of Unregulated Emissions Units and/or Activities.