Duke Energy Florida, Inc. (DEF)

University of Florida Cogeneration Plant

Facility ID No. 0010001

Alachua County

Title V Air Operation Permit Renewal

Permit No. 0010001-016-AV

Permitting Authority

State of Florida

Department of Environmental Protection

Division of Air Resource Management

Office of Permitting and Compliance

2600 Blair Stone Road

Mail Station #5505

Tallahassee, Florida  32399-2400

Telephone:  850/717-9000

Fax:  850/717-9097

Compliance Authority

State of Florida

Department of Environmental Protection

Northeast District Office

7777 Baymeadows Way West, Suite B-100

Jacksonville, Florida  32256

Telephone:  904/256-1700

Fax:  904/256-1590

Title V Air Operation Permit Renewal

Permit No. 0010001-016-AV

Table of Contents

Section	Page Number

I.	Facility Information.

A.	Facility Description. 	 2

B.	Summary of Emissions Units. 	 2

C.	Applicable Regulations. 	 2

II.	Facility-wide Conditions. 	 3

III.	Emissions Units and Conditions.

A.	Steam Boilers No. 4 & No. 5. 	 6

B.	Combustion Turbine and Duct Burner (DB) with Heat Recovery Steam Generator (HRSG).	 10

C.   Emergency Generator.	18

IV.	Acid Rain Part. 	 22

Phase II Acid Rain Application/Compliance Plan.

V.	Clean Air Interstate Rule Part. 	 27

VI.	Appendices. 	 33

Appendix A, Glossary.

Appendix HI – Heat Input vs. Inlet Temperature Curve.

Appendix I, List of Insignificant Emissions Units and/or Activities.

Appendix NSPS, Subpart A – General Provisions.

Appendix NSPS, Subpart Db – Standards of Performance for Industrial-Commercial-Institutional Steam Generating Units.

Appendix NSPS, Subpart GG – Standards of Performance for Stationary Gas Turbines.

Appendix NESHAP, Subpart A

Appendix NESHAP, Subpart JJJJJJ, National Emission Standards for Hazardous Air Pollutants for Industrial, Commercial, and Institutional Boilers Area Sources

Appendix NESHAP, Subpart ZZZZ, National Emissions Standard for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines (RICE).

Appendix RR, Facility-wide Reporting Requirements.

Appendix TR, Facility-wide Testing Requirements.

Appendix TV, Title V General Conditions.

Referenced Attachments. 	 At End

Figure 1, Summary Report-Gaseous and Opacity Excess Emission and

Monitoring System Performance (40 CFR 60, July, 1996).

Table H, Permit History.

Permittee:

Duke Energy Florida, Inc.	Permit No. 0010001-016-AV

1928 Mowry Road, Building 82	University of Florida Cogeneration Plant

University of Florida	Facility ID No. 0010001

Gainesville, Florida  32611-2295	Title V Air Operation Permit Renewal

The purpose of this permit is to renew the Title V Air Operation Permit for the above referenced facility.

The existing University of Florida Cogeneration Plant is located in Alachua County on Mowry Road at Building 82, Gainesville, Florida.  UTM Coordinates are:  Zone 17, 369.39 km East and 3279.29 km North.  Latitude is:  29° 38′ 23" North; and, Longitude is:  82° 20′ 55” West.

The Title V air operation permit is issued under the provisions of Chapter 403, Florida Statutes (F.S.), and Florida Administrative Code (F.A.C.) Chapters 62-4, 62-210, 62-213 and 62-214.  The above named permittee is hereby authorized to operate the facility, in accordance with the terms and conditions of this permit.

Effective Date:  January 1, 2015

Renewal Application Due Date:  May 20, 2019

Expiration Date:  December 31, 2019

Executed in Tallahassee, Florida.

(Draft/Proposed)

for:  Jeffery F. Koerner, Program Administrator

Office of Permitting and Compliance

Division of Air Resource Management

JFK/dlr/tbc

Subsection A.  Facility Description.

This facility consists of one nominal 48 MW General Electric (GE) LM6000-PC-ESPRINT Combustion Turbine (CT), one Duct Burner (DB) with a Heat Recovery Steam Generator (HRSG), and two Steam Boilers.  The CT utilizes spray intercooling to maximize throughput, thus reducing supplemental firing in the duct burner for meeting steam and power requirements.  Emissions from the CT and DB are vented through a common stack.  NOX emissions are controlled with steam injection.  The steam boilers, each having a separate exhaust stack, are used only as back-up sources.  Compliance is demonstrated with a NOX CEMS.

Subsection B.  Summary of Emissions Units.

| EU No. | ## Brief Description |
| --- | --- |
| Regulated Emissions Units |  |
| 002 | No. 4 Steam Boiler |
| 003 | No. 5 Steam Boiler |
| 005 | Duct Burner System with HRSG |
| 007 | Combustion Turbine |
| 009 | Emergency Generator |

Also, included in this permit are miscellaneous insignificant emissions units and/or activities.

Subsection C.  Applicable Regulations.

Based on the Title V Air Operation Renewal application received May 15, 2009, this facility is not a major source of hazardous air pollutants (HAP).  Because this facility operates a stationary reciprocating internal combustion engine, it is subject to regulation under 40 CFR 63, Subpart ZZZZ - National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines.  Appendices 40 CFR 63, Subpart A and 40 CFR 63, Subpart ZZZZ, are included in the Appendix Section as applicable requirements.  Detailed specific conditions will be established (as applicable) within the body of the permit for these regulated emissions units at the time of the next renewal.  This facility is classified as a PSD major facility.  A summary of applicable regulations is shown in the following table.

| Regulation | ## EU No(s). |
| --- | --- |
| 40 CFR 60, Subpart A, NSPS General Provisions | 005, 007 |
| 40 CFR 60, Subpart Db | 005 |
| 40 CFR 60, Subpart GG | 007 |
| 40 CFR 63, Subpart JJJJJJ | 002, 003 |
| 40 CFR 63, Subpart ZZZZ | 009 |
| 40 CFR 75 Acid Rain Monitoring Provisions | 007 |
| 62-296.406, F.A.C. | 002, 003, 005 |
| 62-296.470, F.A.C. – Clean Air Interstate Rule (CAIR) | 005, 007 |

The following conditions apply facility-wide to all emission units and activities:

- Appendices.  The permittee shall comply with all documents identified in Section VI, Appendices, listed in the Table of Contents.  Each document is an enforceable part of this permit unless otherwise indicated.  [Rule 62-213.440, F.A.C.]

Emissions and Controls

- Not federally Enforceable.  Objectionable Odor Prohibited.  No person shall cause, suffer, allow or permit the discharge of air pollutants, which cause or contribute to an objectionable odor.  An “objectionable odor” means any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance.  [Rule 62-296.320(2) and 62-210.200(Definitions), F.A.C.]

- General Volatile Organic Compounds (VOC) Emissions or Organic Solvents (OS) Emissions.  The permittee shall allow no person to store, pump, handle, process, load, unload or use in any process or installation, volatile organic compounds or organic solvents without applying known and existing vapor emission control devices or systems deemed unnecessary and ordered by the Department.  Nothing is deemed necessary and ordered at this time.  [Rule 62-296.320(1), F.A.C.]

- General Visible Emissions.  No person shall cause, let, permit, suffer or allow to be discharged into the atmosphere the emissions of air pollutants from any activity equal to or greater than 20% opacity.  EPA Method 9 is the method of compliance pursuant to Chapter 62-297, F.A.C.  This regulation does not impose a specific testing requirement.  [Rule 62-296.320(4)(b), F.A.C.]

- Unconfined Particulate Matter.  No person shall cause, let, permit, suffer or allow the emissions of unconfined particulate matter from any activity, including vehicular movement; transportation of materials; construction; alteration; demolition or wrecking; or industrially related activities such as loading, unloading, storing or handling; without taking reasonable precautions to prevent such emissions.  Reasonable precautions to prevent emissions of unconfined particulate matter at this facility include:

a.	Application of chemicals or water to unpaved roads and unpaved yard areas;

b.	Paving and maintenance of roads, parking areas and yards;

c.	Regular mowing of grass and care of vegetation and landscaping or planting of vegetation;

d.	Limiting access to plant property by unnecessary vehicles;

e.	Covering and/or application of water or chemicals to the affected areas, as necessary; and,

f.	Additional or alternative activities may be utilized to minimize unconfined particulate emissions.

[Rule 62-296.320(4)(c), F.A.C.; proposed by applicant in Title V air operation permit renewal application received May 16, 2014; and, Permit No. 0010001-003-AC.]

Annual Reports and Fees

See Appendix RR, Facility-wide Reporting Requirements for additional details.

- Annual Operating Report.  The permittee shall submit an annual report that summarizes the actual operating rates and emissions from this facility.  Annual operating reports shall be submitted to the Compliance Authority by April 1st of each year.  [Rule 62-210.370(3), F.A.C.]

- Electronic Annual Operating Report and Title V Annual Emissions Fees.  The information required by the Annual Operating Report for Air Pollutant Emitting Facility [Including Title V Source Emissions Fee Calculation] (DEP Form No. 62-210.900(5)) shall be submitted by April 1 of each year, for the previous calendar year, to the Department of Environmental Protection’s Division of Air Resource Management.  Each Title V source shall submit the annual operating report using the DEP’s Electronic Annual Operating Report (EAOR) software, unless the Title V source claims a technical or financial hardship by submitting DEP Form No. 62-210.900(5) to the DEP Division of Air Resource Management instead of using the reporting software. Emissions shall be computed in accordance with the provisions of subsection 62-210.370(2), F.A.C.  Each Title V source must pay between January 15 and April 1 of each year an annual emissions fee in an amount determined as set forth in subsection 62-213.205(1), F.A.C.  The annual fee shall only apply to those regulated pollutants, except carbon monoxide and greenhouse gases, for which an allowable numeric emission-limiting standard is specified in the source’s most recent construction permit or operation permit.  Upon completing the required EAOR entries, the EAOR Title V Fee Invoice can be printed by the source showing which of the reported emissions are subject to the fee and the total Title V Annual Emissions Fee that is due.  The submission of the annual Title V emissions fee payment is also due (postmarked) by April 1st of each year.  A copy of the system-generated EAOR Title V Annual Emissions Fee Invoice and the indicated total fee shall be submitted to:  Major Air Pollution Source Annual Emissions Fee, P.O. Box 3070, Tallahassee, Florida  32315-3070.  Additional information is available by accessing the Title V Annual Emissions Fee On-line Information Center at the following Internet web site:  http://www.dep.state.fl.us/air/emission/tvfee.htm.  [Rules 62-210.370(3), 62-210.900 & 62-213.205, F.A.C.; and, §403.0872(11), Florida Statutes (2013)]

{Permitting Note:  Resources to help you complete your AOR are available on the electronic AOR (EAOR) website at:  http://www.dep.state.fl.us/air/emission/eaor.  If you have questions or need assistance after reviewing the information posted on the EAOR website, please contact the Department by phone at (850) 717-9000 or email at eaor@dep.state.fl.us.}

{Permitting Note:  The Title V Annual Emissions Fee form (DEP Form No. 62-213.900(1)) has been repealed.  A separate Annual Emissions Fee form is no longer required to be submitted by March 1st each year.}

- Annual Statement of Compliance.  The permittee shall submit an annual statement of compliance to the compliance authority at the address shown on the cover of this permit within 60 days after the end of each calendar year during which the Title V permit was effective.  [Rules 62-213.440(3)(a)2. & 3. and (b), F.A.C.]

FW9. 	Prevention of Accidental Releases (Section 112(r) of CAA).  If and when the facility becomes subject to 112(r), the permittee shall:

a.	Submit its Risk Management Plan (RMP) to the Chemical Emergency Preparedness and Prevention Office (CEPPO) RMP Reporting Center.  Any Risk Management Plans, original submittals, revisions or updates to submittals, should be sent to:  RMP Reporting Center, Post Office Box 10162, Fairfax, VA  22038, Telephone:  (703) 227-7650.

b.	Submit to the permitting authority Title V certification forms or a compliance schedule in accordance with Rule 62-213.440(2), F.A.C.

[40 CFR 68]

Other Requirements

FW10.	Facility-Wide Annual NOX Emission Cap.  NOX emissions shall not exceed 185.3 tons per year for any calendar year for all emissions units regulated by this air construction permit (EU 002, 003, 005 and 007). The backup steam boilers may operate individually or in combination provided NOX emissions from all emissions units regulated by this permit comply with this facility-wide NOX emissions cap.  [PSD avoidance pursuant to 62-212.400(12), F.A.C., and Permit No. 0010001-011-AC/PSD-FL-181B]

FW11.	Annual Facility-wide NOx Emissions Report.  By April 1st of each year, the permittee shall report the facility-wide annual NOx emissions along with the Annual Operating Report.  To demonstrate compliance with the facility-wide annual NOx emissions cap, the permittee shall calculate and record annual emissions as follows:

a. 	Annual NOX emissions from the combined cycle combustion turbine and duct burner system shall be determined by data collected from the NOx CEMS.

b. 	Annual NOX emissions from the backup steam boilers shall be determined based on the annual fuel consumption rate and either the following NOx emissions factors or more recent stack test data (at the option of the permittee).

- No. 4 Steam Boiler: 0.0745 lb NOx/MMBtu (gas) and 0.0815 lb NOx/MMBtu (oil), and

- No. 5 Steam Boiler: 0.110 lb NOx/MMBtu (gas) and 0.1070 lb NOx/MMBtu (oil).

c. 	If the facility-wide annual NOX emissions exceed the NOX emissions cap, the permittee shall notify the Compliance Authority within three working days of discovery.

[Permit No. 0010001-011-AC/PSD-FL-181B]

FW12.	Modifications. The permittee shall give written notification to the Department when there is any modification to this facility.  This notice shall be submitted sufficiently in advance of any critical date involved to allow sufficient time for review, discussion, and revision of plans, if necessary.  Such notice shall include, but not be limited to, information describing the precise nature of the change; modifications to any emission control system; production capacity of the facility before and after the change; and the anticipated completion date of the change.  [Chapters 62-210 & 62-212, F.A.C.]

FW13.	Recordkeeping and Reporting.  The permittee shall maintain the required fuel use records and include the total NOX emission calculation in each annual operating report; and the records shall be retained for a five year period.  [Rules 62-212.400(12) & 62-213.440, F.A.C]

FW14.	Fuel Consumption Rates Monthly Monitoring.  By the 15th calendar day of each month, the permittee shall record the monthly fuel consumption rates of the duct burner and backup steam boilers.  The written log shall summarize the fuel consumption for the previous month of operation and the previous 12 months of operation.  Information may be recorded and stored as an electronic file.  Records shall be available for inspection and printing within at least three days of a request by the Department or Compliance Authority.  [Permit No. 0010001-011-AC/PSD-FL-181B]

The specific conditions in this section apply to the following emissions units:

| EU No. | Brief Description |
| --- | --- |
| 002 | No. 4 Steam Boiler |
| 003 | No. 5 Steam Boiler |

The steam boilers are used only as back-up sources.  Each boiler has its own exhaust stack.  The maximum heat input rate for the No. 4 steam boiler is 69.6 MMBtu/hr.  The maximum heat input is based on permitted firing limits of 68,000 cubic feet (cf) of natural gas per hour and 444 gallons per hour of No. 2 fuel oil.  The maximum heat input rate for the No. 5 steam boiler is 168 MMBtu/hr.  The maximum heat input is based on permit firing limits of 164,000 cf of natural gas per hour and 1,067 gallons per hour of No. 2 fuel oil.  The emission units began commercial service in January 1976.  No. 4 steam boiler has a stack height of 82 feet, exit diameter of 5 feet, exit temperature of 350 °F and actual volumetric flow rate of 13,500 acfm.  No. 5 steam boiler has a stack height of 82 feet, exit diameter of 6 feet, exit temperature of 400 °F and actual volumetric flow rate of 56,250 acfm.  The emissions units are regulated under permit Nos. 0010001-011-AC/PSD-FL-181B; and, Rule 62-296.406, F.A.C., Fossil Fuel Steam Generators with Less than 250 MMBtu per Hour Heat Input.

Essential Potential to Emit (PTE) Parameters

- Permitted Capacity.  The maximum allowable heat input rate is as follows:

| EU No. | MMBtu/hr Heat Input | Fuel Type |
| --- | --- | --- |
| 002 | 69.6 | No. 2 Fuel Oil Natural Gas |
| 003 | 168 | No. 2 Fuel Oil Natural Gas |

[Rules 62-4.160(2), 62-204.800, 62-210.200(PTE), 62-214.330 & 62-296.405, F.A.C.; and, Permit No. 0010001-011-AC/PSD-FL-181(B)]

- Emissions Unit Operating Rate Limitation After Testing.  See the related testing provisions in Appendix TR, Facility-wide Testing Requirements.  [Rule 62-297.310(2), F.A.C.]

- Methods of Operation - Fuels.  The fuels that are allowed to be burned in these units are:

  - No. 2 distillate fuel oil with a maximum sulfur content of 0.5% by weight, and

  - Natural gas with a maximum sulfur content of 2 grains of sulfur per 100 scf of natural gas (annual average based on vendor data).

  - The units are exempt from the requirements of NESHAP, Subpart JJJJJJ as long as fuel oil firing is limited to 48 hours per calendar year for periodic testing.

  - Fuel oil firing is not limited during periods of gas curtailment or gas supply interruptions.

{Permitting Note: Because the UF CoGen site is supplied by a single natural gas pipeline examples of periods of gas interruptions include, pressure testing of the gas supply pipeline, maintenance and repair of gas valves and gas leak repair.  If a back-up boiler exceeds the fuel oil firing limitations and no longer meets the definition of “gas-fired boiler” contained in 40 CFR Part 63 Subpart JJJJJJ, the boiler shall comply with all the requirements of the subpart with in the deadlines delineated in this subpart.}

[Rules 62-212.400(12), F.A.C. and 62-213.410, F.A.C., and Permit No. 0010001-011-AC/PSD-FL-181B; 0010001-015-AC, Specific Condition 2.]

- Hours of Operation.  The boilers may be operated as necessary for backup to the CT and DB, and as long as the total NOX emissions from the four emission units (EU Nos. 002, 003, 005 & 007) at the facility does not exceed 185.3 TPY for any calendar year (see Facility-wide Condition FW10.).  Emission factors pursuant to Specific Condition A.18. shall be applied to the fuel consumed by Boilers Nos. 4 and 5 to determine compliance with the facility cap.  See Facility-Wide Condition FW10.  [Rules 62-212.400(12), F.A.C. and 62-213.410, F.A.C., and Permit No. 0010001-011-AC/PSD-FL-181B]

Emission Limitations and Standards

Unless otherwise specified, the averaging time(s) for Specific Conditions A.5 – A.9. are based on the specified averaging time of the applicable test method.

- Emissions Standards – Backup Steam Boilers.  To control PM and SO2 emissions, the backup steam boilers shall fire only natural gas or No. 2 fuel oil.  As determined by EPA Method 9, visible emissions when firing any authorized fuel shall not exceed 20% opacity except for one, 6-minute block average per hour not to exceed 27% opacity.  [Rule 62-296.406(BACT), F.A.C., and Permit No. 0010001-011-AC/PSD-FL-181B]

- Visible Emissions - Soot Blowing and Load Change.  Visible emissions shall not exceed 60 percent opacity during the 3-hours in any 24 hour period of excess emissions allowed for boiler cleaning (soot blowing) and load change.  A load change occurs when the operational capacity of a unit is in the 10 percent to 100 percent capacity range, other than startup or shutdown, which exceeds 10 percent of the unit’s rated capacity and which occurs at a rate of 0.5 percent per minute or more.  [Rule 62-210.700(3), F.A.C.]

- Particulate Matter.  Particulate matter emissions shall be controlled by the firing of natural gas and/or low sulfur content No. 2 fuel oil.  [Rule 62-296.406(2), F.A.C., BACT]

- Sulfur Dioxide.  Sulfur dioxide emissions shall be controlled by firing natural gas and No. 2 fuel oil with a sulfur content that shall not exceed 0.5 percent, by weight.  [Rule 62-296.406(3), F.A.C., BACT; and, Permit No. 0010001-011-AC/PSD-FL-181B]

- Nitrogen Oxides.  These emissions units are also subject to the facility-wide NOX limit contained in Facility-wide Condition FW10.  [Rule 62-212.400(12), F.A.C. and Permit No. 0010001-011-AC/PSD-FL-181B]

Excess Emissions

Rule 62-210.700 (Excess Emissions), F.A.C. cannot vary any requirement of an NSPS, NESHAP or Acid Rain program provision.

- Excess Emissions From Malfunctions Allowed.  Excess emissions due to malfunctions shall be permitted providing (1) best operational practices to minimize emissions are adhered to and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24 hour period unless specifically authorized by the Department for longer duration.  [Rule 62-210.700(1), F.A.C.]

- Excess Emissions From Startup or Shutdown Allowed.  Excess emissions resulting from startup or shutdown shall be permitted provided that best operational practices to minimize emissions are adhered to and the duration of excess emissions shall be minimized.  [Rule 62-210.700(2), F.A.C.]

- Excess Emissions Prohibited.  Excess emissions which are caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure which may reasonably be prevented during startup, shutdown, or malfunction shall be prohibited.  [Rule 62-210.700(4), F.A.C.]

Test Methods and Procedures

- Test Methods.  Required tests shall be performed in accordance with the following reference methods:

| Method | Description of Method and Comments |
| --- | --- |
| 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| 5 | Method for Determining Particulate Matter Emissions |
| 7E | Determination of Nitrogen Oxide Emissions from Stationary Sources |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |
| 19 | Determination of Sulfur Dioxide Removal Efficiency and Particulate Matter, Sulfur Dioxide, and Nitrogen Oxides Emission Rates (Optional F-factor method may be used to determine flow rate and gas analysis to calculate mass emissions in lieu of Methods 1-4.) |
| 20 | Determination of Nitrogen Oxides, Sulfur Dioxide and Diluent Emissions from Stationary Gas Turbines |
| ASTM D2622-92, ASTM D4294-90, or both ASTM D4057-88 and ASTM D129-91, ASTM D1552 or equivalent method or the latest edition(s) | Standard Test Method for Sulfur in Petroleum Products by Wavelength Dispersive X-ray Fluorescence Spectrometry, Standard Test Method for Sulfur in Petroleum Products by Energy-Dispersive X-Ray Fluorescence Spectroscopy, Standard Practice for Manual Sampling of Petroleum and Petroleum Products, Standard Test Method for Sulfur in Petroleum Products (General Bomb Method), Standard Test Method for Sulfur in Petroleum Products (High-Temperature Method) |
| ASTM4084-82, D3246-81, D5504* or equivalent method or the latest edition(s) | Standard Method for Analysis of Hydrogen Sulfide in Gaseous Fuels (Lead Acetate Reaction Rate Method), Standard Method for Sulfur in Petroleum Gas by Oxidative Microcoulometry |

The above methods are described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Permit No. 0010001-011-AC/PSD-FL-181B; Rules 62-213.440 & 62-297.401, F.A.C.; and, *Applicant Request.]

- Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310, F.A.C.]

- Annual Compliance Tests.  Except as provided for in Specific Condition A.20., during each federal fiscal year (October 1st to September 30th), each emissions unit (002 and 003) shall be tested to demonstrate compliance with the emissions standards for VE.  Compliance with the liquid fuel sulfur limit shall be demonstrated through fuel sampling as specified in Specific Condition A.19. and the submission of an annual report detailing the results of the samples from the previous year.  [Rules 62-213.440 and 62-297.310(7), F.A.C.]

- Compliance Tests Prior to Renewal.  Compliance tests shall be performed for VE prior to obtaining a renewed operating permit to demonstrate compliance with the emission limits in Specific Conditions A.5. and A.6.  Compliance with the liquid fuel sulfur limit contained in Specific Condition A.8. shall be demonstrated through fuel sampling as specified in Specific Condition A.19. and the submission of an annual report detailing the results of the samples from the previous year.  [Rules 62-210.300(2)(a), 62-213.440 and 62-297.310(7)(a), F.A.C.]

- Visible emissions.  The test method for visible emissions shall be EPA Method 9, incorporated in Chapter 62-297, F.A.C.  [Rules 62-213.440 and 62-297.401, F.A.C.]

- Nitrogen Oxides.  A “lbs/hr” or "lbs/MMBtu" emissions factor for nitrogen oxides for each boiler and for each fuel type fired was established during the initial performance tests required by permit No. AC01-204652/PSD-FL-181.  This emissions factor per fuel type shall be used in conjunction with the actual hours operated or total heat input in the previous year per fuel type to assess the nitrogen oxides contribution toward the facility cap of 185.3 TPY.  See Specific Conditions A.4. and FW10.  [Rules 62-210.200(PTE), 62-212.400(12), 62-213.440, 62-297.310(7), 62-297.401, F.A.C.]

- Sulfur Dioxide - Sulfur Content.  The permittee shall demonstrate compliance with the liquid fuel sulfur limit by the vendor providing a fuel analysis upon each fuel delivery.  The fuel sulfur content percent by weight, for liquid fuels shall be evaluated using either:  ASTM D2622-92, ASTM D2494-90, both D4057-88 and ASTM D129-91, ASTM D1552 or equivalent method, or the latest edition(s).  Current applicable alternative methods that are approved ASTM methods as adopted in Rule 62-297.440(1), F.A.C. are also acceptable.  [Rules 62-213.440, F.A.C., 62-296.406(3), F.A.C., 62-297.440, F.A.C., BACT]

{Permitting Note:  The permittee may elect to perform on-site sampling analysis using the ASTM methods listed above and in accordance with Part 75 Appendix D (See Specific Condition B.28.) instead of relying upon the vendor’s delivery receipts.}

- Annual VE Test Waiver.  By this permit, annual emissions compliance testing for visible emissions is not required for these emissions units while burning:

a.	only gaseous fuel(s); or

b.	gaseous fuel(s) in combination with any amount of liquid fuel(s) for less than 400 hours per year; or

c.	only liquid fuel(s) for less than 400 hours per year.

[Rule 62-297.310(7)(a)4., F.A.C.; 0010001-015-AC, Specific Condition 2.]

Recordkeeping and Reporting Requirements

- The permittee shall maintain the required fuel use records and include the total NOX emission calculation in each annual operating report.  [Rule 62-213.440(1)(b), F.A.C.]

- Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.  [Rule 62-213.440(1)(b), F.A.C.]

- Annual Facility-wide NOx Emissions Report:  By April 1st of each year, the permittee shall report the facility-wide annual NOx emissions along with the Annual Operating Report.  To demonstrate compliance with the facility-wide annual NOx emissions cap, the permittee shall calculate and record annual emissions as follows:

a. 	Annual NOx emissions from the combined cycle combustion turbine and duct burner system shall be determined by data collected from the NOx CEMS.

b. 	Annual NOx emissions from the backup steam boilers shall be determined based on the annual fuel consumption rate and either the following NOx emissions factors or more recent stack test data (at the option of the permittee).

- No. 4 Steam Boiler: 0.0745 lb NOx/MMBtu (gas) and 0.0815 lb NOx/MMBtu (oil), and

- No. 5 Steam Boiler: 0.110 lb NOx/MMBtu (gas) and 0.1070 lb NOx/MMBtu (oil).

c. 	If the facility-wide annual NOx emissions exceed the NOx emissions cap, the permittee shall notify the Compliance Authority within three working days of discovery.

[Permit No. 0010001-011-AC/PSD-FL-181B]

The specific conditions in this section apply to the following emissions units:

| EU No. | Brief Description |
| --- | --- |
| 007 | GE LM6000-PC-ESPRINT Combustion Turbine |
| 005 | Duct Burner System associated with a Heat Recovery Steam Generator |

Emissions units 007 and 005 are a combustion turbine (CT) with a duct burner-fired (DB) heat recovery steam generator (HRSG), respectively.  The CT is a GE LM6000-PC-ESPRINT combustion turbine with a nominal generator rating of 48 megawatts (MW) fired with natural gas.  The CT utilizes spray intercooling to maximize throughput, thus reducing supplemental firing in the duct burner for meeting steam and power requirements.  The NOX emissions are controlled with steam injection.  The HRSG is equipped with a natural gas-fired duct burner.  The DB is equipped with low-NOX burners to control NOX emissions.  The CT and the DB exhaust through the same HRSG and common stack.  The common stack has a height of 93 feet, exit diameter of 9.8 feet, exit temperature of 257 °F, and actual volumetric flow rate of 365,700 acfm, based on CT only @ 59 °F, 60% relative humidity at inlet, maximum dry standard flow rate of 216,956 dscfm, and exit velocity of 80.8 feet per second.  The 48 MW CT began commercial service on September 24, 2002 (replacing the original 43 MW CT that was installed in 1994).  The DB and HRSG began commercial service January 31, 1994.

{Permitting Note:  The CT is regulated under Acid Rain, Phase II; CAIR; 40 CFR 60, Subpart GG, Standards of Performance for Stationary Gas Turbines, adopted and incorporated by reference in Rule 62-204.800(7)(b), F.A.C.  The DB and HRSG are regulated under 40 CFR 60, Subpart Db, Standards of Performance for Industrial-Commercial-Institutional Steam Generating Units, adopted and incorporated by reference in Rule 62-204.800(7), F.A.C.}

B.1.	Combined Cycle Combustion Turbine System.  The combustion turbine system generally consists of the following components:  gas generator, accessory drive system, air inlet and filtration system, fuel delivery system, cooling system, lubrication system, control system, starting system and exhaust system with stack.  This aero-derivative gas turbine is designed with modular components to facilitate quick repairs.  Common “wear items” include compressor vanes, turbine nozzles, compressor blades, turbine blades, fuel nozzles, combustion chambers, seals, and shaft packing.  The concept of modular design extends to the complete replacement of major components of the gas turbine.  Replacements are authorized provided the following requirements are met.

- The “hot section” components (e.g., combustors and high-speed turbines including blades, nozzles and other components) shall be replaced with equivalent “like-kind” equipment.  Replacement components shall not increase the maximum heat input rate, capacity or emissions from the combustion turbine.  Replacement components shall be designed to achieve and shall achieve the emissions standards specified in this permit or better.

- Within 90 days of replacing a gas generator, the permittee shall conduct emissions stack tests to demonstrate compliance with the emission standards for CO and visible emissions.  The permittee shall comply with the requirements for notification, test methods, test procedures, and reporting required by this permit.

- To up-rate the gas turbine or increase the maximum heat input rate or capacity, the permittee shall submit an application for an air construction permit.

[Permit No. 0010001-011-AC/PSD-FL-181B]

B.2.	Federal Rule Requirements.  (See Section VI. – Appendices.)

a.	Combustion Turbine.  In addition to the requirements listed below, the combustion turbine shall also comply with all of the terms and requirements of 40 CFR 60, Subpart GG - Standards Of Performance For Stationary Gas Turbines (attached as Appendix GG - Standards Of Performance For Stationary Gas Turbines).

b.	Duct Burner.  In addition to the requirements listed below, the duct burner shall also comply with all of the terms and requirements of 40 CFR 60, Subpart Db - Standards Of Performance For Industrial-Commercial-Institutional Steam Generating Units (attached as Appendix Db - Standards Of Performance For Industrial-Commercial-Institutional Steam Generating Units).

c.	CT and DB.  In addition to the requirements listed below, the CT and the DB shall also comply with all of the applicable general provisions for NSPS units contained in 40 CFR 60, Subpart A – General Provisions.

[Permit No. 0010001-011-AC/PSD-FL-181B]

Essential Potential to Emit (PTE) Parameters

B.3.	Permitted Capacity.

  - Combustion Turbine.  The heat input to the combustion turbine shall not exceed the values defined by the manufacturer’s performance curve of heat input rate vs. compressor inlet temperature.  The maximum heat input limits are based on the lower heating value (LHV) of natural gas, 100% load and ambient conditions of 60% relative humidity and 14.7 psia.  The maximum heat input rates will vary depending upon ambient conditions, the combustion turbine characteristics and the demand.

{Permitting Note:  The maximum design heat input rate to the combustion turbine is 480 MMBtu/hour for a compressor inlet temperature of 59°F. See the turbine manufacturer’s performance curve of heat input vs. compressor inlet temperature curve in Appendix HI – Heat Input Rate vs. Compressor Inlet Temperature.}

  - Duct Burner.  The maximum design heat input to the duct burner system is 188 MMBtu/hour of natural gas.  The duct burner shall not fire more than 519.5 million ft3/year of natural gas based on the lower heating value (LHV) of 950 Btu/ft3.

[Rules 62-4.160(2), 62-204.800, 62-210.200(PTE), F.A.C., Permit No. 0010001-011-AC/PSD-FL-181B]

B.4.	Emissions Unit Operating Rate Limitation After Testing.  See the related testing provisions in Appendix TR, Facility-wide Testing Requirements.  [Rule 62-297.310(2), F.A.C.]

B.5.	Methods of Operation – Fuels.

- Combustion Turbine.  The only fuel that is allowed to be burned in the CT is natural gas with a maximum sulfur content of 2 grains of sulfur per 100 scf of natural gas (annual average based on vendor data).

b.	Duct Burner.

(1)	The only fuel that is allowed to be burned in the DB is natural gas with a maximum sulfur content of 2 grains of sulfur per 100 scf of natural gas (annual average based on vendor data).

(2)	The maximum consumption for natural gas in the DB is limited to 519.5 million ft3/yr.

[Rule 62-213.410, F.A.C. and Permit No. 0010001-011-AC/PSD-FL-181B]

B.6.	Hours of Operation.

a.	Combustion Turbine:   Continuously (i.e. 8,760 hours per year).

b.	Duct Burner.  Continuously (i.e. 8,760 hours per year).

[Rule 62-210.200(PTE), F.A.C. and Permit No. 0010001-011-AC/PSD-FL-181B]

Control Technology

B.7.	Combustion Turbine – Steam Injection.  A steam injection system shall be installed to reduce NOx emissions from the combustion turbine exhaust.  In accordance with 40 CFR 60.334, the permittee shall install and operate a continuous monitoring system to monitor and record the ratio of steam to fuel being fired in the combustion turbine.  The permittee shall establish the steam-to-fuel ratio that demonstrates compliance with the emissions standards of this permit by correlating with data collected by the NOx CEMS. When the NOx CEMS is down, the permittee shall operate at a steam-to-fuel injection rate that demonstrates compliance.  [Rule 62-4.070(3), F.A.C.; 40 CFR 60, Subpart GG; and, Permit No. 0010001-011-AC/PSD-FL-181B]

Emission Limitations and Standards

Unless otherwise specified, the averaging times for Specific Conditions B.8. - B.12 are based on the specified averaging time of the applicable test method.

B.8.	Emissions Standards – Combined Cycle Combustion Turbine with Duct Burner.

- Carbon Monoxide (CO) Emissions:

(1) 	As determined by EPA Method 10, CO emissions from the combustion turbine shall not exceed 36.0 ppmvd corrected to 15% oxygen.  {Permitting Note:  This is equivalent to 35.8 lb/hour at a compressor inlet temperature of 59°F.}

(2) 	As determined by EPA Method 10, CO emissions from the duct burner shall not exceed 0.15 lb/MMBtu and 28.1 lb/hour.

b. 	Nitrogen Oxides (NOx) Emissions:

(1) 	As determined by CEMS, NOx emissions from the combustion turbine shall not exceed 39.6 lb/hour with the duct burner “off” and 58.3 lb/hour with the duct burner “on”, based on 30-day rolling averages. {Permitting Note: The basis for the NOX limit on the combustion turbine is 25 ppmvd corrected to 15% oxygen as provided by the vendor.}

(2) 	As determined by CEMS, NOx emissions from the combustion turbine shall not exceed the applicable NSPS emissions standard in 40 CFR 60.332:

(14.4)

STD = 75 ppmvd corrected to 15% oxygen ------------ = 123 ppmvd corrected to 15% oxygen

(8.8)

where:

STD = allowable NOx emissions standard corrected to ISO conditions based on a 4-hour rolling CEMS average.  [40 CFR 60.334]

Y = 8.8 kilojoules per watt hour (kJ/W-hr) based on 950 Btu/SCF (LHV) for natural gas, which is the manufacturer’s rated heat rate at manufacturer's rated load (kilojoules per watt-hour) or, actual measured heat rate based on lower heating value of fuel as measured at actual peak load for the facility. The value of Y shall not exceed 14.4 kJ/W-hr.

There is no NOX emission allowance for fuel-bound nitrogen for natural gas.  [40 CFR 60.334]

(3) 	As determined by CEMS data pursuant to 40 CFR 60.46b, NOx emissions from the duct burner shall not exceed 0.1 lb/MMBtu and 18.7 lb/hour based on 30-day rolling average.  [40 CFR 60.44b]

c. 	Sulfur Dioxide (SO2) Emissions:  SO2 emissions from the combustion turbine shall be controlled by firing natural gas with a maximum sulfur content of 2 grains of sulfur per 100 standard cubic feet of natural gas. This condition also ensures that the fuel contains less than 0.8% by weight pursuant to 40 CFR 60.333(b). [Rules 62-212.400(12) and 40 CFR 60.333]

d. 	Visible Emissions:  As determined by EPA Method 9, visible emissions shall not exceed 10% opacity from the combustion turbine with or without the duct burner in operation.

[Permit No. 0010001-011-AC/PSD-FL-181B]

B.9.  	Visible Emissions.

a.	Combustion Turbine.  Visible emissions shall not exceed 10% opacity.

b.	Duct Burner.  Visible emissions shall not exceed 10% opacity.

c.	CT and DB.  Since the CT and DB are in series, the natural gas opacity standard is applicable when the CT or the CT and DB are in operation.

[Permit No. 0010001-011-AC/PSD-FL-181B]

B.10.	NOX Emissions.  The combustion turbine and the duct burner are subject to the facility-wide NOX limit of 185.3 TPY contained in Facility-wide Condition FW10.  The NOX emissions limits include oxides of nitrogen consisting of both nitric oxide (NO) and nitrogen dioxide (NO2).  By convention, total NOX on a mass basis is expressed as equivalent NO2.  NOX concentration (ppm) is measured as NO by EPA stack sampling methods 7E and 20, and as NO2 by the CEM analyzer.  The NOX concentration is converted to mass emissions by applying the molecular weight of NO2 to the total flow rate.  [Rules 62-212.400(2) & (12), F.A.C.: and, Permit No. 0010001-011-AC/PSD-FL-181B]

B.11.	Particulate Matter.  Particulate matter emissions from the duct burner shall be controlled by the firing of natural gas.  [Rule 62-296.406(2), F.A.C.]

B.12.	Sulfur Dioxide.

- Combustion Turbine.  SO2 emissions shall not exceed 0.015 percent by volume at 15% O2 and on a dry basis.  The sulfur content of the natural gas shall not exceed 2 grains per 100 standard cubic feet of natural gas.

b.	Duct Burner.  Sulfur dioxide emissions from the duct burner shall be controlled by firing natural gas with a sulfur content not to exceed 2 grain per 100 standard cubic feet of natural gas.

{Permitting Note: The 2 grains of sulfur (S) per 100 SCF of natural gas ensures the  40 CFR Part 60, Subpart GG sulfur dioxide (SO2) mission limit of 0.015% by volume at 15% O2 on a dry basis is met.}

[Rule 62-296.406(3), F.A.C.; 40 CFR 60.333(a); and, Permit No. 0010001-011-AC/PSD-FL-181B]

Excess Emissions

Rule 62-210.700 (Excess Emissions), F.A.C. cannot vary any requirement of an NSPS, NESHAP or Acid Rain program provision.

B.13.	Excess Emissions Allowed.  Best operational practices shall be used to minimize hourly emissions that may occur during episodes of startup, shutdown and malfunction. Excess emissions resulting from startup, shutdown, and malfunction shall be permitted providing: (1) best operational practices to minimize emissions are adhered to, and (2) the duration of excess emissions shall be minimized but in no case exceed two hours in any 24-hour period unless specifically authorized by the Department for longer duration. For the combined cycle combustion turbine with a 30-day NOx averaging period, this requirement shall mean the following. The 24-hour period shall be defined as the 24-hour block based on data collected from the NOx CEMS. If the NOx CEMS reports emissions in excess of the 30-day rolling average, the permittee may exclude up to two hours of excess emissions data caused by each startup, shutdown and malfunction during the 30-day period to determine compliance. No NOx emission data shall be excluded from the annual NOx emission caps. This requirement is not intended to limit the duration of a startup – only the amount of data that may be excluded from the 30-day compliance averaging period. If the 30-day rolling NOx emissions rate exceeds the standard, the permittee shall notify the Compliance Authority within one working day with a preliminary report of: the nature, extent, and duration of the excess emissions; the cause of the excess emissions; and the actions taken to correct the problem. In addition, the Department may request a written summary report of the incident.  [Rule 62-210.700(1), F.A.C. and 0010001-011-AC/PSD-FL-181B]

B14.	Excess Emissions From Startup or Shutdown of The Duct Burner Allowed.  Excess emissions resulting from startup or shutdown of the duct burner shall be permitted provided that best operational practices to minimize emissions are adhered to and the duration of excess emissions shall be minimized.  [Rule 62-210.700(2)]

B.15.	Excess Emissions Prohibited.   Excess emissions caused entirely or in part by poor maintenance, poor operation, or any other equipment or process failure that may reasonably be prevented during startup, shutdown or malfunction are prohibited. These emissions shall be included in the compliance averages for NOx emissions.  [Permit No. 0010001-011-AC/PSD-FL-181B]

Monitoring Requirements

B.16.	Fuel Consumption Monitoring of Operations.  The permittee shall monitor and record the rates of consumption of natural gas in accordance with the provisions of 40 CFR 75, Appendix D.  The permittee shall monitor and record the operating rate of the combustion turbine on a daily average basis, considering the number of hours of operation during each day (including the times of startup, shutdown and malfunction).  Such monitoring shall be made using a monitoring component of the CEM system required above, or by monitoring daily rates of consumption and heat content of natural gas in accordance with the provisions of 40 CFR 75, Appendix D.  [Permit No. 0010001-011-AC/PSD-FL-181B]

B.17.	Fuel Consumption Rates Monthly Monitoring.  By the15th calendar day of each month, the permittee shall record the monthly fuel consumption and hours of operation for the CT.  The information shall be recorded in a verifiable manner and shall summarize the previous month of operation and the previous 12 months of operation.  Information recorded and stored as an electronic file shall be available for inspection and printing within at least three days of a request by the Department.  [Permit No. 0010001-011-AC/PSD-FL-181B]

Continuous Monitoring Requirements

B.18.	Continuous Operations Monitoring Systems.  Continuous operations monitoring systems shall be operated and maintained in accordance with 40 CFR 60.334.  The natural gas and steam injection flows to the cogeneration turbine along with the power output of the generator shall be metered and continuously recorded.  The data shall be logged daily and maintained so that it can be provided to the Department upon request.  [Permit No. 0010001-011-AC/PSD-FL-181B]

B.19.	Continuous NOX Emission Monitoring System.  The owner or operator shall calibrate, maintain, and operate a continuous emission monitoring (CEM) system in the stack to measure and record the emissions of NOX from the turbine and the duct burner in a manner sufficient to demonstrate compliance with the emission limits of this permit.  The NOX emission rate in lbs/hr and tons/yr from the cogeneration (CT and DB) stack shall be calculated using a continuous emissions monitoring (CEM) system, which is certified pursuant to 40 CFR 75, and used to determine lbs/MMBtu of NOX.  The CEM system shall be operated and maintained in accordance with the applicable requirements of 40 CFR 75, Subparts B and C.  Missing data shall be substituted in a manner pursuant to 40 CFR 75, Subpart D.  Recordkeeping and reporting shall be conducted pursuant to 40 CFR 75, Subparts F and G.  Excess emissions pursuant to 40 CFR 60.334 shall be determined using the 40 CFR Part 75 CEM system.  The oxygen content or the carbon dioxide (CO2) content of the flue gas shall also be monitored at the location where NOX is monitored to correct the measured NOX emissions rates to 15% oxygen.  [40 CFR 60, Subpart GG & 40 CFR 75; Rule 62-210.700, F.A.C.; Permit No. 0010001-011-AC/PSD-FL-181B; and, Applicant request]

B.20.	Use of NOX CEMS for CT and Duct Burner Compliance.  The permittee has elected to demonstrate compliance with the CT and DB’s NOX emission limits using the NOX CEMS with hourly heat input rates applied to actual operating hours as follows:

a.	Since the CT and DB are in series, the allowable emissions for both emissions units shall be combined for ongoing compliance demonstration purposes.  For the purpose of demonstrating ongoing compliance with the applicable combined emissions limits for both the CT and DB, using the stack CEMS, compliance is considered to occur when the NOX emissions are less than or equal to:

(1)	39.6 lbs/hr when only the CT is operating or,

(2)	58.3 lbs/hr when both the CT and DB are operating and firing natural gas.

b.	The daily rolling average compliance value shall be calculated based on the proportion of hours operated in a day (midnight to midnight) that the CT or both the CT and DB are operating.  Any portion of an hour that the DB operates shall be recognized as an hour-period on the daily operation.  For example, in a given daily timeframe, with 20 hours of CT operation only while firing natural gas and 4 hours of CT/DB operation while firing natural gas:

Calculated Daily NOX Emissions Value = [(39.6 lbs/hr x 20 hrs) + (58.3 lbs/hr x 4 hrs)]/24 hrs =

42.72 lbs/hr daily NOx emissions value

c.	For the 30-day rolling average, this daily calculated emissions value will then be added to the previous 29-day period of daily calculated emission values and divided by 30 (days) to establish the 30-day average emissions value for comparing to the CEMS data over the same 30-day period.

Calculated 30-Day Average NOX Emissions Value =

[42.72 lbs/day + "previous 29-daily emission values (lbs/day) summation"]/30-days =

# lbs/30-day average NOX emissions value

d.	Compliance with the permitted NOX emission limitation is considered satisfied as long as the NOX emissions value from the stack CEMS is less than or equal to the calculated NOX emissions value, averaged over the same 30-day period.

[Rule 62-212.400(12), F.A.C.; 40 CFR 60.44b(a)(4) & (i); and, Permit No. 0010001-011-AC/PSD-FL-181B]

Test Methods and Procedures

B.21.	Test Methods.  Required tests shall be performed in accordance with the following reference methods.

| Method | Description of Method and Comments |
| --- | --- |
| 1-4 | Traverse Points, Velocity and Flow Rate, Gas Analysis, and Moisture Content |
| 5 | Method for Determining Particulate Matter Emissions |
| 7E | Determination of Nitrogen Oxide Emissions from Stationary Sources |
| 9 | Visual Determination of the Opacity of Emissions from Stationary Sources |
| 10 | Determination of Carbon Monoxide Emissions from Stationary Sources {Note: The method shall be based on a continuous sampling train.} |
| 19 | Determination of Sulfur Dioxide Removal Efficiency and Particulate Matter, Sulfur Dioxide, and Nitrogen Oxides Emission Rates (Optional F-factor method may be used to determine flow rate and gas analysis to calculate mass emissions in lieu of Methods 1-4.) |
| 20 | Determination of Nitrogen Oxides, Sulfur Dioxide and Diluent Emissions from Stationary Gas Turbines |
| ASTM D2622-92, ASTM D4294-90, or both ASTM D4057-88 and ASTM D129-91, ASTM D1552 or equivalent method or the latest edition(s) | Standard Test Method for Sulfur in Petroleum Products by Wavelength Dispersive X-ray Fluorescence Spectrometry, Standard Test Method for Sulfur in Petroleum Products by Energy-Dispersive X-Ray Fluorescence Spectroscopy, Standard Practice for Manual Sampling of Petroleum and Petroleum Products, Standard Test Method for Sulfur in Petroleum Products (General Bomb Method), Standard Test Method for Sulfur in Petroleum Products (High-Temperature Method) |
| ASTM4084-82, D3246-81, D5504* or equivalent method or the latest edition(s) | Standard Method for Analysis of Hydrogen Sulfide in Gaseous Fuels (Lead Acetate Reaction Rate Method), Standard Method for Sulfur in Petroleum Gas by Oxidative Microcoulometry |

The above methods are described in 40 CFR 60, Appendix A, and adopted by reference in Rule 62-204.800, F.A.C.  No other methods may be used unless prior written approval is received from the Department.  [Permit No. 0010001-011-AC/PSD-FL-181B; Rules 62-213.440 and 62-297.401, F.A.C.; and, *Applicant Request.]

B.22.	Common Testing Requirements.  Unless otherwise specified, tests shall be conducted in accordance with the requirements and procedures specified in Appendix TR, Facility-Wide Testing Requirements, of this permit.  [Rule 62-297.310(7), F.A.C.]

B.23.	Annual Compliance Tests.  During each federal fiscal year (October 1st to September 30th), the combined cycle combustion turbine system shall be tested to demonstrate compliance with the CO and visible emissions standards.  Due to safety considerations, stack testing while firing the duct burner when there is no demand for steam would require dumping excess steam, which presents a safety issue given the existing configuration. Therefore, subsequent periodic testing for CO emissions may be with the duct burner on or off, as dictated by the system demand. Visible emissions for each backup steam boiler shall be conducted only if No. 2 fuel oil is fired for more than 400 hours during the federal fiscal year.  {Permitting Note: A safety evaluation of the steam vent system indicated that it did not meet code and was deemed unsafe; therefore, it was dismantled.}  [Permit No. 0010001-011-AC/PSD-FL-181B; 0010001-015-AC, Specific Condition 3.]

B.24.	Compliance Tests Prior to Renewal.  Compliance tests shall be performed for NOX, CO, VE and SO2 once every 5 years.  The tests shall occur prior to obtaining a renewed operating permit to demonstrate compliance with the emission limits in Specific Conditions B.8. – B.12.  [Rules 62-210.300(2) & 62-297.310(7)(a), F.A.C.]

B.25.	Visible Emissions.  The test method for visible emissions (VE) shall be EPA Method 9, incorporated and adopted by reference in Rule 62-204.800, F.A.C., and referenced in Chapter 62-297, F.A.C.  [Rules 62-204.800, 62-296.320(4)(b)4.a. & 62-297.401, F.A.C.]

B.26.	Carbon Monoxide.  EPA Method 10 shall be used to demonstrate compliance with the CO limits of this permit, in accordance with Chapter 62-297, F.A.C., and 40 CFR 60, Appendix A.  [Permit No. 0010001-011-AC/PSD-FL-181B]

B.27.	Sulfur Dioxide.  When required, the test method for sulfur dioxide shall be EPA Method 20, incorporated and adopted by reference in Rule 62-204.800, F.A.C., and referenced in Chapter 62-297, F.A.C.  [Rule 62-4.070(3), F.A.C.]

B.28.	Sulfur Dioxide Annual Test Waiver.  In lieu of an annual compliance test for SO2, the fuels fired in the CT and the DB shall meet the sulfur content limits listed in Specific Condition B.12.  Ongoing compliance with the fuel sulfur limit for natural gas shall be demonstrated by the fuel supplier’s analysis reports containing the sulfur content of the fuel being supplied.  Methods for determining the sulfur content of natural gas shall be ASTM methods D4084-82, D3246-81, D5504* or more recent versions or equivalent approved ASTM analytical methods.  Current applicable alternative methods that are approved ASTM methods as adopted in Rule 62-297.440(1), F.A.C. are also acceptable.  At the request of the Department’s Northeast District office, the permittee shall perform additional sampling and analysis for the fuel sulfur content.  [Rules 62-4.070(3) & 62-4.160(15), F.A.C., *Applicant Request, Permit No. 0010001-011-AC/PSD-FL-181B]

{Permitting Note:  The permittee may elect to perform on-site sampling and analysis using the ASTM methods listed above instead of relying upon the vendor’s delivery receipts.}

B.29.	Nitrogen Oxides.  The test methods for NOX shall be EPA Method 7E or EPA Method 20, incorporated and adopted by reference in Rule 62-204.800, F.A.C., and referenced in Chapter 62-297, F.A.C.  Ongoing and annual compliance for the CT, and the CT and DB firing simultaneously, shall be determined by the existing NOX CEM system on a 30-day rolling average basis and reported as required by this permit, except for the following addition/revision.  To verify the facility-wide compliance with the 185.3 TPY cap for NOX emissions, including the CT, the DB and Boilers Nos. 4 and 5 (EUs 002 and 003, respectively), and to provide reasonable assurance that NOX emissions will not be PSD-significant, CEM system records for the CT and DB, along with cumulative fuel consumption records for Boiler Nos. 4 and 5, shall be kept and maintained by the permittee.  The NOX emission rate (lbs/MMBtu) from the CT and DB shall be calculated using the NOX analyzer data and equation F-6 from 40 CFR 75, Appendix F.  Hourly heat input rates (MMBtu/hr) shall be used to convert lbs/MMBtu of NOX to lbs/hr of NOX and actual operating hours shall be used to obtain tons per year.  Total NOX emissions for both the calendar year caps shall be reported in the facility’s annual operating report.  [Rules 62-4.070(3) & 62-212.400(12), F.A.C.; and Permit No 0010001-011-AC/PSD-FL-181B]

{Permitting Note: Because the permittee has agreed to use the NOX CEMS for compliance and the formal annual stack test requirement is being incorporated into the CEMS RATA demonstration, then a separate annual stack test is not required.  However, this does not preclude the imposition of a "Special Compliance Test" pursuant to Rule 62-297.310(7)(b), F.A.C.  (See Appendix TR)}

Recordkeeping and Reporting Requirements

B.30.	Reporting Schedule.  The following reports and notifications shall be submitted to the Compliance Authority:

| Report | Reporting Deadline | Related Condition(s) |
| --- | --- | --- |
| Notice of Excess Emissions | Semi-annually | B.33. |
| Notice of Excess Emissions, Startup, Shutdown and Malfunction | Immediately | B.34. |

B.31.	Other Reporting Requirements.  See Appendix RR, Facility-Wide Reporting Requirements, for additional reporting requirements.

B.32.	NSPS Notifications.  All applicable notifications and reports required by 40 CFR 60, Subpart A, shall be submitted to the Department’s Northeast District office.  [Permit No. 0010001-011-AC/PSD-FL-181B]

B.33.	Semi-Annual Reports.  Semi-annual excess emission reports, in accordance with 40 CFR 60.7(c), shall be submitted to the Department’s Northeast District office.  See Appendix NSPS, Subpart A - General Provisions.  [Permit No. 0010001-011-AC/PSD-FL-181B]

B.34.	Notification of Excess Emissions During Startup, Shutdown, and Documented Unavoidable Malfunctions.  If a CEM system reports emissions in excess of the standard, the permittee shall notify the Department’s Northeast District office within (1) working day with a preliminary report of:  the nature, extent, and duration of the excess emissions; the cause of the excess emissions; and the actions taken to correct the problem.  In addition, the Department may request a written summary report of the incident.  [Rule 62-210.700, F.A.C. and Permit No. 0010001-011-AC/PSD-FL-181B]

The specific conditions in this section apply to the following emissions units:

| E.U. ID No. | Brief Description of Engine |
| --- | --- |
| 009 | Caterpillar 544 HP Diesel Engine Driven Emergency Generator |

The following table provides important details for the RICE engine:

| Engines Description | Engine Brake HP | Date of Purchase | Displacement liters | Model No. |
| --- | --- | --- | --- | --- |
| Diesel Generator | 544 HP (406 KW) | 1986 | <10 | 3406D1 |

{Permitting Note:  These compression ignition reciprocating internal combustion engines (CI RICE) are regulated under 40 CFR 63, Subpart ZZZZ, National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines (RICE) adopted in Rule 62.204.800(11)(b), F.A.C.  This permit section addresses “existing” emergency stationary CI RICE that are located at an area source of HAP and that have not been modified or reconstructed after 6/12/2006.  If the RICE are modified or reconstructed after 7/11/2005, the NSPS 40 CFR 60, Subpart IIII, will then apply.  In accordance with 40 CFR 63.6595(a)(1), the permittee shall comply with the following emissions limitations, operating limitations, and other requirements.}

Essential Potential to Emit (PTE) Parameters

- Hours of Operation.

  - Emergency Situations.  There is no time limit on the use of emergency stationary RICE in emergency situations.  [40 CFR 63.6640(f)(1)]

  - Other Situations.  You may operate your emergency stationary RICE for any combination of the purposes specified in paragraphs (1) of this section for a maximum of 100 hours per calendar year.

    - Maintenance and Testing:  These units are authorized to operate for the purpose of maintenance checks and readiness testing, provided that the tests are recommended by federal, state or local government, the manufacturer, the vendor, or the insurance company associated with the engine.  Maintenance checks and readiness testing of such units is limited to 100 hours per year.  The owner or operator may petition the Administrator for approval of additional hours to be used for maintenance checks and readiness testing, but a petition is not required if the owner or operator maintains records indicating that Federal, State, or local standards require maintenance and testing of emergency RICE beyond 100 hours per year.  [40 CFR 63.6640(f)(2)(i)]

  - Non-emergency Situations.  These units are authorized to operate up to 50 hours per year in non-emergency situations, but those 50 hours are counted towards the 100 hours per year provided for maintenance and testing.  [40 CFR 63.6640(f)(4)]

Emission Limitations and Operating Requirements

- Work or Management Practice Standards.

- Oil.  Change oil and filter every 500 hours of operation or annually, whichever comes first.  [40 CFR 63.6603 & Table 2d.4.a.]

- Air Cleaner.  Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first, and replace as necessary.  [40 CFR 63.6603 & Table 2d.4.b.]

- Hoses and Belts.  Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary.  [40 CFR 63.6603 & Table 2d.4.c.]

- Operation and Maintenance.  Operate and maintain the stationary RICE according to the manufacturer's emission-related operation and maintenance instructions or develop and follow your own maintenance plan which must provide, to the extent practicable for the maintenance and operation of the engine in a manner consistent with good air pollution control practice for minimizing emissions.  [40 CFR 63.6625(e)(3) & Table 6].

- Engine Startup.  During periods of startup the owner or operator must minimize the engine's time spent at idle and minimize the engine's startup time to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes.  [40 CFR 63.6625(h) and Table 2d]

- Oil Analysis.  The owner or operator has the option of using oil analysis to extend the oil change requirement.  The oil analysis must be performed at the same frequency specified for changing the oil in paragraph a., of this condition.  The analysis program must at a minimum analyze the following three parameters:  Total Base Number, viscosity, and percent water content.  The condemning limits for these parameters are as follows:  Total Base Number is less than 30 percent of the Total Base Number of the oil when new; viscosity of the oil has changed by more than 20 percent from the viscosity of the oil when new; or percent water content (by volume) is greater than 0.5.  If all of these condemning limits are not exceeded, the engine owner or operator is not required to change the oil.  If any of the limits are exceeded, the engine owner or operator must change the oil within 2 days of receiving the results of the analysis; if the engine is not in operation when the results of the analysis are received, the engine owner or operator must change the oil within 2 days or before commencing operation, whichever is later.  The owner or operator must keep records of the parameters that are analyzed as part of the program, the results of the analysis, and the oil changes for the engine.  The analysis program must be part of the maintenance plan for the engine.  [40 CFR 63.6625(i)]

Monitoring of Operations

- Hour Meter.  The owner or operator must install a non-resettable hour meter if one is not already installed.  [40 CFR 63.6625(f)]

Compliance

- Continuous Compliance.  Each unit shall be in compliance with the emission limitations, operating limitations, and other requirements in this section at all times.  [40 CFR 63.6605(a)]

- Operation and Maintenance of Equipment.  At all times the owner or operator must operate and maintain, any affected source, including associated air pollution control equipment and monitoring equipment, in a manner consistent with safety and good air pollution control practices for minimizing emissions.  Determination of whether such operation and maintenance procedures are being used will be based on information available to the compliance authority which may include, but is not limited to, monitoring results, review of operation and maintenance procedures, review of operation and maintenance records, and inspection of the source.  [40 CFR 63.6605(b)]

Recordkeeping Requirements

- Notification, Performance and Compliance Records.  The owner or operator must keep.

- A copy of each notification and report that the owner or operator submitted to comply with this section, including all documentation supporting any Initial Notification or Notification of Compliance Status that the owner or operator submitted.

- Records of the occurrence and duration of each malfunction of operation.

- Records of all required maintenance performed on the hour meter.

- Records of actions taken during periods of malfunction to minimize emissions in accordance with specific condition C.5., including corrective actions to restore malfunctioning process and monitoring equipment to its normal or usual manner of operation.

- Records of the actions required in specific condition C.2.d. to show continuous compliance with each emission limitation or operating requirement.

- Records of the Work or Management Practice Standards specified in specific condition C.2.

- Records of the maintenance conducted in order to demonstrate that the RICE was operated and maintained according to your own maintenance plan.

- Records of the hours of operation of the engine that is recorded through the non-resettable hour meter.  The owner or operator must document how many hours are spent for emergency operation including what classified the operation as emergency and how many hours are spent for non-emergency operation.  If the engines are used for emergency demand response operation or for periods of voltage or frequency deviations, the owner or operator must keep records of the notification of the emergency situation, and the time of engine operation for these purposes.

[40 CFR 63.6655]

- Records Retention.

- The owner or operator must keep records in a suitable and readily available form for expeditious reviews.

- The owner or operator must keep each record readily accessible in hard copy or electronic form for at least 5 years after the date of each occurrence, measurement, maintenance, corrective action, report, or record.

[40 CFR 63.6660 and 40 CFR 63.10(b)(1)]

General Provisions

- 40 CFR 63 Subpart A, General Provisions.  The owner or operator shall comply with the following applicable requirements of 40 CFR 63 Subpart A, General Provisions, which have been adopted by reference in Rule 62-204.800(11)(d)1., F.A.C., except that the Secretary is not the Administrator for purposes of 40 CFR 63.5(e), 40 CFR 63.5(f), 40 CFR 63.6(g), 40 CFR 63.6(h)(9), 40 CFR 63.6(j), 40 CFR 63.13, and 40 CFR 63.14.  Link to 40 CFR 63, Subpart A - General Provisions

| General Provisions Citation | Subject of Citation |
| --- | --- |
| §63.1 | General applicability of the General Provisions |
| §63.2 | Definitions (Additional terms defined in §63.6675) |
| §63.3 | Units and abbreviations |
| §63.4 | Prohibited activities and circumvention |
| §63.5 | Construction and reconstruction |
| §63.6(a) | Applicability |
| §63.6(c) | Compliance dates for existing sources |
| §63.9(a) | Applicability and State delegation of notification requirements |
| §63.9(b)(1)–(5) | Initial notifications. Except that §63.9(b)(3) is reserved. |
| §63.9(i) | Adjustment of submittal deadlines |
| §63.9(j) | Change in previous information |
| §63.10(a) | Administrative provisions for recordkeeping/reporting |
| §63.10(b)(1) | Record retention |
| §63.10(b)(2)(vi)–(xi) | Records |
| §63.10(b)(2)(xii) | Record when under waiver |
| §63.10(b)(2)(xiv) | Records of supporting documentation |
| §63.10(b)(3) | Records of applicability determination |
| §63.10(d)(1) | General reporting requirements |
| §63.10(f) | Waiver for recordkeeping/reporting |
| §63.12 | State authority and delegations |
| §63.13 | Addresses |
| §63.14 | Incorporation by reference |
| §63.15 | Availability of information |

[40 CFR 63.6665 & Table 8 to Subpart ZZZZ of Part 63]

Operated By:  Duke Energy Florida, Inc. (DEF)

Plant:  University of Florida Cogeneration Facility

ORIS Code:  7345

The emissions units listed below are regulated under Acid Rain, Phase II.

| EU No. | EPA Unit ID# | Brief Description |
| --- | --- | --- |
| 007 | 1 | General Electric LM6000-PC-ESPRINT Combustion Turbine |

A.1.	The Phase II Acid Rain Part application submitted for this facility, as approved by the Department, is a part of this permit.  The owners and operators of these Phase II acid rain units must comply with the standard requirements and special provisions set forth in the application listed below:

a.	DEP Form No. 62-210.900(1)(a), dated 05/01/14, received 05/16/14.

[Chapter 62-213, F.A.C. and Rule 62-214.320, F.A.C.]

A.2.	Sulfur dioxide (SO2) Emission Allowances.  SO2 emissions from sources subject to the Federal Acid Rain Program (Title IV) shall not exceed any allowances that the source lawfully holds under the Federal Acid Rain Program.  Allowances shall not be used to demonstrate compliance with a non-Title IV applicable requirement of the Act.

a.	No permit revision shall be required for increases in emissions that are authorized by allowances acquired pursuant to the Federal Acid Rain Program, provided that such increases do not require a permit revision pursuant to Rule 62-213.400(3), F.A.C.

b.	No limit shall be placed on the number of allowances held by the source under the Federal Acid Rain Program.

c.	Allowances shall be accounted for under the Federal Acid Rain Program.

[Rule 62-213.440(1)(c)1., 2. & 3., F.A.C.]

A.3.	Comments, notes, and justifications:  None.

Operated by:  Duke Energy Florida, Inc. (DEF)

Plant:  University of Florida Cogeneration Facility

ORIS Code:  7345

The emissions units below are regulated under the Clean Air Interstate Rule.

| EU No. | EPA Unit ID# | Brief Description |
| --- | --- | --- |
| 007 | 1 | General Electric LM6000-PC-ESPRINT Combustion Turbine |

- Clean Air Interstate Rule Application.  The Clean Air Interstate Rule Part Form submitted for this facility is a part of this permit.  The owners and operators of these CAIR units as identified in this form must comply with the standard requirements and special provisions set forth in the CAIR Part Form (DEP Form No. 62-210.900(1)(b)) dated May 16, 2014, which is attached at the end of this section.  [Chapter 62-213, F.A.C. and Rule 62-210.200, F.A.C.]

Appendix A, Glossary.

Appendix HI, Heat Input vs. Inlet temperature Curve.

Appendix I, List of Insignificant Emissions Units and/or Activities.

Appendix NSPS, Subpart A – General Provisions.

Appendix NSPS, Subpart Db – Standards of Performance for Industrial-Commercial-Institutional Steam Generating Units.

Appendix NSPS, Subpart GG – Standards of Performance for Stationary Gas Turbines.

Appendix NESHAP, Subpart A

Appendix NESHAP, Subpart JJJJJJ, National Emission Standards for Hazardous Air Pollutants for Industrial, Commercial, and Institutional Boilers Area Sources

Appendix NESHAP, Subpart ZZZZ, National Emissions Standard for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines (RICE).

Appendix RR, Facility-wide Reporting Requirements.

Appendix TR, Facility-wide Testing Requirements.

Appendix TV, Title V General Conditions.