| Emission Unit & ID No. |  |  |  |  |  | Allowable Emissions |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Pollutant | Fuel(s) | Hrs/Yr |  |  | Basis of Limitation | lbs/hr | TPY |  | Regulation(s)/Permit |  | Permit Condition(s) |
| CT - 007 |  |  |  |  |  |  |  |  |  |  |
| NOx | Gas |  |  |  | 25 ppmvd @ 15% O2 | 39.6 | 142.7 |  | PSD-FL-181B |  | B.8. |
| SO2 | Gas |  |  |  | 0.015% @15% O2 | 2 grains/100 scf |  |  | PSD-FL-181B |  | B.12. |
| VE | Gas |  |  |  |  | 10% opacity |  |  | PSD-FL-181B |  | B.9. |
| CO | Gas |  |  |  | 36.0 ppmvd @ 15% O2 | 38.8 | 158.0 |  | PSD-FL-181B |  | B.8. |
| DB - 005 |  |  |  |  |  |  |  |  |  |  |
| NOx | Gas |  |  |  | 0.1 lb/MMBtu | 18.7 | 24.6 |  | PSD-FL-181B |  | B.4. |
| VE | Gas |  |  |  |  | 10% opacity |  |  | PSD-FL-181B |  | B.4. |
| CO | Gas |  |  |  | 0.15 lb/MMBtu | 28.1 | 36.9 |  | PSD-FL-181B |  | B.4. |
| Boiler No.4 - 002 |  |  |  |  |  |  |  |  |  |  |
| SO2 | Oil |  |  |  | BACT | max. 0.5% S, by wt. |  |  | Rule 62-296.406(3), F.A.C. |  | A.8. |
| VE | Gas/Oil |  |  |  |  | 20%/27%3 (60%4) |  |  | Rule 62-212.400(6), F.A.C. Rule 62-296.406(1), F.A.C.3 Rule 62-210.700(3), F.A.C. |  | A.5. A.5. A.6. |
| Boiler No.5 - 003 |  |  |  |  |  |  |  |  |  |  |
| SO2 | Oil |  |  |  | BACT | max. 0.5% S, by wt. |  |  | Rule 62-296.406(3), F.A.C. |  | A.8 |
| VE | Gas/Oil |  |  |  |  | 20%/27%3 (60%4) |  |  | Rule 62-212.400(6), F.A.C. Rule 62-296.406(1), F.A.C.3 Rule 62-210.700(3), F.A.C. |  | A.5. A.5. A.6. |
| Facility Wide Cap - [E.U.'s - 001, 002, 003 & 004] |  |  |  |  |  |  |  |  |  |  |  |
| Total NOx | Gas/Oil |  |  |  |  |  | 185.3 |  | PSD-FL-181B |  | Facility-wide Condition 10 |

3  Exception is one 6-minute period per hour during which the opacity shall not exceed 27% while firing No. 2 fuel oil..

4  During the 3-hours in any 24 hour period of excess emissions allowed for boiler cleaning (soot blowing) and load change.