Contents

The Following Appendices Are Enforceable Parts of This Permit:

Appendix A, Glossary.

Appendix CAM, Compliance Assurance Monitoring Plan.

Appendix I, List of Insignificant Emissions Units and/or Activities.

Appendix NESHAP, Subpart A – General Provisions.

Appendix NESHAP, Subpart YYYY - National Emission Standards for Hazardous Air Pollutants for Stationary Combustion Turbines.

Appendix NESHAP, Subpart ZZZZ – National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines.

Appendix NSPS, Subpart A – General Provisions.

Appendix NSPS, Subpart GG – Standards of Performance for Stationary Gas Turbines.

Appendix NSPS, Subpart IIII – Standards of Performance for Stationary Compression Ignition Internal    Combustion Engines.

Appendix NSPS, Subpart JJJJ – Standards of Performance for Stationary Spark Ignition Internal Combustion Engines.

Appendix RR, Facility-wide Reporting Requirements.

Appendix TR, Facility-wide Testing Requirements.

Appendix TV, Title V General Conditions.

Appendix U, List of Unregulated Emissions Units and/or Activities.

Referenced Attachments (Included for Convenience and Informational Purposes Only):

Figure 1, Summary Report-Gaseous and Opacity Excess Emission and Monitoring System Performance (40 CFR 60, July, 1996).

Table H, Permit History.

Table 1, Summary of Air Pollutant Standards and Terms.

Table 2, Summary of Compliance Requirements.

Abbreviations and Acronyms:

°F:  degrees Fahrenheit

acfm:  actual cubic feet per minute

AOR:  Annual Operating Report

ARMS:  Air Resource Management System (Department’s database)

BACT:  best available control technology

BHP:  brake horsepower

Btu:  British thermal units

CAA:  Clean Air Act

CAAA:  Clean Air Act Amendments of 1990

CAM:  compliance assurance monitoring

CEMS:  continuous emissions monitoring system

cfm:  cubic feet per minute

CFR:  Code of Federal Regulations

CI:  compression ignition

CO:  carbon monoxide

COMS:  continuous opacity monitoring system

DARM:  Division of Air Resource Management

DCA:  Department of Community Affairs

DEP:  Department of Environmental Protection

Department:  Department of Environmental Protection

dscfm:  dry standard cubic feet per minute

EPA:  Environmental Protection Agency

ESP:  electrostatic precipitator (control system for reducing particulate matter)

EU:  emissions unit

F.A.C.:  Florida Administrative Code

F.D.:  forced draft

F.S.:  Florida Statutes

FGR:  flue gas recirculation

Fl:  fluoride

ft2:  square feet

ft3:  cubic feet

g:  grams

gpm:  gallons per minute

gr:  grains

HAP:  hazardous air pollutant

HP:  horsepower

Hg:  mercury

ICE:  internal combustion engine

I.D.:  induced draft

ID:  identification

ISO:  International Standards Organization (refers to those conditions at 288 Kelvin, 60% relative humidity and 101.3 kilopascals pressure.)

kPa:  kilopascals

kW:  kilowatts

LAT:  Latitude

lb:  pound

lbs/hr:  pounds per hour

LONG:  Longitude

MACT:  maximum achievable technology

mm:  millimeter

MMBtu:  million British thermal units

MSDS:  material safety data sheets

MW:  megawatt

NESHAP:  National Emissions Standards for Hazardous Air Pollutants

NOX:  nitrogen oxides

NSPS:  New Source Performance Standards

O&M:  operation and maintenance

O2:  oxygen

ORIS:  Office of Regulatory Information Systems

OS:  Organic Solvent

Pb:  lead

PM:  particulate matter

PM10:  particulate matter with a mean aerodynamic diameter of 10 microns or less

PSD:  prevention of significant deterioration

psi:  pounds per square inch

PTE:  potential to emit

RACT:  reasonably available control technology

RATA:  relative accuracy test audit

RICE:  reciprocating internal combustion engine

RMP:  Risk Management Plan

RO:  Responsible Official

SAM:  sulfuric acid mist

scf:  standard cubic feet

scfm:  standard cubic feet per minute

SI:  spark ignition

SIC:  standard industrial classification code

SNCR:  selective non-catalytic reduction (control system used for reducing emissions of nitrogen oxides)

SOA:  Specific Operating Agreement

SO2:  sulfur dioxide

TPH:  tons per hour

TPY:  tons per year

UTM:  Universal Transverse Mercator coordinate system

VE:  visible emissions

VOC:  volatile organic compounds

x:   By or times

Citations:

The following examples illustrate the methods used in this permit to abbreviate and cite the references of rules, regulations, guidance memorandums, permit numbers and ID numbers.

Code of Federal Regulations:

Example:	[40 CFR 60.334]

Where:

40   	refers to	Title 40

CFR   	refers to	Code of Federal Regulations

60	refers to	Part 60

60.334	refers to	Regulation 60.334

Florida Administrative Code (F.A.C.) Rules:

Example:	[Rule 62-213.205, F.A.C.]

Where:

62		refers to	Title 62

62-213		refers to	Chapter 62-213

62-213.205   	refers to	Rule 62-213.205, F.A.C.

_____________________________________________________________________________________

Identification Numbers:

Facility Identification (ID) Number:

Example:	Facility ID No.:  1050221

Where:

105  =  3-digit number code identifying the facility is located in Polk County

0221  =  4-digit number assigned by state database.

Permit Numbers:

Example:	1050221-002-AV, or

1050221-001-AC

Where:

AC	  =	Air Construction Permit

AV	  = 	Air Operation Permit (Title V Source)

105	  = 	3-digit number code identifying the facility is located in Polk County

0221	  = 	4-digit number assigned by permit tracking database

001 or 002 = 	3-digit sequential project number assigned by permit tracking database

Example:	PSD-FL-185

PA95-01

AC53-208321

Where:

PSD	=	Prevention of Significant Deterioration Permit

PA  	=	Power Plant Siting Act Permit

AC53	=	old Air Construction Permit numbering identifying the facility is located in Polk County.

Back to Top

Pursuant to Rule 62-213.440(1)(b)1.a., F.A.C., the CAM plans that are included in this appendix contain the monitoring requirements necessary to satisfy 40 CFR 64.  Conditions 1. – 17. are generic conditions applicable to all emissions units that are subject to the CAM requirements.  Specific requirements related to each emissions unit are contained in the attached tables, as submitted by the applicant and approved by the Department.

40 CFR 64.6 Approval of Monitoring.

1.	The attached CAM plan, as submitted by the applicant, is approved for the purposes of satisfying the requirements of 40 CFR 64.3.  [40 CFR 64.6(a)]

2.	The attached CAM plan include the following information:

a.	The indicator(s) to be monitored (such as temperature, pressure drop, emissions, or similar parameter);

b.	The means or device to be used to measure the indicator(s) (such as temperature measurement device, visual observation, or CEMS); and

c.	The performance requirements established to satisfy 40 CFR 64.3(b) or (d), as applicable.

[40 CFR 64.6(c)(1)]

3.	The attached CAM plan describe the means by which the owner or operator will define an exceedance of the permitted limits or an excursion from the stated indicator ranges and averaging periods for purposes of responding to (see CAM Conditions 5. - 9.) and reporting exceedences or excursions (see CAM Conditions 10. – 14.).  [40 CFR 64.6(c)(2)]

4.	The permittee is required to conduct the monitoring specified in the attached CAM plan and shall fulfill the obligations specified in the conditions below (see CAM Conditions 5. - 17.).  [40 CFR 64.6(c)(3)]

40 CFR 64.7 Operation of Approved Monitoring.

5.	Commencement of Operation.  The owner or operator shall conduct the monitoring required under this appendix upon the effective date of this Title V permit.  [40 CFR 64.7(a)]

6.	Proper Maintenance.  At all times, the owner or operator shall maintain the monitoring, including but not limited to, maintaining necessary parts for routine repairs of the monitoring equipment.  [40 CFR 64.7(b)]

7.	Continued Operation.  Except for, as applicable, monitoring malfunctions, associated repairs, and required quality assurance or control activities (including, as applicable, calibration checks and required zero and span adjustments), the owner or operator shall conduct all monitoring in continuous operation (or shall collect data at all required intervals) at all times that the pollutant-specific emissions unit is operating.  Data recorded during monitoring malfunctions, associated repairs, and required quality assurance or control activities shall not be used for purposes of this part, including data averages and calculations, or fulfilling a minimum data availability requirement, if applicable.  The owner or operator shall use all the data collected during all other periods in assessing the operation of the control device and associated control system.  A monitoring malfunction is any sudden, infrequent, not reasonably preventable failure of the monitoring to provide valid data.  Monitoring failures that are caused in part by poor maintenance or careless operation are not malfunctions.  [40 CFR 64.7(c)]

8.	Response to Excursions or Exceedences.

a.	Upon detecting an excursion or exceedance, the owner or operator shall restore operation of the pollutant-specific emissions unit (including the control device and associated capture system) to its normal or usual manner of operation as expeditiously as practicable in accordance with good air pollution control practices for minimizing emissions.  The response shall include minimizing the period of any startup, shutdown or malfunction and taking any necessary corrective actions to restore normal operation and prevent the likely recurrence of the cause of an excursion or exceedance (other than those caused by excused startup or shutdown conditions, if allowed by this permit).  Such actions may include initial inspection and evaluation, recording that operations returned to normal without operator action (such as through response by a computerized distribution control system), or any necessary follow-up actions to return operation to within the indicator range, designated condition, or below the applicable emission limitation or standard, as applicable.

b.	Determination of whether the owner or operator has used acceptable procedures in response to an excursion or exceedance will be based on information available, which may include but is not limited to, monitoring results, review of operation and maintenance procedures and records, and inspection of the control device, associated capture system, and the process.

[40 CFR 64.7(d)(1) & (2)]

9.	Documentation of Need for Improved Monitoring.  If the owner or operator identifies a failure to achieve compliance with an emission limitation or standard for which the approved monitoring did not provide an indication of an excursion or exceedance while providing valid data, or the results of compliance or performance testing document a need to modify the existing indicator ranges or designated conditions, the owner or operator shall promptly notify the permitting authority and, if necessary, submit a proposed modification to the Title V permit to address the necessary monitoring changes.  Such a modification may include, but is not limited to, reestablishing indicator ranges or designated conditions, modifying the frequency of conducting monitoring and collecting data, or the monitoring of additional parameters.  [40 CFR 64.7(e)]

40 CFR 64.8 Quality Improvement Plan (QIP) Requirements.

10.	Based on the results of a determination made under CAM Condition 8.b., above, the permitting authority may require the owner or operator to develop and implement a QIP.  Consistent with CAM Condition 4., an accumulation of exceedences or excursions exceeding 5 percent duration of a pollutant-specific emissions unit's operating time for a reporting period, may require the implementation of a QIP.  The threshold may be set at a higher or lower percent or may rely on other criteria for purposes of indicating whether a pollutant-specific emissions unit is being maintained and operated in a manner consistent with good air pollution control practices.  [40 CFR 64.8(a)]

11.	Elements of a QIP:

a.	The owner or operator shall maintain a written QIP, if required, and have it available for inspection.

b.	The plan initially shall include procedures for evaluating the control performance problems and, based on the results of the evaluation procedures, the owner or operator shall modify the plan to include procedures for conducting one or more of the following actions, as appropriate:

(1)	Improved preventive maintenance practices.

(2)	Process operation changes.

(3)	Appropriate improvements to control methods.

(4)	Other steps appropriate to correct control performance.

(5)	More frequent or improved monitoring (only in conjunction with one or more steps under CAM Condition 11.b(1) through (4), above).

[40 CFR 64.8(b)]

12.	If a QIP is required, the owner or operator shall develop and implement a QIP as expeditiously as practicable and shall notify the permitting authority if the period for completing the improvements contained in the QIP exceeds 180 days from the date on which the need to implement the QIP was determined.  [40 CFR 64.8(c)]

13.	Following implementation of a QIP, upon any subsequent determination pursuant to CAM Condition 8.b., the permitting authority may require that an owner or operator make reasonable changes to the QIP if the QIP is found to have:

a.	Failed to address the cause of the control device performance problems; or

b.	Failed to provide adequate procedures for correcting control device performance problems as expeditiously as practicable in accordance with good air pollution control practices for minimizing emissions.

[40 CFR 64.8(d)]

14.	Implementation of a QIP shall not excuse the owner or operator of a source from compliance with any existing emission limitation or standard, or any existing monitoring, testing, reporting or recordkeeping requirement that may apply under federal, state, or local law, or any other applicable requirements under the Act.  [40 CFR 64.8(e)]

40 CFR 64.9 Reporting And Recordkeeping Requirements.

15.	General Reporting Requirements.

a.	Commencing from the effective date of this permit, the owner or operator shall submit monitoring reports semi-annually to the compliance authority in accordance with Rule 62-213.440(1)(b)3.a., F.A.C.  In addition to deviations from any other permit requirement, the semi-annual reports shall also include all instances of deviations from the CAM requirements.

b.	A report for monitoring under this part shall include, at a minimum, the information required under Rule 62-213.440(1)(b)3.a., F.A.C., and the following information, as applicable:

(1)	Summary information on the number, duration and cause (including unknown cause, if applicable) of excursions or exceedences, as applicable, and the corrective actions taken;

(2)	Summary information on the number, duration and cause (including unknown cause, if applicable) for monitor downtime incidents (other than downtime associated with zero and span or other daily calibration checks, if applicable); and

(3)	A description of the actions taken to implement a QIP during the reporting period as specified in CAM Conditions 10. through 14.  Upon completion of a QIP, the owner or operator shall include in the next summary report documentation that the implementation of the plan has been completed and reduced the likelihood of similar levels of excursions or exceedences occurring.

[40 CFR 64.9(a)]

16.	General Recordkeeping Requirements.

a.	The owner or operator shall comply with the recordkeeping requirements specified in Rule 62-213.440(1)(b)2., F.A.C.  The owner or operator shall maintain records of monitoring data, monitor performance data, corrective actions taken, any written quality improvement plan required pursuant to CAM Conditions 10. through 14. and any activities undertaken to implement a quality improvement plan, and other supporting information required to be maintained under this part (such as data used to document the adequacy of monitoring, or records of monitoring maintenance or corrective actions).

b.	Instead of paper records, the owner or operator may maintain records on alternative media, such as microfilm, computer files, magnetic tape disks, or microfiche, provided that the use of such alternative media allows for expeditious inspection and review, and does not conflict with other applicable recordkeeping requirements.

[40 CFR 64.9(b)]

40 CFR 64.10 Savings Provisions.

17.	It should be noted that nothing in this appendix shall:

a.	Excuse the owner or operator of a source from compliance with any existing emission limitation or standard, or any existing monitoring, testing, reporting or recordkeeping requirement that may apply under federal, state, or local law, or any other applicable requirements under the Act.  The requirements of this appendix shall not be used to justify the approval of monitoring less stringent than the monitoring which is required under separate legal authority and are not intended to establish minimum requirements for the purpose of determining the monitoring to be imposed under separate authority under the Act, including monitoring in permits issued pursuant to Title I of the Act.  The purpose of this part is to require, as part of the issuance of a permit under Title V of the Act, improved or new monitoring at those emissions units where monitoring requirements do not exist or are inadequate to meet the requirements of this part.

b.	Restrict or abrogate the authority of the Administrator or the permitting authority to impose additional or more stringent monitoring, recordkeeping, testing, or reporting requirements on any owner or operator of a source under any provision of the Act, including but not limited to sections 114(a)(1) and 504(b), or state law, as applicable.

c.	Restrict or abrogate the authority of the Administrator or permitting authority to take any enforcement action under the Act for any violation of an applicable requirement or of any person to take action under section 304 of the Act.

[40 CFR 64.10]

Table 1:  Monitoring Approach

|  | Indicator no. 1 | Indicator no. 2 |
| --- | --- | --- |
| - Indicator | Catalyst inlet temperature | Pressure differential across catalyst bed |
| Measurement approach | Thermocouples | Pressure sensors |
| - Indicator range | Minimum temp.: 392° F (200° C) Maximum temp.: 1250° F (677° C) | Maximum pressure diff. = 3” of water column (w.c.) |
|  | An excursion is defined as falling below 392°F (200°C) or rising above 1250°F (677°C) during normal operation. | An excursion is defined as rising above 3” w.c. During normal operation. |
| - Performance criteria |  |  |
| A. Data Representativeness | The thermocouples are located at the inlet face of the catalyst bed. | The pressure sensors are located on the inlet and outlet faces of the catalyst bed. |
| B. Verification of Operational Status | Plant control room operators monitor the alarm system 24 hours/day and record data once per day. | Plant control room operators monitor the alarm system 24 hours/day and record data once per day. |
| C. Qa/Qc Practices and Criteria | Annual testing & calibration of the temperature sensor transmitters. | Annual testing & calibration of the pressure sensor transmitters. |
| D. Monitoring Frequency | Daily | Daily |
| Data Collection Procedures | Temperature readings are recorded daily. | Pressure readings are recorded daily. |
| Averaging Procedures | Na (monitoring data does not correspond to actual emissions rate). | Na (monitoring data does not correspond to actual emissions rate). |

Back to Top

The facilities, emissions units, or pollutant-emitting activities listed in Rule 62-210.300(3)(a), F.A.C., Categorical Exemptions, are exempt from the permitting requirements of Chapters 62-210 and 62-4, F.A.C.; provided, however, that exempt emissions units shall be subject to any applicable emission limiting standards and the emissions from exempt emissions units or activities shall be considered in determining the potential emissions of the facility containing such emissions units.  Emissions units and pollutant-emitting activities exempt from permitting under Rule 62-210.300(3)(a), F.A.C., shall not be exempt from the permitting requirements of Chapter 62-213, F.A.C., if they are contained within a Title V source; however, such emissions units and activities shall be considered insignificant for Title V purposes provided they also meet the criteria of Rule 62-213.430(6)(b), F.A.C.  No emissions unit shall be entitled to an exemption from permitting under Rule 62.210.300(3)(a), F.A.C., if its emissions, in combination with the emissions of other units and activities at the facility, would cause the facility to emit or have the potential to emit any pollutant in such amount as to make the facility a Title V source.

The below listed emissions units and/or activities are considered insignificant pursuant to Rule 62-213.430(6), F.A.C.

| 1. Applications of fungicides, herbicides and pesticides. |  |
| --- | --- |
| 2. Battery charging. |  |
| 3. Blueprint reproduction. |  |
| 4. Brazing, soldering and welding. |  |
| 5. Campfires. |  |
| 6. Compressed air systems, including air compressors and driers. |  |
| 7. Degasifiers. |  |
| 8. Electric drying oven with no air pollutant emissions expected. |  |
| 9. Equipment used exclusively for space heating. |  |
| 10. Equipment used exclusively to sand and shape wood or plastic. |  |
| 11. Fireplaces. |  |
| 12. Fresh water cooling towers. |  |
| 13. Generator venting. |  |
| 14. HVAC and chiller units that are in compliance with Rule 62-213.300(3)(o), F.A.C. |  |
| 15. Inorganic substance storage tanks >550 gallons. |  |
| 16. Kitchen exhaust. |  |
| 17. Laboratory hood vents. |  |
| 18. Latex injection. |  |
| 19. Laundry dryers. |  |
| 20. Lube oil tank vents. |  |
| 21. Lube oil vents associated with rotating equipment. |  |
| 22. Maintenance activity associated with transformers, switches, switchgear processing (including cleaning, changing and venting). |  |
| 23. Natural gas gate and compression station, including odorant addition equipment. |  |
| 24. Natural gas system maintenance. |  |
| 25. Office equipment and office ventilation. |  |
| 26. Oil and organic solvent storage tanks >550 gallons |  |
| 27. Oil truck unloading equipment. |  |
| 28. Oil/water separators. |  |
| 29. Parts cleaning and degreasing stations, except for those subject to Rule 62-213.300(1)(c), F.A.C. |  |
| 30. Pool heaters with less than 1 MMBtu/hr maximum gross heat output each. |  |
| 31. Portable kerosene space heaters. |  |
| 32. Recycling operations, including sorting, compacting and baling. |  |
| 33. Refrigeration systems that are in compliance with Rule 62-213.300(3)(o), F.A.C. |  |
| 34. Routine maintenance and repair activities, except painting |  |
| 35. Sewage treatment facilities. |  |
| 36. Sewer line vents. |  |
| 37. Silk screening. |  |
| 38. Smokehouse. |  |
| 39. Special effects. |  |
| 40. Stack test sampling equipment. |  |
| 41. Tiki torches. |  |
| 42. Turbine vapor extractor. |  |
| 43. Miscellaneous Architectural painting |  |
| 44. Water heaters used for comfort heating with less than 1 MMBtu/hr maximum gross heat output each: |  |
|  | a. Disney’s Animal Kingdom. Fifty-three (53) natural gas fired radiant comfort heaters with a gross maximum heat output of less than one million Btu per hour per unit pursuant to Rule 62-210.300(3)(a)4., F.A.C. (DAKE-1 thru DAKE-53) |
| 45. Two (2) petroleum solvent dry cleaning machines with a total solvent consumption of less than 3,250 gallons per year pursuant to Rule 62-210.300(3)(a)25., F.A.C. |  |
| 46. Floral Department Spray Booth. This unit is used for spraying floral arrangements and other products for floral displays. The maximum potential VOC emissions are approximately 350 lb/yr (0.18 tpy). |  |
| 47. Studio Scenic Shop Spray Booth. This unit is used for spraying show props and scenic materials. The maximum potential VOC emissions are approximately are approximately 200 lb/yr (0.1 tpy). |  |

Back to Top

Link to 40 CFR 63, Subpart A - General Provisions

Back to Top

##### Federal Regulations Adopted by Reference

##### In accordance with Rule 62-204.800, F.A.C., the following federal regulation in Title 40 of the Code of Federal Regulations (CFR) was adopted by reference.

##### 40 CFR 63, Subpart YYYY - National Emissions Standards for Hazardous Air Pollutants for Stationary Combustion Turbines

##### Link to 40 CFR 63, Subpart YYYY

Applicability of NESHAP Subpart YYYY

Pursuant to Subpart YYYY, Emissions Unit 088 is an affected source that meets the criteria for a “new stationary combustion turbine” because construction commenced after January 14, 2003 at a major source of HAP.

Staying of the Rule

On August 18, 2004, the U.S. EPA stayed the effectiveness of 40 CFR 63, Subpart YYYY for lean premix gas turbines.  The following is the federal regulation amendment that stays the effectiveness of 40 CFR 63, Subpart YYYY:

§ 63.6095(d) Stay of standards for gas-fired subcategories.

If you start up a new or reconstructed stationary combustion turbine that is a lean premix gas-fired stationary combustion turbine or diffusion flame gas-fired stationary combustion turbine as defined by this subpart, you must comply with the Initial Notification requirements set forth in Sec. 63.6145 but need not comply with any other requirement of this subpart until EPA takes final action to require compliance and publishes a document in the Federal Register.

Requirements

The applicable requirements in 40 CFR 63, Subpart YYYY are:

§ 63.6145 What notifications must I submit and when?

- You must submit all of the notifications in §§ 63.7(b) and (c), 63.8(e), 63.8(f)(4), and 63.9(b) and (h) that apply to you by the dates specified.

- As specified in § 63.9(b)(2), if you start up your new or reconstructed stationary combustion turbine before March 5, 2004, you must submit an Initial Notification not later than 120 calendar days after March 5, 2004.

- As specified in § 63.9(b), if you start up your new or reconstructed stationary combustion turbine on or after March 5, 2004, you must submit an Initial Notification not later than 120 calendar days after you become subject to this subpart.

- If you are required to submit an Initial Notification but are otherwise not affected by the emission limitation requirements of this subpart, in accordance with § 63.6090(b), your notification must include the information in § 63.9(b)(2)(i) through (v) and a statement that your new or reconstructed stationary combustion turbine has no additional emission limitation requirements and must explain the basis of the exclusion (for example, that it operates exclusively as an emergency stationary combustion turbine).

- If you are required to conduct an initial performance test, you must submit a notification of intent to conduct an initial performance test at least 60 calendar days before the initial performance test is scheduled to begin as required in § 63.7(b)(1).

- If you are required to comply with the emission limitation for formaldehyde, you must submit a Notification of Compliance Status according to § 63.9(h)(2)(ii).  For each performance test required to demonstrate compliance with the emission limitation for formaldehyde, you must submit the Notification of Compliance Status, including the performance test results, before the close of business on the 60th calendar day following the completion of the performance test.

Back to Top

Link to 40 CFR 63, Subpart ZZZZ

Back to Top

##### Link to 40 CFR 60, Subpart A - General Provisions

Back to Top

##### Federal Regulations Adopted by Reference

##### In accordance with Rule 62-204.800, F.A.C., the following federal regulation in Title 40 of the Code of Federal Regulations (CFR) was adopted by reference.  The original federal rule numbering has been retained.

##### Federal Revision Date:  February 24, 2006

##### State Rule Effective Date:  July 1, 2006

##### Standardized Conditions Revision Date:  August 6, 2009

##### 40 CFR Part 60, Subpart GG - Standards of Performance for Stationary Gas Turbines

##### § 60.330   Applicability and designation of affected facility.

(a)	The provisions of this subpart are applicable to the following affected facilities: All stationary gas turbines with a heat input at peak load equal to or greater than 10.7 gigajoules (10 million Btu) per hour, based on the lower heating value of the fuel fired.

(b)	Any facility under paragraph (a) of this section which commences construction, modification, or reconstruction after October 3, 1977, is subject to the requirements of this part except as provided in paragraphs (e) and (j) of §60.332.

[44 FR 52798, Sept. 10, 1979, as amended at 52 FR 42434, Nov. 5, 1987; 65 FR 61759, Oct. 17, 2000]

##### § 60.331   Definitions.

As used in this subpart, all terms not defined herein shall have the meaning given them in the Act and in subpart A of this part.

(a)	Stationary gas turbine means any simple cycle gas turbine, regenerative cycle gas turbine or any gas turbine portion of a combined cycle steam/electric generating system that is not self propelled. It may, however, be mounted on a vehicle for portability.

(b)	Simple cycle gas turbine means any stationary gas turbine which does not recover heat from the gas turbine exhaust gases to preheat the inlet combustion air to the gas turbine, or which does not recover heat from the gas turbine exhaust gases to heat water or generate steam.

(c)	Regenerative cycle gas turbine means any stationary gas turbine which recovers heat from the gas turbine exhaust gases to preheat the inlet combustion air to the gas turbine.

(d)	Combined cycle gas turbine means any stationary gas turbine which recovers heat from the gas turbine exhaust gases to heat water or generate steam.

(e)	Emergency gas turbine means any stationary gas turbine which operates as a mechanical or electrical power source only when the primary power source for a facility has been rendered inoperable by an emergency situation.

(f)	Ice fog means an atmospheric suspension of highly reflective ice crystals.

(g)	ISO standard day conditions means 288 degrees Kelvin, 60 percent relative humidity and 101.3 kilopascals pressure.

(h)	Efficiency means the gas turbine manufacturer's rated heat rate at peak load in terms of heat input per unit of power output based on the lower heating value of the fuel.

(i)	Peak load means 100 percent of the manufacturer's design capacity of the gas turbine at ISO standard day conditions.

(j)	Base load means the load level at which a gas turbine is normally operated.

(k)	Fire-fighting turbine means any stationary gas turbine that is used solely to pump water for extinguishing fires.

(l)	Turbines employed in oil/gas production or oil/gas transportation means any stationary gas turbine used to provide power to extract crude oil/natural gas from the earth or to move crude oil/natural gas, or products refined from these substances through pipelines.

(m)	A Metropolitan Statistical Area or MSA as defined by the Department of Commerce.

(n)	Offshore platform gas turbines means any stationary gas turbine located on a platform in an ocean.

(o)	Garrison facility means any permanent military installation.

(p)	Gas turbine model means a group of gas turbines having the same nominal air flow, combuster inlet pressure, combuster inlet temperature, firing temperature, turbine inlet temperature and turbine inlet pressure.

(q)	Electric utility stationary gas turbine means any stationary gas turbine constructed for the purpose of supplying more than one-third of its potential electric output capacity to any utility power distribution system for sale.

(r)	Emergency fuel is a fuel fired by a gas turbine only during circumstances, such as natural gas supply curtailment or breakdown of delivery system, that make it impossible to fire natural gas in the gas turbine.

(s)	Unit operating hour means a clock hour during which any fuel is combusted in the affected unit. If the unit combusts fuel for the entire clock hour, it is considered to be a full unit operating hour. If the unit combusts fuel for only part of the clock hour, it is considered to be a partial unit operating hour.

(t)	Excess emissions means a specified averaging period over which either:

(1)	The NOX emissions are higher than the applicable emission limit in §60.332;

(2)	The total sulfur content of the fuel being combusted in the affected facility exceeds the limit specified in §60.333; or

(3)	The recorded value of a particular monitored parameter is outside the acceptable range specified in the parameter monitoring plan for the affected unit.

(u)	Natural gas means a naturally occurring fluid mixture of hydrocarbons ( e.g. , methane, ethane, or propane) produced in geological formations beneath the Earth's surface that maintains a gaseous state at standard atmospheric temperature and pressure under ordinary conditions. Natural gas contains 20.0 grains or less of total sulfur per 100 standard cubic feet. Equivalents of this in other units are as follows: 0.068 weight percent total sulfur, 680 parts per million by weight (ppmw) total sulfur, and 338 parts per million by volume (ppmv) at 20 degrees Celsius total sulfur. Additionally, natural gas must either be composed of at least 70 percent methane by volume or have a gross calorific value between 950 and 1100 British thermal units (Btu) per standard cubic foot. Natural gas does not include the following gaseous fuels: landfill gas, digester gas, refinery gas, sour gas, blast furnace gas, coal-derived gas, producer gas, coke oven gas, or any gaseous fuel produced in a process which might result in highly variable sulfur content or heating value.

(v)	Duct burner means a device that combusts fuel and that is placed in the exhaust duct from another source, such as a stationary gas turbine, internal combustion engine, kiln, etc., to allow the firing of additional fuel to heat the exhaust gases before the exhaust gases enter a heat recovery steam generating unit.

(w)	Lean premix stationary combustion turbine means any stationary combustion turbine where the air and fuel are thoroughly mixed to form a lean mixture for combustion in the combustor. Mixing may occur before or in the combustion chamber. A unit which is capable of operating in both lean premix and diffusion flame modes is considered a lean premix stationary combustion turbine when it is in the lean premix mode, and it is considered a diffusion flame stationary combustion turbine when it is in the diffusion flame mode.

(x)	Diffusion flame stationary combustion turbine means any stationary combustion turbine where fuel and air are injected at the combustor and are mixed only by diffusion prior to ignition. A unit which is capable of operating in both lean premix and diffusion flame modes is considered a lean premix stationary combustion turbine when it is in the lean premix mode, and it is considered a diffusion flame stationary combustion turbine when it is in the diffusion flame mode.

(y)	Unit operating day means a 24-hour period between 12:00 midnight and the following midnight during which any fuel is combusted at any time in the unit. It is not necessary for fuel to be combusted continuously for the entire 24-hour period.

[44 FR 52798, Sept. 10, 1979, as amended at 47 FR 3770, Jan. 27, 1982; 65 FR 61759, Oct. 17, 2000; 69 FR 41359, July 8, 2004]

##### § 60.332   Standard for nitrogen oxides.

(a)	On and after the date on which the performance test required by §60.8 is completed, every owner or operator subject to the provisions of this subpart as specified in paragraphs (b), (c), and (d) of this section shall comply with one of the following, except as provided in paragraphs (e), (f), (g), (h), (i), (j), (k), and (l) of this section.

(1)	No owner or operator subject to the provisions of this subpart shall cause to be discharged into the atmosphere from any stationary gas turbine, any gases which contain nitrogen oxides in excess of:

where:

STD  =  allowable ISO corrected (if required as given in §60.335(b)(1)) NOX emission concentration (percent by volume at 15 percent oxygen and on a dry basis),

Y  =  manufacturer's rated heat rate at manufacturer's rated load (kilojoules per watt hour) or, actual measured heat rate based on lower heating value of fuel as measured at actual peak load for the facility. The value of Y shall not exceed 14.4 kilojoules per watt hour, and

F  =  NOX emission allowance for fuel-bound nitrogen as defined in paragraph (a)(4) of this section.

(2)	No owner or operator subject to the provisions of this subpart shall cause to be discharged into the atmosphere from any stationary gas turbine, any gases which contain nitrogen oxides in excess of:

where:

STD  =  allowable ISO corrected (if required as given in §60.335(b)(1)) NOX emission concentration (percent by volume at 15 percent oxygen and on a dry basis),

Y  =  manufacturer's rated heat rate at manufacturer's rated peak load (kilojoules per watt hour), or actual measured heat rate based on lower heating value of fuel as measured at actual peak load for the facility. The value of Y shall not exceed 14.4 kilojoules per watt hour, and

F  =  NOX emission allowance for fuel-bound nitrogen as defined in paragraph (a)(4) of this section.

(3)	The use of F in paragraphs (a)(1) and (2) of this section is optional. That is, the owner or operator may choose to apply a NOX allowance for fuel-bound nitrogen and determine the appropriate F-value in accordance with paragraph (a)(4) of this section or may accept an F-value of zero.

(4)	If the owner or operator elects to apply a NOX emission allowance for fuel-bound nitrogen, F shall be defined according to the nitrogen content of the fuel during the most recent performance test required under §60.8 as follows:

| Fuel-bound nitrogen (percent by weight) | F (NOX percent by volume) |
| --- | --- |
| N ≤ 0.015 | 0 |
| 0.015 < N≤ 0.1 | 0.04(N) |
| 0.1 < N ≤ 0.25 | 0.004+0.0067(N–0.1) |
| N > 0.25 | 0.005 |

Where:

N  =  the nitrogen content of the fuel (percent by weight).

or:

Manufacturers may develop and submit to EPA custom fuel-bound nitrogen allowances for each gas turbine model they manufacture. These fuel-bound nitrogen allowances shall be substantiated with data and must be approved for use by the Administrator before the initial performance test required by §60.8. Notices of approval of custom fuel-bound nitrogen allowances will be published in the Federal Register.

(b)	Electric utility stationary gas turbines with a heat input at peak load greater than 107.2 gigajoules per hour (100 million Btu/hour) based on the lower heating value of the fuel fired shall comply with the provisions of paragraph (a)(1) of this section.

(c)	Stationary gas turbines with a heat input at peak load equal to or greater than 10.7 gigajoules per hour (10 million Btu/hour) but less than or equal to 107.2 gigajoules per hour (100 million Btu/hour) based on the lower heating value of the fuel fired, shall comply with the provisions of paragraph (a)(2) of this section.

(d)	Stationary gas turbines with a manufacturer's rated base load at ISO conditions of 30 megawatts or less except as provided in §60.332(b) shall comply with paragraph (a)(2) of this section.

(e)	Stationary gas turbines with a heat input at peak load equal to or greater than 10.7 gigajoules per hour (10 million Btu/hour) but less than or equal to 107.2 gigajoules per hour (100 million Btu/hour) based on the lower heating value of the fuel fired and that have commenced construction prior to October 3, 1982 are exempt from paragraph (a) of this section.

(f)	Stationary gas turbines using water or steam injection for control of NOX emissions are exempt from paragraph (a) when ice fog is deemed a traffic hazard by the owner or operator of the gas turbine.

(g)	Emergency gas turbines, military gas turbines for use in other than a garrison facility, military gas turbines installed for use as military training facilities, and fire fighting gas turbines are exempt from paragraph (a) of this section.

(h)	Stationary gas turbines engaged by manufacturers in research and development of equipment for both gas turbine emission control techniques and gas turbine efficiency improvements are exempt from paragraph (a) on a case-by-case basis as determined by the Administrator.

(i)	Exemptions from the requirements of paragraph (a) of this section will be granted on a case-by-case basis as determined by the Administrator in specific geographical areas where mandatory water restrictions are required by governmental agencies because of drought conditions. These exemptions will be allowed only while the mandatory water restrictions are in effect.

(j)	Stationary gas turbines with a heat input at peak load greater than 107.2 gigajoules per hour that commenced construction, modification, or reconstruction between the dates of October 3, 1977, and January 27, 1982, and were required in the September 10, 1979, Federal Register(44 FR 52792) to comply with paragraph (a)(1) of this section, except electric utility stationary gas turbines, are exempt from paragraph (a) of this section.

(k)	Stationary gas turbines with a heat input greater than or equal to 10.7 gigajoules per hour (10 million Btu/hour) when fired with natural gas are exempt from paragraph (a)(2) of this section when being fired with an emergency fuel.

(l)	Regenerative cycle gas turbines with a heat input less than or equal to 107.2 gigajoules per hour (100 million Btu/hour) are exempt from paragraph (a) of this section.

[44 FR 52798, Sept. 10, 1979, as amended at 47 FR 3770, Jan. 27, 1982; 65 FR 61759, Oct. 17, 2000; 69 FR 41359, July 8, 2004]

##### § 60.333   Standard for sulfur dioxide.

On and after the date on which the performance test required to be conducted by §60.8 is completed, every owner or operator subject to the provision of this subpart shall comply with one or the other of the following conditions:

(a)	No owner or operator subject to the provisions of this subpart shall cause to be discharged into the atmosphere from any stationary gas turbine any gases which contains sulfur dioxide in excess of 0.015 percent by volume at 15 percent oxygen and on a dry basis.

(b)	No owner or operator subject to the provisions of this subpart shall burn in any stationary gas turbine any fuel which contains total sulfur in excess of 0.8 percent by weight (8000 ppmw).

[44 FR 52798, Sept. 10, 1979, as amended at 69 FR 41360, July 8, 2004]

##### § 60.334   Monitoring of operations.

(a)	Except as provided in paragraph (b) of this section, the owner or operator of any stationary gas turbine subject to the provisions of this subpart and using water or steam injection to control NOX emissions shall install, calibrate, maintain and operate a continuous monitoring system to monitor and record the fuel consumption and the ratio of water or steam to fuel being fired in the turbine.

(b)	The owner or operator of any stationary gas turbine that commenced construction, reconstruction or modification after October 3, 1977, but before July 8, 2004, and which uses water or steam injection to control NOX emissions may, as an alternative to operating the continuous monitoring system described in paragraph (a) of this section, install, certify, maintain, operate, and quality-assure a continuous emission monitoring system (CEMS) consisting of NOX and O2 monitors. As an alternative, a CO2 monitor may be used to adjust the measured NOX concentrations to 15 percent O2 by either converting the CO2 hourly averages to equivalent O2 concentrations using Equation F–14a or F–14b in appendix F to part 75 of this chapter and making the adjustments to 15 percent O2, or by using the CO2 readings directly to make the adjustments, as described in Method 20. If the option to use a CEMS is chosen, the CEMS shall be installed, certified, maintained and operated as follows:

(1)	Each CEMS must be installed and certified according to PS 2 and 3 (for diluent) of 40 CFR part 60, appendix B, except the 7-day calibration drift is based on unit operating days, not calendar days. Appendix F, Procedure 1 is not required. The relative accuracy test audit (RATA) of the NOX and diluent monitors may be performed individually or on a combined basis, i.e. , the relative accuracy tests of the CEMS may be performed either:

(i)	On a ppm basis (for NOX) and a percent O2 basis for oxygen; or

(ii)	On a ppm at 15 percent O2 basis; or

(iii)	On a ppm basis (for NOX) and a percent CO2 basis (for a CO2 monitor that uses the procedures in Method 20 to correct the NOX data to 15 percent O2).

(2)	As specified in §60.13(e)(2), during each full unit operating hour, each monitor must complete a minimum of one cycle of operation (sampling, analyzing, and data recording) for each 15-minute quadrant of the hour, to validate the hour. For partial unit operating hours, at least one valid data point must be obtained for each quadrant of the hour in which the unit operates. For unit operating hours in which required quality assurance and maintenance activities are performed on the CEMS, a minimum of two valid data points (one in each of two quadrants) are required to validate the hour.

(3)	For purposes of identifying excess emissions, CEMS data must be reduced to hourly averages as specified in §60.13(h).

(i)	For each unit operating hour in which a valid hourly average, as described in paragraph (b)(2) of this section, is obtained for both NOX and diluent, the data acquisition and handling system must calculate and record the hourly NOX emissions in the units of the applicable NOX emission standard under §60.332(a), i.e. , percent NOX by volume, dry basis, corrected to 15 percent O2 and International Organization for Standardization (ISO) standard conditions (if required as given in §60.335(b)(1)). For any hour in which the hourly average O2 concentration exceeds 19.0 percent O2, a diluent cap value of 19.0 percent O2 may be used in the emission calculations.

(ii)	A worst case ISO correction factor may be calculated and applied using historical ambient data. For the purpose of this calculation, substitute the maximum humidity of ambient air (Ho), minimum ambient temperature (Ta), and minimum combustor inlet absolute pressure (Po) into the ISO correction equation.

(iii)	If the owner or operator has installed a NOX CEMS to meet the requirements of part 75 of this chapter, and is continuing to meet the ongoing requirements of part 75 of this chapter, the CEMS may be used to meet the requirements of this section, except that the missing data substitution methodology provided for at 40 CFR part 75, subpart D, is not required for purposes of identifying excess emissions. Instead, periods of missing CEMS data are to be reported as monitor downtime in the excess emissions and monitoring performance report required in §60.7(c).

(c)	For any turbine that commenced construction, reconstruction or modification after October 3, 1977, but before July 8, 2004, and which does not use steam or water injection to control NOX emissions, the owner or operator may, but is not required to, for purposes of determining excess emissions, use a CEMS that meets the requirements of paragraph (b) of this section. Also, if the owner or operator has previously submitted and received EPA, State, or local permitting authority approval of a procedure for monitoring compliance with the applicable NOX emission limit under §60.332, that approved procedure may continue to be used.

(d)	The owner or operator of any new turbine constructed after July 8, 2004, and which uses water or steam injection to control NOX emissions may elect to use either the requirements in paragraph (a) of this section for continuous water or steam to fuel ratio monitoring or may use a NOX CEMS installed, certified, operated, maintained, and quality-assured as described in paragraph (b) of this section.

(e)	The owner or operator of any new turbine that commences construction after July 8, 2004, and which does not use water or steam injection to control NOX emissions, may, but is not required to, elect to use a NOX CEMS installed, certified, operated, maintained, and quality-assured as described in paragraph (b) of this section. Other acceptable monitoring approaches include periodic testing approved by EPA or the State or local permitting authority or continuous parameter monitoring as described in paragraph (f) of this section.

(f)	The owner or operator of a new turbine that commences construction after July 8, 2004, which does not use water or steam injection to control NOX emissions may, but is not required to, perform continuous parameter monitoring as follows:

(1)	For a diffusion flame turbine without add-on selective catalytic reduction controls (SCR), the owner or operator shall define at least four parameters indicative of the unit's NOX formation characteristics and shall monitor these parameters continuously.

(2)	For any lean premix stationary combustion turbine, the owner or operator shall continuously monitor the appropriate parameters to determine whether the unit is operating in low-NOX mode.

(3)	For any turbine that uses SCR to reduce NOX emissions, the owner or operator shall continuously monitor appropriate parameters to verify the proper operation of the emission controls.

(4)	For affected units that are also regulated under part 75 of this chapter, if the owner or operator elects to monitor NOX emission rate using the methodology in appendix E to part 75 of this chapter, or the low mass emissions methodology in §75.19 of this chapter, the requirements of this paragraph (f) may be met by performing the parametric monitoring described in section 2.3 of appendix E or in §75.19(c)(1)(iv)(H) of this chapter.

(g)	The steam or water to fuel ratio or other parameters that are continuously monitored as described in paragraphs (a), (d) or (f) of this section shall be monitored during the performance test required under §60.8, to establish acceptable values and ranges. The owner or operator may supplement the performance test data with engineering analyses, design specifications, manufacturer's recommendations and other relevant information to define the acceptable parametric ranges more precisely. The owner or operator shall develop and keep on-site a parameter monitoring plan which explains the procedures used to document proper operation of the NOX emission controls. The plan shall include the parameter(s) monitored and the acceptable range(s) of the parameter(s) as well as the basis for designating the parameter(s) and acceptable range(s). Any supplemental data such as engineering analyses, design specifications, manufacturer's recommendations and other relevant information shall be included in the monitoring plan. For affected units that are also subject to part 75 of this chapter and that use the low mass emissions methodology in §75.19 of this chapter or the NOX emission measurement methodology in appendix E to part 75, the owner or operator may meet the requirements of this paragraph by developing and keeping on-site (or at a central location for unmanned facilities) a quality-assurance plan, as described in §75.19 (e)(5) or in section 2.3 of appendix E and section 1.3.6 of appendix B to part 75 of this chapter.

(h)	The owner or operator of any stationary gas turbine subject to the provisions of this subpart:

(1)	Shall monitor the total sulfur content of the fuel being fired in the turbine, except as provided in paragraph (h)(3) of this section. The sulfur content of the fuel must be determined using total sulfur methods described in §60.335(b)(10). Alternatively, if the total sulfur content of the gaseous fuel during the most recent performance test was less than 0.4 weight percent (4000 ppmw), ASTM D4084–82, 94, D5504–01, D6228–98, or Gas Processors Association Standard 2377–86 (all of which are incorporated by reference-see §60.17), which measure the major sulfur compounds may be used; and

(2)	Shall monitor the nitrogen content of the fuel combusted in the turbine, if the owner or operator claims an allowance for fuel bound nitrogen ( i.e. , if an F-value greater than zero is being or will be used by the owner or operator to calculate STD in §60.332). The nitrogen content of the fuel shall be determined using methods described in §60.335(b)(9) or an approved alternative.

(3)	Notwithstanding the provisions of paragraph (h)(1) of this section, the owner or operator may elect not to monitor the total sulfur content of the gaseous fuel combusted in the turbine, if the gaseous fuel is demonstrated to meet the definition of natural gas in §60.331(u), regardless of whether an existing custom schedule approved by the administrator for subpart GG requires such monitoring. The owner or operator shall use one of the following sources of information to make the required demonstration:

(i)	The gas quality characteristics in a current, valid purchase contract, tariff sheet or transportation contract for the gaseous fuel, specifying that the maximum total sulfur content of the fuel is 20.0 grains/100 scf or less; or

(ii)	Representative fuel sampling data which show that the sulfur content of the gaseous fuel does not exceed 20 grains/100 scf. At a minimum, the amount of fuel sampling data specified in section 2.3.1.4 or 2.3.2.4 of appendix D to part 75 of this chapter is required.

(4)	For any turbine that commenced construction, reconstruction or modification after October 3, 1977, but before July 8, 2004, and for which a custom fuel monitoring schedule has previously been approved, the owner or operator may, without submitting a special petition to the Administrator, continue monitoring on this schedule.

(i)	The frequency of determining the sulfur and nitrogen content of the fuel shall be as follows:

(1)	Fuel oil. For fuel oil, use one of the total sulfur sampling options and the associated sampling frequency described in sections 2.2.3, 2.2.4.1, 2.2.4.2, and 2.2.4.3 of appendix D to part 75 of this chapter ( i.e. , flow proportional sampling, daily sampling, sampling from the unit's storage tank after each addition of fuel to the tank, or sampling each delivery prior to combining it with fuel oil already in the intended storage tank). If an emission allowance is being claimed for fuel-bound nitrogen, the nitrogen content of the oil shall be determined and recorded once per unit operating day.

(2)	Gaseous fuel. Any applicable nitrogen content value of the gaseous fuel shall be determined and recorded once per unit operating day. For owners and operators that elect not to demonstrate sulfur content using options in paragraph (h)(3) of this section, and for which the fuel is supplied without intermediate bulk storage, the sulfur content value of the gaseous fuel shall be determined and recorded once per unit operating day.

(3)	Custom schedules. Notwithstanding the requirements of paragraph (i)(2) of this section, operators or fuel vendors may develop custom schedules for determination of the total sulfur content of gaseous fuels, based on the design and operation of the affected facility and the characteristics of the fuel supply. Except as provided in paragraphs (i)(3)(i) and (i)(3)(ii) of this section, custom schedules shall be substantiated with data and shall be approved by the Administrator before they can be used to comply with the standard in §60.333.

(i)	The two custom sulfur monitoring schedules set forth in paragraphs (i)(3)(i)(A) through (D) and in paragraph (i)(3)(ii) of this section are acceptable, without prior Administrative approval:

(A)	The owner or operator shall obtain daily total sulfur content measurements for 30 consecutive unit operating days, using the applicable methods specified in this subpart. Based on the results of the 30 daily samples, the required frequency for subsequent monitoring of the fuel's total sulfur content shall be as specified in paragraph (i)(3)(i)(B), (C), or (D) of this section, as applicable.

(B)	If none of the 30 daily measurements of the fuel's total sulfur content exceeds 0.4 weight percent (4000 ppmw), subsequent sulfur content monitoring may be performed at 12 month intervals. If any of the samples taken at 12-month intervals has a total sulfur content between 0.4 and 0.8 weight percent (4000 and 8000 ppmw), follow the procedures in paragraph (i)(3)(i)(C) of this section. If any measurement exceeds 0.8 weight percent (8000 ppmw), follow the procedures in paragraph (i)(3)(i)(D) of this section.

(C)	If at least one of the 30 daily measurements of the fuel's total sulfur content is between 0.4 and 0.8 weight percent (4000 and 8000 ppmw), but none exceeds 0.8 weight percent (8000 ppmw), then:

( 1 )	Collect and analyze a sample every 30 days for three months. If any sulfur content measurement exceeds 0.8 weight percent (8000 ppmw), follow the procedures in paragraph (i)(3)(i)(D) of this section. Otherwise, follow the procedures in paragraph (i)(3)(i)(C)( 2 ) of this section.

( 2 )	Begin monitoring at 6-month intervals for 12 months. If any sulfur content measurement exceeds 0.8 weight percent (8000 ppmw), follow the procedures in paragraph (i)(3)(i)(D) of this section. Otherwise, follow the procedures in paragraph (i)(3)(i)(C)( 3 ) of this section.

( 3 )	Begin monitoring at 12-month intervals. If any sulfur content measurement exceeds 0.8 weight percent (8000 ppmw), follow the procedures in paragraph (i)(3)(i)(D) of this section. Otherwise, continue to monitor at this frequency.

(D)	If a sulfur content measurement exceeds 0.8 weight percent (8000 ppmw), immediately begin daily monitoring according to paragraph (i)(3)(i)(A) of this section. Daily monitoring shall continue until 30 consecutive daily samples, each having a sulfur content no greater than 0.8 weight percent (8000 ppmw), are obtained. At that point, the applicable procedures of paragraph (i)(3)(i)(B) or (C) of this section shall be followed.

(ii)	The owner or operator may use the data collected from the 720-hour sulfur sampling demonstration described in section 2.3.6 of appendix D to part 75 of this chapter to determine a custom sulfur sampling schedule, as follows:

(A)	If the maximum fuel sulfur content obtained from the 720 hourly samples does not exceed 20 grains/100 scf ( i.e. , the maximum total sulfur content of natural gas as defined in §60.331(u)), no additional monitoring of the sulfur content of the gas is required, for the purposes of this subpart.

(B)	If the maximum fuel sulfur content obtained from any of the 720 hourly samples exceeds 20 grains/100 scf, but none of the sulfur content values (when converted to weight percent sulfur) exceeds 0.4 weight percent (4000 ppmw), then the minimum required sampling frequency shall be one sample at 12 month intervals.

(C)	If any sample result exceeds 0.4 weight percent sulfur (4000 ppmw), but none exceeds 0.8 weight percent sulfur (8000 ppmw), follow the provisions of paragraph (i)(3)(i)(C) of this section.

(D)	If the sulfur content of any of the 720 hourly samples exceeds 0.8 weight percent (8000 ppmw), follow the provisions of paragraph (i)(3)(i)(D) of this section.

(j)	For each affected unit that elects to continuously monitor parameters or emissions, or to periodically determine the fuel sulfur content or fuel nitrogen content under this subpart, the owner or operator shall submit reports of excess emissions and monitor downtime, in accordance with §60.7(c). Excess emissions shall be reported for all periods of unit operation, including startup, shutdown and malfunction. For the purpose of reports required under §60.7(c), periods of excess emissions and monitor downtime that shall be reported are defined as follows:

(1)	Nitrogen oxides.

(i)	For turbines using water or steam to fuel ratio monitoring:

(A)	An excess emission shall be any unit operating hour for which the average steam or water to fuel ratio, as measured by the continuous monitoring system, falls below the acceptable steam or water to fuel ratio needed to demonstrate compliance with §60.332, as established during the performance test required in §60.8. Any unit operating hour in which no water or steam is injected into the turbine shall also be considered an excess emission.

(B)	A period of monitor downtime shall be any unit operating hour in which water or steam is injected into the turbine, but the essential parametric data needed to determine the steam or water to fuel ratio are unavailable or invalid.

(C)	Each report shall include the average steam or water to fuel ratio, average fuel consumption, ambient conditions (temperature, pressure, and humidity), gas turbine load, and (if applicable) the nitrogen content of the fuel during each excess emission. You do not have to report ambient conditions if you opt to use the worst case ISO correction factor as specified in §60.334(b)(3)(ii), or if you are not using the ISO correction equation under the provisions of §60.335(b)(1).

(ii)	If the owner or operator elects to take an emission allowance for fuel bound nitrogen, then excess emissions and periods of monitor downtime are as described in paragraphs (j)(1)(ii)(A) and (B) of this section.

(A)	An excess emission shall be the period of time during which the fuel-bound nitrogen (N) is greater than the value measured during the performance test required in §60.8 and used to determine the allowance. The excess emission begins on the date and hour of the sample which shows that N is greater than the performance test value, and ends with the date and hour of a subsequent sample which shows a fuel nitrogen content less than or equal to the performance test value.

(B)	A period of monitor downtime begins when a required sample is not taken by its due date. A period of monitor downtime also begins on the date and hour that a required sample is taken, if invalid results are obtained. The period of monitor downtime ends on the date and hour of the next valid sample.

(iii)	For turbines using NOX and diluent CEMS:

(A)	An hour of excess emissions shall be any unit operating hour in which the 4-hour rolling average NOX concentration exceeds the applicable emission limit in §60.332(a)(1) or (2). For the purposes of this subpart, a “4-hour rolling average NOX concentration” is the arithmetic average of the average NOX concentration measured by the CEMS for a given hour (corrected to 15 percent O2 and, if required under §60.335(b)(1), to ISO standard conditions) and the three unit operating hour average NOX concentrations immediately preceding that unit operating hour.

(B)	A period of monitor downtime shall be any unit operating hour in which sufficient data are not obtained to validate the hour, for either NOX concentration or diluent (or both).

(C)	Each report shall include the ambient conditions (temperature, pressure, and humidity) at the time of the excess emission period and (if the owner or operator has claimed an emission allowance for fuel bound nitrogen) the nitrogen content of the fuel during the period of excess emissions. You do not have to report ambient conditions if you opt to use the worst case ISO correction factor as specified in §60.334(b)(3)(ii), or if you are not using the ISO correction equation under the provisions of §60.335(b)(1).

(iv)	For owners or operators that elect, under paragraph (f) of this section, to monitor combustion parameters or parameters that document proper operation of the NOX emission controls:

(A)	An excess emission shall be a 4-hour rolling unit operating hour average in which any monitored parameter does not achieve the target value or is outside the acceptable range defined in the parameter monitoring plan for the unit.

(B)	A period of monitor downtime shall be a unit operating hour in which any of the required parametric data are either not recorded or are invalid.

(2)	Sulfur dioxide. If the owner or operator is required to monitor the sulfur content of the fuel under paragraph (h) of this section:

(i)	For samples of gaseous fuel and for oil samples obtained using daily sampling, flow proportional sampling, or sampling from the unit's storage tank, an excess emission occurs each unit operating hour included in the period beginning on the date and hour of any sample for which the sulfur content of the fuel being fired in the gas turbine exceeds 0.8 weight percent and ending on the date and hour that a subsequent sample is taken that demonstrates compliance with the sulfur limit.

(ii)	If the option to sample each delivery of fuel oil has been selected, the owner or operator shall immediately switch to one of the other oil sampling options ( i.e. , daily sampling, flow proportional sampling, or sampling from the unit's storage tank) if the sulfur content of a delivery exceeds 0.8 weight percent. The owner or operator shall continue to use one of the other sampling options until all of the oil from the delivery has been combusted, and shall evaluate excess emissions according to paragraph (j)(2)(i) of this section. When all of the fuel from the delivery has been burned, the owner or operator may resume using the as-delivered sampling option.

(iii)	A period of monitor downtime begins when a required sample is not taken by its due date. A period of monitor downtime also begins on the date and hour of a required sample, if invalid results are obtained. The period of monitor downtime shall include only unit operating hours, and ends on the date and hour of the next valid sample.

(3)	Ice fog. Each period during which an exemption provided in §60.332(f) is in effect shall be reported in writing to the Administrator quarterly. For each period the ambient conditions existing during the period, the date and time the air pollution control system was deactivated, and the date and time the air pollution control system was reactivated shall be reported. All quarterly reports shall be postmarked by the 30th day following the end of each calendar quarter.

(4)	Emergency fuel. Each period during which an exemption provided in §60.332(k) is in effect shall be included in the report required in §60.7(c). For each period, the type, reasons, and duration of the firing of the emergency fuel shall be reported.

(5)	All reports required under §60.7(c) shall be postmarked by the 30th day following the end of each 6-month period.

[44 FR 52798, Sept. 10, 1979, as amended at 47 FR 3770, Jan. 27, 1982; 65 FR 61759, Oct. 17, 2000; 69 FR 41360, July 8, 2004; 71 FR 9457, Feb. 24, 2006]

##### § 60.335   Test methods and procedures.

(a)	The owner or operator shall conduct the performance tests required in §60.8, using either

(1)	EPA Method 20,

(2)	ASTM D6522–00 (incorporated by reference, see §60.17), or

(3)	EPA Method 7E and either EPA Method 3 or 3A in appendix A to this part, to determine NOX and diluent concentration.

(4)	Sampling traverse points are to be selected following Method 20 or Method 1, (non-particulate procedures) and sampled for equal time intervals. The sampling shall be performed with a traversing single-hole probe or, if feasible, with a stationary multi-hole probe that samples each of the points sequentially. Alternatively, a multi-hole probe designed and documented to sample equal volumes from each hole may be used to sample simultaneously at the required points.

(5)	Notwithstanding paragraph (a)(4) of this section, the owner or operator may test at few points than are specified in Method 1 or Method 20 if the following conditions are met:

(i)	You may perform a stratification test for NOX and diluent pursuant to

(A)	[Reserved]

(B)	The procedures specified in section 6.5.6.1(a) through (e) appendix A to part 75 of this chapter.

(ii)	Once the stratification sampling is completed, the owner or operator may use the following alternative sample point selection criteria for the performance test:

(A)	If each of the individual traverse point NOX concentrations, normalized to 15 percent O2, is within ±10 percent of the mean normalized concentration for all traverse points, then you may use 3 points (located either 16.7, 50.0, and 83.3 percent of the way across the stack or duct, or, for circular stacks or ducts greater than 2.4 meters (7.8 feet) in diameter, at 0.4, 1.2, and 2.0 meters from the wall). The 3 points shall be located along the measurement line that exhibited the highest average normalized NOX concentration during the stratification test; or

(B)	If each of the individual traverse point NOX concentrations, normalized to 15 percent O2, is within ±5 percent of the mean normalized concentration for all traverse points, then you may sample at a single point, located at least 1 meter from the stack wall or at the stack centroid.

(6)	Other acceptable alternative reference methods and procedures are given in paragraph (c) of this section.

(b)	The owner or operator shall determine compliance with the applicable nitrogen oxides emission limitation in §60.332 and shall meet the performance test requirements of §60.8 as follows:

(1)	For each run of the performance test, the mean nitrogen oxides emission concentration (NOXo) corrected to 15 percent O2 shall be corrected to ISO standard conditions using the following equation. Notwithstanding this requirement, use of the ISO correction equation is optional for: Lean premix stationary combustion turbines; units used in association with heat recovery steam generators (HRSG) equipped with duct burners; and units equipped with add-on emission control devices:

NOX  =  (NOXo)(Pr/Po)0.5 e19 (Ho−0.00633)(288°K/Ta)1.53

Where:

NOX  =  emission concentration of NOX at 15 percent O2and ISO standard ambient conditions, ppm by volume, dry basis,

NOXo  =  mean observed NOX concentration, ppm by volume, dry basis, at 15 percent O2,

Pr  =  reference combustor inlet absolute pressure at 101.3 kilopascals ambient pressure, mm Hg,

Po  =  observed combustor inlet absolute pressure at test, mm Hg,

Ho  =  observed humidity of ambient air, g H2O/g air,

e  =  transcendental constant, 2.718, and

Ta  =  ambient temperature, °K.

(2)	The 3-run performance test required by §60.8 must be performed within ±5 percent at 30, 50, 75, and 90-to-100 percent of peak load or at four evenly-spaced load points in the normal operating range of the gas turbine, including the minimum point in the operating range and 90-to-100 percent of peak load, or at the highest achievable load point if 90-to-100 percent of peak load cannot be physically achieved in practice. If the turbine combusts both oil and gas as primary or backup fuels, separate performance testing is required for each fuel. Notwithstanding these requirements, performance testing is not required for any emergency fuel (as defined in §60.331).

(3)	For a combined cycle turbine system with supplemental heat (duct burner), the owner or operator may elect to measure the turbine NOX emissions after the duct burner rather than directly after the turbine. If the owner or operator elects to use this alternative sampling location, the applicable NOX emission limit in §60.332 for the combustion turbine must still be met.

(4)	If water or steam injection is used to control NOX with no additional post-combustion NOX control and the owner or operator chooses to monitor the steam or water to fuel ratio in accordance with §60.334(a), then that monitoring system must be operated concurrently with each EPA Method 20, ASTM D6522–00 (incorporated by reference, see §60.17), or EPA Method 7E run and shall be used to determine the fuel consumption and the steam or water to fuel ratio necessary to comply with the applicable §60.332 NOX emission limit.

(5)	If the owner operator elects to claim an emission allowance for fuel bound nitrogen as described in §60.332, then concurrently with each reference method run, a representative sample of the fuel used shall be collected and analyzed, following the applicable procedures described in §60.335(b)(9). These data shall be used to determine the maximum fuel nitrogen content for which the established water (or steam) to fuel ratio will be valid.

(6)	If the owner or operator elects to install a CEMS, the performance evaluation of the CEMS may either be conducted separately (as described in paragraph (b)(7) of this section) or as part of the initial performance test of the affected unit.

(7)	If the owner or operator elects to install and certify a NOX CEMS under §60.334(e), then the initial performance test required under §60.8 may be done in the following alternative manner:

(i)	Perform a minimum of 9 reference method runs, with a minimum time per run of 21 minutes, at a single load level, between 90 and 100 percent of peak (or the highest physically achievable) load.

(ii)	Use the test data both to demonstrate compliance with the applicable NOX emission limit under §60.332 and to provide the required reference method data for the RATA of the CEMS described under §60.334(b).

(iii)	The requirement to test at three additional load levels is waived.

(8)	If the owner or operator elects under §60.334(f) to monitor combustion parameters or parameters indicative of proper operation of NOX emission controls, the appropriate parameters shall be continuously monitored and recorded during each run of the initial performance test, to establish acceptable operating ranges, for purposes of the parameter monitoring plan for the affected unit, as specified in §60.334(g).

(9)	To determine the fuel bound nitrogen content of fuel being fired (if an emission allowance is claimed for fuel bound nitrogen), the owner or operator may use equipment and procedures meeting the requirements of:

(i)	For liquid fuels, ASTM D2597–94 (Reapproved 1999), D6366–99, D4629–02, D5762–02 (all of which are incorporated by reference, see §60.17); or

(ii)	For gaseous fuels, shall use analytical methods and procedures that are accurate to within 5 percent of the instrument range and are approved by the Administrator.

(10)	If the owner or operator is required under §60.334(i)(1) or (3) to periodically determine the sulfur content of the fuel combusted in the turbine, a minimum of three fuel samples shall be collected during the performance test. Analyze the samples for the total sulfur content of the fuel using:

(i)	For liquid fuels, ASTM D129–00, D2622–98, D4294–02, D1266–98, D5453–00 or D1552–01 (all of which are incorporated by reference, see §60.17); or

(ii)	For gaseous fuels, ASTM D1072–80, 90 (Reapproved 1994); D3246–81, 92, 96; D4468–85 (Reapproved 2000); or D6667–01 (all of which are incorporated by reference, see §60.17). The applicable ranges of some ASTM methods mentioned above are not adequate to measure the levels of sulfur in some fuel gases. Dilution of samples before analysis (with verification of the dilution ratio) may be used, subject to the prior approval of the Administrator.

(11)	The fuel analyses required under paragraphs (b)(9) and (b)(10) of this section may be performed by the owner or operator, a service contractor retained by the owner or operator, the fuel vendor, or any other qualified agency.

(c)	The owner or operator may use the following as alternatives to the reference methods and procedures specified in this section:

(1)	Instead of using the equation in paragraph (b)(1) of this section, manufacturers may develop ambient condition correction factors to adjust the nitrogen oxides emission level measured by the performance test as provided in §60.8 to ISO standard day conditions.

[69 FR 41363, July 8, 2004, as amended at 71 FR 9458, Feb. 24, 2006]

Back to Top

Link to 40 CFR 60, Subpart IIII

Back to Top

Link to 40 CFR 60, Subpart JJJJ

Back to Top

RR1.	Reporting Schedule.	This table summarizes information for convenience purposes only.  It does not supersede any of the terms or conditions of this permit.

| Report | Reporting Deadline(s) | Related Condition(s) |
| --- | --- | --- |
| Plant Problems/Permit Deviations | Immediately upon occurrence (See RR2.d.) | RR2, RR3 |
| Malfunction Excess Emissions Report | Quarterly (if requested) | RR3 |
| Semi-Annual Monitoring Report | Every 6 months | RR4 |
| Annual Operating Report | April 1 | RR5 |
| EAOR Title V Annual Emissions Fee Invoice and Fee Payment | April 1 | RR6 |
| Annual Statement of Compliance | Within 60 days after the end of each calendar year (or more frequently if specified by Rule 62-213.440(2), F.A.C., or by any other applicable requirement); and Within 60 days after submittal of a written agreement for transfer of responsibility, or Within 60 days after permanent shutdown. | RR7 |
| Notification of Administrative Permit Corrections | As needed | RR8 |
| Notification of Startup after Shutdown for More than One Year | Minimum of 60 days prior to the intended startup date or, if emergency startup, as soon as possible after the startup date is ascertained | RR9 |
| Permit Renewal Application | 225 days prior to the expiration date of permit | TV17 |
| Test Reports | Maximum 45 days following compliance tests | TR8 |

{Permitting Note:  See permit Section III.  Emissions Units and Specific Conditions, for any additional Emission Unit-specific reporting requirements.}

RR2.	Reports of Problems.

a.	Plant Operation-Problems.  If the permittee is temporarily unable to comply with any of the conditions of the permit due to breakdown of equipment or destruction by hazard of fire, wind or by other cause, the permittee shall immediately notify the Department. Notification shall include pertinent information as to the cause of the problem, and what steps are being taken to correct the problem and to prevent its recurrence, and where applicable, the owner's intent toward reconstruction of destroyed facilities.  Such notification does not release the permittee from any liability for failure to comply with Department rules.

b.	If, for any reason, the permittee does not comply with or will be unable to comply with any condition or limitation specified in this permit, the permittee shall immediately provide the Department with the following information:

(1)	A description of and cause of noncompliance; and

(2)	The period of noncompliance, including dates and times; or, if not corrected, the anticipated time the noncompliance is expected to continue, and steps being taken to reduce, eliminate, and prevent recurrence of the noncompliance.  The permittee shall be responsible for any and all damages which may result and may be subject to enforcement action by the Department for penalties or for revocation of this permit.

c.	When requested by the Department, the permittee shall within a reasonable time furnish any information required by law which is needed to determine compliance with the permit.  If the permittee becomes aware the relevant facts were not submitted or were incorrect in the permit application or in any report to the Department, such facts or information shall be corrected promptly.

d.	“Immediately” shall mean the same day, if during a workday (i.e., 8:00 a.m. - 5:00 p.m.), or the first business day after the incident, excluding weekends and holidays; and, for purposes of Rule 62-4.160(15) and 40 CFR 70.6(a)(3)(iii)(B), “promptly” or "prompt"  shall have the same meaning as "immediately".

[Rule 62-4.130, Rule 62-4.160(8), Rule 62-4.160(15), and Rule 62-213.440(1)(b), F.A.C.; 40 CFR 70.6(a)(3)(iii)(B)]

RR3.	Reports of Deviations from Permit Requirements.  The permittee shall report in accordance with the requirements of Rule 62-210.700(6), F.A.C. (below), and Rule 62-4.130, F.A.C. (condition RR2.), deviations from permit requirements, including those attributable to upset conditions as defined in the permit.  Reports shall include the probable cause of such deviations, and any corrective actions or preventive measures taken.

Rule 62-210.700(6):  In case of excess emissions resulting from malfunctions, each owner or operator shall notify the Department or the appropriate Local Program in accordance with Rule 62-4.130, F.A.C. (See condition RR2.).  A full written report on the malfunctions shall be submitted in a quarterly report, if requested by the Department.

[Rules 62-213.440(1)(b)3.b., and 62-210.700(6)F.A.C.]

RR4.	Semi-Annual Monitoring Reports.  The permittee shall submit reports of any required monitoring at least every six (6) months.  All instances of deviations from permit requirements must be clearly identified in such reports.  [Rule 62-213.440(1)(b)3.a., F.A.C.]

RR5.	Annual Operating Report.  The information required by the Annual Operating Report for Air Pollutant Emitting Facility [Including Title V Source Emissions Fee Calculation] (DEP Form No. 62-210.900(5)) shall be submitted by April 1 of each year, for the previous calendar year, to the Department of Environmental Protection’s Division of Air Resource Management.  Each Title V source shall submit the annual operating report using the DEP’s Electronic Annual Operating Report (EAOR) software, unless the Title V source claims a technical or financial hardship by submitting DEP Form No. 62-210.900(5) to the DEP Division of Air Resource Management instead of using the reporting software. Emissions shall be computed in accordance with the provisions of subsection 62-210.370(2), F.A.C.  [Rules 62-210.370(2) & (3), 62-210.900 and 62-213.440(3)(a)2., F.A.C.]

RR6.	EAOR Title V Annual Emissions Fee Invoice and Fee Payment.  Each Title V source permitted to operate in Florida must pay between January 15 and April 1 of each year, an annual emissions fee in an amount determined as set forth in Rule 62-213.205(1), F.A.C.

- If the Department has not received the fee by March 1 of the year following the calendar year for which the fee is calculated, the Department will send the primary responsible official of the Title V source a written warning of the consequences for failing to pay the fee by April 1. If the fee is not postmarked or electronically submitted by April 1 of the year due, the Department shall impose, in addition to the fee, a penalty of 50 percent of the amount of the fee unpaid plus interest on such amount computed in accordance with Section 220.807, F.S. If the Department determines that a submitted fee was inaccurately calculated, the Department shall either refund to the permittee any amount overpaid or notify the permittee of any amount underpaid. The Department shall not impose a penalty or interest on any amount underpaid, provided that the permittee has timely remitted payment of at least 90 percent of the amount determined to be due and remits full payment within 60 days after receipt of notice of the amount underpaid. The Department shall waive the collection of underpayment and shall not refund overpayment of the fee, if the amount is less than one percent of the fee due, up to $50.00. The Department shall make every effort to provide a timely assessment of the adequacy of the submitted fee. Failure to pay timely any required annual emissions fee, penalty, or interest constitutes grounds for permit revocation pursuant to Rule 62-4.100, F.A.C.

b.	Any documentation of actual hours of operation, actual material or heat input, actual production amount, or actual emissions used to calculate the annual emissions fee shall be retained by the owner for a minimum of five years and shall be made available to the Department upon request.

c.	A copy of the EAOR Title V Annual Emissions Fee Invoice generated by the electronic annual operating report (EAOR) application, must be submitted along with the annual emissions fee payment.

[Rules 62-210.370(3), 62-210.900  and 62-213.205, F.A.C.]

RR7.	Annual Statement of Compliance.

a.	The permittee shall submit a Statement of Compliance with all terms and conditions of the permit that includes all the provisions of 40 CFR 70.6(c)(5)(iii), incorporated by reference at Rule 62-204.800, F.A.C., using DEP Form No. 62-213.900(2).  Such statement shall be accompanied by a certification in accordance with Rule 62-213.420(4), F.A.C., for Title V requirements and with Rule 62-214.350, F.A.C., for Acid Rain requirements.  Such statements shall be submitted (postmarked) to the Department and EPA:

(1)	Annually, within 60 days after the end of each calendar year during which the Title V permit was effective, or more frequently if specified by Rule 62-213.440(2), F.A.C., or by any other applicable requirement; and

(2)	Within 60 days after submittal of a written agreement for transfer of responsibility as required pursuant to 40 CFR 70.7(d)(1)(iv), adopted and incorporated by reference at Rule 62-204.800, F.A.C., or within 60 days after permanent shutdown of a facility permitted under Chapter 62-213, F.A.C.; provided that, in either such case, the reporting period shall be the portion of the calendar year the permit was effective up to the date of transfer of responsibility or permanent facility shutdown, as applicable.

b.	In lieu of individually identifying all applicable requirements and specifying times of compliance with, non-compliance with, and deviation from each, the responsible official may use DEP Form No. 62-213.900(2) as such statement of compliance so long as the responsible official identifies all reportable deviations from and all instances of non-compliance with any applicable requirements and includes all information required by the federal regulation relating to each reportable deviation and instance of non-compliance.

c.	The responsible official may treat compliance with all other applicable requirements as a surrogate for compliance with Rule 62-296.320(2), Objectionable Odor Prohibited.

[Rules 62-213.440(3)(a)2. & 3. and (b), F.A.C.]

RR8.	Notification of Administrative Permit Corrections.

A facility owner shall notify the Department by letter of minor corrections to information contained in a permit.  Such notifications shall include:

a.	Typographical errors noted in the permit;

b.	Name, address or phone number change from that in the permit;

c.	A change requiring more frequent monitoring or reporting by the permittee;

d.	A change in ownership or operational control of a facility, subject to the following provisions:

(1)	The Department determines that no other change in the permit is necessary;

(2)	The permittee and proposed new permittee have submitted an Application for Transfer of Air Permit, and the Department has approved the transfer pursuant to Rule 62-210.300(7), F.A.C.; and

(3)	The new permittee has notified the Department of the effective date of sale or legal transfer.

e.	Changes listed at 40 CFR 72.83(a)(1), (2), (6), (9) and (10), adopted and incorporated by reference at Rule 62-204.800, F.A.C., and changes made pursuant to Rules 62-214.340(1) and (2), F.A.C., to Title V sources subject to emissions limitations or reductions pursuant to 42 USC ss. 7651-7651o;

f.	Changes listed at 40 CFR 72.83(a)(11) and (12), adopted and incorporated by reference at Rule 62-204.800, F.A.C., to Title V sources subject to emissions limitations or reductions pursuant to 42 USC ss. 7651-7651o, provided the notification is accompanied by a copy of any EPA determination concerning the similarity of the change to those listed at Rule 62-210.360(1)(e), F.A.C.; and

g.	Any other similar minor administrative change at the source.

[Rule 62-210.360, F.A.C.]

RR9.	Notification of Startup.  The owners or operator of any emissions unit or facility which has a valid air operation permit which has been shut down more than one year, shall notify the Department in writing of the intent to start up such emissions unit or facility, a minimum of 60 days prior to the intended startup date.

a.	The notification shall include information as to the startup date, anticipated emission rates or pollutants released, changes to processes or control devices which will result in changes to emission rates, and any other conditions which may differ from the valid outstanding operation permit.

b.	If, due to an emergency, a startup date is not known 60 days prior thereto, the owner shall notify the Department as soon as possible after the date of such startup is ascertained.

[Rule 62-210.300(5), F.A.C.]

RR10.	Report Submission.  The permittee shall submit all compliance related notifications and reports required of this permit to the Compliance Authority.  {See front of permit for address and phone number.}

RR11.	EPA Report Submission.  Any reports, data, notifications, certifications, and requests required to be sent to the United States Environmental Protection Agency, Region 4, should be sent to:  Air, Pesticides & Toxics Management Division, United States Environmental Protection Agency, Region 4, Sam Nunn Atlanta Federal Center, 61 Forsyth Street SW, Atlanta, GA  30303-8960.  Phone:  404/562-9077.

RR12.	Acid Rain Report Submission.  Acid Rain Program Information shall be submitted, as necessary, to:  Department of Environmental Protection, 2600 Blair Stone Road, Mail Station #5510, Tallahassee, Florida  32399-2400.  Phone:  850/488-6140.  Fax:  850/922-6979.

RR13.	Report Certification.  All reports shall be accompanied by a certification by a responsible official, pursuant to Rule 62-213.420(4), F.A.C.  [Rule 62-213.440(1)(b)3.c, F.A.C.]

RR14.	Certification by Responsible Official (RO).  In addition to the professional engineering certification required for applications by Rule 62-4.050(3), F.A.C., any application form, report, compliance statement, compliance plan and compliance schedule submitted pursuant to Chapter 62-213, F.A.C., shall contain a certification signed by a responsible official that, based on information and belief formed after reasonable inquiry, the statements and information in the document are true, accurate, and complete.  Any responsible official who fails to submit any required information or who has submitted incorrect information shall, upon becoming aware of such failure or incorrect submittal, promptly submit such supplementary information or correct information.  [Rule 62-213.420(4), F.A.C.]

RR15.	Confidential Information.  Whenever an applicant submits information under a claim of confidentiality pursuant to Section 403.111, F.S., the applicant shall also submit a copy of all such information and claim directly to EPA.  Any permittee may claim confidentiality of any data or other information by complying with this procedure.  [Rules 62-213.420(2), and 62-213.440(1)(d)6., F.A.C.]

RR16.	Forms and Instructions.  The forms used by the Department in the Title V source operation program are adopted and incorporated by reference in Rule 62-213.900, F.A.C.  The forms are listed by rule number, which is also the form number, and with the subject, title, and effective date.  Copies of forms may be obtained by writing to the Department of Environmental Protection, Division of Air Resource Management, 2600 Blair Stone Road, Tallahassee, Florida  32399-2400, by contacting the appropriate permitting authority or by accessing the Department’s web site at: http://www.dep.state.fl.us/air/rules/forms.htm.

a.	 Annual Operating Report for Air Pollutant Emitting Facility [Including Title V Source Emissions Fee Calculation] (DEP Form No. 62-210.900(5)) (Effective 12/31/2013)

b.	Statement of Compliance Form (Effective 06/02/2002).

c.	Responsible Official Notification Form (Effective 06/02/2002).

[Rule 62-213.900, F.A.C.:  Forms (1), (7) and (8)]

Back to Top

Unless otherwise specified in the permit, the following testing requirements apply to each emissions unit for which testing is required.  The terms “stack” and “duct” are used interchangeably in this appendix.

TR1.	Required Number of Test Runs.  For mass emission limitations, a compliance test shall consist of three complete and separate determinations of the total air pollutant emission rate through the test section of the stack or duct and three complete and separate determinations of any applicable process variables corresponding to the three distinct time periods during which the stack emission rate was measured; provided, however, that three complete and separate determinations shall not be required if the process variables are not subject to variation during a compliance test, or if three determinations are not necessary in order to calculate the unit's emission rate.  The three required test runs shall be completed within one consecutive five-day period.  In the event that a sample is lost or one of the three runs must be discontinued because of circumstances beyond the control of the owner or operator, and a valid third run cannot be obtained within the five-day period allowed for the test, the Secretary or his or her designee may accept the results of two complete runs as proof of compliance, provided that the arithmetic mean of the two complete runs is at least 20% below the allowable emission limiting standard.  [Rule 62-297.310(1), F.A.C.]

TR2.	Operating Rate During Testing.  Testing of emissions shall be conducted with the emissions unit operating at permitted capacity.  If it is impractical to test at permitted capacity, an emissions unit may be tested at less than the maximum permitted capacity; in this case, subsequent emissions unit operation is limited to 110 percent of the test rate until a new test is conducted.  Once the unit is so limited, operation at higher capacities is allowed for no more than 15 consecutive days for the purpose of additional compliance testing to regain the authority to operate at the permitted capacity.  Permitted capacity is defined as 90 to 100 percent of the maximum operation rate allowed by the permit.  [Rule 62-297.310(2), F.A.C.]

TR3.	Calculation of Emission Rate.  For each emissions performance test, the indicated emission rate or concentration shall be the arithmetic average of the emission rate or concentration determined by each of the three separate test runs unless otherwise specified in a particular test method or applicable rule.  [Rule 62-297.310(3), F.A.C.]

TR4. 	Applicable Test Procedures.

a.	Required Sampling Time.

(1)	Unless otherwise specified in the applicable rule, the required sampling time for each test run shall be no less than one hour and no greater than four hours, and the sampling time at each sampling point shall be of equal intervals of at least two minutes.

(2)	Opacity Compliance Tests.  When either EPA Method 9 or DEP Method 9 is specified as the applicable opacity test method, the required minimum period of observation for a compliance test shall be sixty (60) minutes for emissions units which emit or have the potential to emit 100 tons per year or more of particulate matter, and thirty (30) minutes for emissions units which have potential emissions less than 100 tons per year of particulate matter and are not subject to a multiple-valued opacity standard.  The opacity test observation period shall include the period during which the highest opacity emissions can reasonably be expected to occur.  Exceptions to these requirements are as follows:

(a)	For batch, cyclical processes, or other operations which are normally completed within less than the minimum observation period and do not recur within that time, the period of observation shall be equal to the duration of the batch cycle or operation completion time.

(b)	The observation period for special opacity tests that are conducted to provide data to establish a surrogate standard pursuant to Rule 62-297.310(5)(k), F.A.C., Waiver of Compliance Test Requirements, shall be established as necessary to properly establish the relationship between a proposed surrogate standard and an existing mass emission limiting standard.

(c)	The minimum observation period for opacity tests conducted by employees or agents of the Department to verify the day-to-day continuing compliance of a unit or activity with an applicable opacity standard shall be twelve minutes.

b.	Minimum Sample Volume.  Unless otherwise specified in the applicable rule or test method, the minimum sample volume per run shall be 25 dry standard cubic feet.

c.	Required Flow Rate Range.  For EPA Method 5 particulate sampling, acid mist/sulfur dioxide, and fluoride sampling which uses Greenburg Smith type impingers, the sampling nozzle and sampling time shall be selected such that the average sampling rate will be between 0.5 and 1.0 actual cubic feet per minute, and the required minimum sampling volume will be obtained.

d.	Calibration of Sampling Equipment.  Calibration of the sampling train equipment shall be conducted in accordance with the schedule shown in Table 297.310-1, F.A.C.

| TABLE 297.310-1 CALIBRATION SCHEDULE |  |  |  |
| --- | --- | --- | --- |
| ITEM | MINIMUM CALIBRATION FREQUENCY | REFERENCE INSTRUMENT | TOLERANCE |
| Liquid in glass thermometer | Annually | ASTM Hg in glass ref. thermometer or equivalent or thermometric points | +/-2% |
| Bimetallic thermometer | Quarterly | Calib. liq. in glass | 5° F |
| Thermocouple | Annually | ASTM Hg in glass ref. thermometer, NBS calibrated reference and potentiometer | 5° F |
| Barometer | Monthly | Hg barometer or NOAA station | +/-1% scale |
| Pitot Tube | When required or when damaged | By construction or measurements in wind tunnel D greater than 16” and standard pitot tube | See EPA Method 2, Fig. 2-2 & 2-3 |
| Probe Nozzles | Before each test or when nicked, dented, or corroded | Micrometer | +/- 0.001” mean of at least three readings; Max. deviation between readings, 0.004” |
| Dry Gas Meter and Orifice Meter | 1. Full Scale: When received, when 5% change observed, annually | Spirometer or calibrated wet test or dry gas test meter | 2% |
|  | 2. One Point: Semiannually |  |  |
|  | 3. Check after each test series | Comparison check | 5% |

e.	Allowed Modification to EPA Method 5.  When EPA Method 5 is required, the following modification is allowed:  the heated filter may be separated from the impingers by a flexible tube.

[Rule 62-297.310(4), F.A.C.]

TR5.	Determination of Process Variables.

a.	Required Equipment.  The owner or operator of an emissions unit for which compliance tests are required shall install, operate, and maintain equipment or instruments necessary to determine process variables, such as process weight input or heat input, when such data are needed in conjunction with emissions data to determine the compliance of the emissions unit with applicable emission limiting standards.

b.	Accuracy of Equipment.  Equipment or instruments used to directly or indirectly determine process variables, including devices such as belt scales, weight hoppers, flow meters, and tank scales, shall be calibrated and adjusted to indicate the true value of the parameter being measured with sufficient accuracy to allow the applicable process variable to be determined within 10% of its true value.

[Rule 62-297.310(5), F.A.C.]

TR6.	Sampling Facilities.  Permittees that are required to sample mass emissions from point sources shall install stack sampling ports and provide sampling facilities that meet the requirements of this condition.  Sampling facilities include sampling ports, work platforms, access to work platforms, electrical power, and sampling equipment support.  All stack sampling facilities must also comply with all applicable Occupational Safety and Health Administration (OSHA) Safety and Health Standards described in 29 CFR Part 1910, Subparts D and E.

a.	Permanent Test Facilities.  The owner or operator of an emissions unit for which a compliance test, other than a visible emissions test, is required on at least an annual basis, shall install and maintain permanent stack sampling facilities.

b.	Temporary Test Facilities.  The owner or operator of an emissions unit that is not required to conduct a compliance test on at least an annual basis may use permanent or temporary stack sampling facilities.  If the owner chooses to use temporary sampling facilities on an emissions unit, and the Department elects to test the unit, such temporary facilities shall be installed on the emissions unit within 5 days of a request by the Department and remain on the emissions unit until the test is completed.

c.	Sampling Ports.

- All sampling ports shall have a minimum inside diameter of 3 inches.

- The ports shall be capable of being sealed when not in use.

- The sampling ports shall be located in the stack at least 2 stack diameters or equivalent diameters downstream and at least 0.5 stack diameter or equivalent diameter upstream from any fan, bend, constriction or other flow disturbance.

- For emissions units for which a complete application to construct has been filed prior to December 1, 1980, at least two sampling ports, 90 degrees apart, shall be installed at each sampling location on all circular stacks that have an outside diameter of 15 feet or less.  For stacks with a larger diameter, four sampling ports, each 90 degrees apart, shall be installed.  For emissions units for which a complete application to construct is filed on or after December 1, 1980, at least two sampling ports, 90 degrees apart, shall be installed at each sampling location on all circular stacks that have an outside diameter of 10 feet or less.  For stacks with larger diameters, four sampling ports, each 90 degrees apart, shall be installed.  On horizontal circular ducts, the ports shall be located so that the probe can enter the stack vertically, horizontally or at a 45 degree angle.

- On rectangular ducts, the cross sectional area shall be divided into the number of equal areas in accordance with EPA Method 1.  Sampling ports shall be provided which allow access to each sampling point. The ports shall be located so that the probe can be inserted perpendicular to the gas flow.

d.	Work Platforms.

- Minimum size of the working platform shall be 24 square feet in area. Platforms shall be at least 3 feet wide.

- On circular stacks with 2 sampling ports, the platform shall extend at least 110 degrees around the stack.

- On circular stacks with more than two sampling ports, the work platform shall extend 360 degrees around the stack.

- All platforms shall be equipped with an adequate safety rail (ropes are not acceptable), toe board, and hinged floor-opening cover if ladder access is used to reach the platform. The safety rail directly in line with the sampling ports shall be removable so that no obstruction exists in an area 14 inches below each sample port and 6 inches on either side of the sampling port.

e.	Access to Work Platform.

- Ladders to the work platform exceeding 15 feet in length shall have safety cages or fall arresters with a minimum of 3 compatible safety belts available for use by sampling personnel.

- Walkways over free-fall areas shall be equipped with safety rails and toe boards.

f.	Electrical Power.

- A minimum of two 120-volt AC, 20-amp outlets shall be provided at the sampling platform within 20 feet of each sampling port.

- If extension cords are used to provide the electrical power, they shall be kept on the plant’s property and be available immediately upon request by sampling personnel.

g.	Sampling Equipment Support.

- A three-quarter inch eyebolt and an angle bracket shall be attached directly above each port on vertical stacks and above each row of sampling ports on the sides of horizontal ducts.

- The bracket shall be a standard 3 inch × 3 inch × one-quarter inch equal-legs bracket which is 1 and one-half inches wide.  A hole that is one-half inch in diameter shall be drilled through the exact center of the horizontal portion of the bracket.  The horizontal portion of the bracket shall be located 14 inches above the centerline of the sampling port.

- A three-eighth inch bolt which protrudes 2 inches from the stack may be substituted for the required bracket.  The bolt shall be located 15 and one-half inches above the centerline of the sampling port.

- The three-quarter inch eyebolt shall be capable of supporting a 500 pound working load.  For stacks that are less than 12 feet in diameter, the eyebolt shall be located 48 inches above the horizontal portion of the angle bracket.  For stacks that are greater than or equal to 12 feet in diameter, the eyebolt shall be located 60 inches above the horizontal portion of the angle bracket.  If the eyebolt is more than 120 inches above the platform, a length of chain shall be attached to it to bring the free end of the chain to within safe reach from the platform.

- A complete monorail or dual rail arrangement may be substituted for the eyebolt and bracket.

- When the sample ports are located in the top of a horizontal duct, a frame shall be provided above the port to allow the sample probe to be secured during the test.

[Rule 62-297.310(6), F.A.C.]

TR7.	Frequency of Compliance Tests.  The following provisions apply only to those emissions units that are subject to an emissions limiting standard for which compliance testing is required.

a.	General Compliance Testing.

(1)	The owner or operator of a new or modified emissions unit that is subject to an emission limiting standard shall conduct a compliance test that demonstrates compliance with the applicable emission limiting standard prior to obtaining an operation permit for such emissions unit.

(2)	For excess emission limitations for particulate matter specified in Rule 62-210.700, F.A.C., a compliance test shall be conducted annually while the emissions unit is operating under soot blowing conditions in each federal fiscal year during which soot blowing is part of normal emissions unit operation, except that such test shall not be required in any federal fiscal year in which a fossil fuel steam generator does not burn liquid and/or solid fuel for more than 400 hours other than during startup.

(3)	The owner or operator of an emissions unit that is subject to any emission limiting standard shall conduct a compliance test that demonstrates compliance with the applicable emission limiting standard prior to obtaining a renewed operation permit.  Emissions units that are required to conduct an annual compliance test may submit the most recent annual compliance test to satisfy the requirements of this provision.  In renewing an air operation permit pursuant to sub-subparagraph 62-210.300(2)(a)3.b., c., or d., F.A.C., the Department shall not require submission of emission compliance test results for any emissions unit that, during the year prior to renewal:

(a)	Did not operate; or

(b)	In the case of a fuel burning emissions unit, burned liquid and/or solid fuel for a total of no more than 400 hours.

(4)	During each federal fiscal year (October 1 – September 30), unless otherwise specified by rule, order, or permit, the owner or operator of each emissions unit shall have a formal compliance test conducted for:

(a)	Visible emissions, if there is an applicable standard;

(b)	Each of the following pollutants, if there is an applicable standard, and if the emissions unit emits or has the potential to emit:  5 tons per year or more of lead or lead compounds measured as elemental lead; 30 tons per year or more of acrylonitrile; or 100 tons per year or more of any other regulated air pollutant; and

(c)	Each NESHAP pollutant, if there is an applicable emission standard.

(5)	An annual compliance test for particulate matter emissions shall not be required for any fuel burning emissions unit that, in a federal fiscal year, does not burn liquid and/or solid fuel, other than during startup, for a total of more than 400 hours.

(6)	For fossil fuel steam generators on a semi-annual particulate matter emission compliance testing schedule, a compliance test shall not be required for any six-month period in which liquid and/or solid fuel is not burned for more than 200 hours other than during startup.

(7)	For emissions units electing to conduct particulate matter emission compliance testing quarterly pursuant to paragraph 62-296.405(2)(a), F.A.C., a compliance test shall not be required for any quarter in which liquid and/or solid fuel is not burned for more than 100 hours other than during startup.

(8)	Any combustion turbine that does not operate for more than 400 hours per year shall conduct a visible emissions compliance test once per each five-year period, coinciding with the term of its air operation permit.

(9)	The owner or operator shall notify the Department, at least 15 days prior to the date on which each formal compliance test is to begin, of the date, time, and place of each such test, and the test contact person who will be responsible for coordinating and having such test conducted for the owner or operator.

(10)	An annual compliance test conducted for visible emissions shall not be required for units exempted from air permitting pursuant to subsection 62-210.300(3), F.A.C.; units determined to be insignificant pursuant to subparagraph 62-213.300(2)(a)1., A.C., or paragraph 62-213.430(6)(b), F.A.C.; or units permitted under the General Permit provisions in paragraph 62-210.300(4)(a) or Rule 62-213.300, F.A.C., unless the general permit specifically requires such testing.

b.	Special Compliance Tests.  When the Department, after investigation, has good reason (such as complaints, increased visible emissions or questionable maintenance of control equipment) to believe that any applicable emission standard contained Department rule or in a permit issued pursuant to those rules is being violated, it shall require the owner or operator of the emissions unit to conduct compliance tests which identify the nature and quantity of pollutant emissions from the emissions unit and to provide a report on the results of said tests to the Department.

c.	Waiver of Compliance Test Requirements.  If the owner or operator of an emissions unit that is subject to a compliance test requirement demonstrates to the Department, pursuant to the procedure established in Rule 62-297.620, F.A.C., that the compliance the emissions unit with an applicable weight emission limiting standard can be adequately determined by means other than the designated test procedure, such as specifying a surrogate standard of no visible emissions for particulate matter sources equipped with a bag house or specifying a fuel analysis for sulfur dioxide emissions, the Department shall waive the compliance test requirements for such emissions units and order that the alternate means of determining compliance be used, provided, however, the provisions of paragraph 62-297.310(7)(b), F.A.C., shall apply.

[Rule 62-297.310(7), F.A.C.]

TR8.	Test Reports.

a.	The owner or operator of an emissions unit for which a compliance test is required shall file a report with the Department on the results of each such test.

b.	The required test report shall be filed with the Department as soon as practical but no later than 45 days after the last sampling run of each test is completed.

c.	The test report shall provide sufficient detail on the emissions unit tested and the test procedures used to allow the Department to determine if the test was properly conducted and the test results properly computed.  As a minimum, the test report, other than for an EPA or DEP Method 9 test, shall provide the following information.

(1)	The type, location, and designation of the emissions unit tested.

(2)	The facility at which the emissions unit is located.

(3)	The owner or operator of the emissions unit.

(4)	The normal type and amount of fuels used and materials processed, and the types and amounts of  fuels used and material processed during each test run.

(5)	The means, raw data and computations used to determine the amount of fuels used and materials  processed, if necessary to determine compliance with an applicable emission limiting standard.

(6)	The type of air pollution control devices installed on the emissions unit, their general condition, their normal operating parameters (pressure drops, total operating current and GPM scrubber water), and their operating parameters during each test run.

(7)	A sketch of the duct within 8 stack diameters upstream and 2 stack diameters downstream of the sampling ports, including the distance to any upstream and downstream bends or other flow disturbances.

(8)	The date, starting time and duration of each sampling run.

(9)	The test procedures used, including any alternative procedures authorized pursuant to Rule 62-297.620, F.A.C.  Where optional procedures are authorized in this chapter, indicate which option was used.

(10)	The number of points sampled and configuration and location of the sampling plane.

(11)	For each sampling point for each run, the dry gas meter reading, velocity head, pressure drop across the stack, temperatures, average meter temperatures and sample time per point.

(12)	The type, manufacturer and configuration of the sampling equipment used.

(13)	Data related to the required calibration of the test equipment.

(14)	Data on the identification, processing and weights of all filters used.

(15)	Data on the types and amounts of any chemical solutions used.

(16)	Data on the amount of pollutant collected from each sampling probe, the filters, and the impingers, are reported separately for the compliance test.

(17)	The names of individuals who furnished the process variable data, conducted the test, analyzed the samples and prepared the report.

(18)	All measured and calculated data required to be determined by each applicable test procedure for each run.

(19)	The detailed calculations for one run that relate the collected data to the calculated emission rate.

(20)	The applicable emission standard and the resulting maximum allowable emission rate for the emissions unit plus the test result in the same form and unit of measure.

(21)	A certification that, to the knowledge of the owner or his authorized agent, all data submitted are true and correct.  When a compliance test is conducted for the Department or its agent, the person who conducts the test shall provide the certification with respect to the test procedures used.  The owner or his authorized agent shall certify that all data required and provided to the person conducting the test are true and correct to his knowledge.

[Rule 62-297.310(8), F.A.C.]

Back to Top

Operation

TV1.	General Prohibition.  A permitted installation may only be operated, maintained, constructed, expanded or modified in a manner that is consistent with the terms of the permit.  [Rule 62-4.030, Florida Administrative Code (F.A.C.)]

TV2.	Validity.  This permit is valid only for the specific processes and operations applied for and indicated in the approved drawings or exhibits.  Any unauthorized deviation from the approved drawings, exhibits, specifications, or conditions of this permit may constitute grounds for revocation and enforcement action by the Department.  [Rule 62-4.160(2), F.A.C.]

TV3.	Proper Operation and Maintenance.  The permittee shall properly operate and maintain the facility and systems of treatment and control (and related appurtenances) that are installed and used by the permittee to achieve compliance with the conditions of this permit, as required by Department rules.  This provision includes the operation of backup or auxiliary facilities or similar systems when necessary to achieve compliance with the conditions of the permit and when required by Department rules.  [Rule 62-4.160(6), F.A.C.]

TV4.	Not Federally Enforceable.  Health, Safety and Welfare.  To ensure protection of public health, safety, and welfare, any construction, modification, or operation of an installation which may be a source of pollution, shall be in accordance with sound professional engineering practices pursuant to Chapter 471, F.S.  [Rule 62-4.050(3), F.A.C.]

TV5.	Continued Operation.  An applicant making timely and complete application for permit, or for permit renewal, shall continue to operate the source under the authority and provisions of any existing valid permit or Florida Electrical Power Plant Siting Certification, and in accordance with applicable requirements of the Acid Rain Program and applicable requirements of the CAIR Program, until the conclusion of proceedings associated with its permit application or until the new permit becomes effective, whichever is later, provided the applicant complies with all the provisions of subparagraphs 62-213.420(1)(b)3., F.A.C.  [Rules 62-213.420(1)(b)2., F.A.C.]

TV6.	Changes Without Permit Revision.  Title V sources having a valid permit issued pursuant to Chapter 62-213, F.A.C., may make the following changes without permit revision, provided that sources shall maintain source logs or records to verify periods of operation:

a.	Permitted sources may change among those alternative methods of operation allowed by the source’s permit as provided by the terms of the permit;

b.	A permitted source may implement operating changes, as defined in Rule 62-210.200, F.A.C., after the source submits any forms required by any applicable requirement and provides the Department and EPA with at least 7 days written notice prior to implementation.  The source and the Department shall attach each notice to the relevant permit;

(1)	The written notice shall include the date on which the change will occur, and a description of the change within the permitted source, the pollutants emitted and any change in emissions, and any term or condition becoming applicable or no longer applicable as a result of the change;

(2)	The permit shield described in Rule 62-213.460, F.A.C., shall not apply to such changes;

c.	Permitted sources may implement changes involving modes of operation only in accordance with Rule 62-213.415, F.A.C.

[Rule 62-213.410, F.A.C.]

TV7.	Circumvention.  No person shall circumvent any air pollution control device, or allow the emission of air pollutants without the applicable air pollution control device operating properly.  [Rule 62-210.650, F.A.C.]

Compliance

TV8.	Compliance with Chapter 403, F.S., and Department Rules.  Except as provided at Rule 62-213.460, Permit Shield, F.A.C., the issuance of a permit does not relieve any person from complying with the requirements of Chapter 403, F.S., or Department rules.  [Rule 62-4.070(7), F.A.C.]

TV9.	Compliance with Federal, State and Local Rules.  Except as provided at Rule 62-213.460, F.A.C., issuance of a permit does not relieve the owner or operator of a facility or an emissions unit from complying with any applicable requirements, any emission limiting standards or other requirements of the air pollution rules of the Department or any other such requirements under federal, state, or local law.  [Rule 62-210.300, F.A.C.]

TV10.	Binding and Enforceable.  The terms, conditions, requirements, limitations and restrictions set forth in this permit, are "permit conditions" and are binding and enforceable pursuant to Sections 403.141, 403.727, or 403.859 through 403.861, F.S.  The permittee is placed on notice that the Department will review this permit periodically and may initiate enforcement action for any violation of these conditions.  [Rule 62-4.160(1), F.A.C.]

TV11.	Timely Information.  When requested by the Department, the permittee shall within a reasonable time furnish any information required by law which is needed to determine compliance with the permit.  If the permittee becomes aware the relevant facts were not submitted or were incorrect in the permit application or in any report to the Department, such facts or information shall be corrected promptly.  [Rule 62-4.160(15), F.A.C.]

TV12.	Halting Or Reduction Of Source Activity.  It shall not be a defense for a permittee in an enforcement action that maintaining compliance with any permit condition would necessitate halting of or reduction of the source activity.  [Rule 62-213.440(1)(d)3., F.A.C.]

TV13.	Final Permit Action.  Any Title V source shall comply with all the terms and conditions of the existing permit until the Department has taken final action on any permit renewal or any requested permit revision, except as provided at Rule 62-213.412(2), F.A.C.  [Rule 62-213.440(1)(d)4., F.A.C.]

TV14.	Sudden And Unforeseeable Events Beyond The Control Of The Source.  A situation arising from sudden and unforeseeable events beyond the control of the source which causes an exceedance of a technology-based emissions limitation because of unavoidable increases in emissions attributable to the situation and which requires immediate corrective action to restore normal operation, shall be an affirmative defense to an enforcement action in accordance with the provisions and requirements of 40 CFR 70.6(g)(2) and (3), hereby adopted and incorporated by reference.  [Rule 62-213.440(1)(d)5., F.A.C.]

TV15.	Permit Shield.  Except as provided in Chapter 62-213, F.A.C., compliance with the terms and conditions of a permit issued pursuant to Chapter 62-213, F.A.C., shall, as of the effective date of the permit, be deemed compliance with any applicable requirements in effect, provided that the source included such applicable requirements in the permit application.  Nothing in this condition or in any permit shall alter or affect the ability of EPA or the Department to deal with an emergency, the liability of an owner or operator of a source for any violation of applicable requirements prior to or at the time of permit issuance, or the requirements of the Federal Acid Rain Program or the CAIR Program.  [Rule 62-213.460, F.A.C.]

TV16.	Compliance With Federal Rules.  A facility or emissions unit subject to any standard or requirement of 40 CFR, Part 60, 61, 63 or 65, adopted and incorporated by reference at Rule 62-204.800, F.A.C., shall comply with such standard or requirement.  Nothing in this chapter shall relieve a facility or emissions unit from complying with such standard or requirement, provided, however, that where a facility or emissions unit is subject to a standard established in Rule 62-296, F.A.C., such standard shall also apply.  [Rule 62-296.100(3), F.A.C.]

Permit Procedures

TV17.	Permit Revision Procedures.  The permittee shall revise its permit as required by Rules 62-213.400, 62-213.412, 62-213.420, 62-213.430 & 62-4.080, F.A.C.; and, in addition, the Department shall revise permits as provided in Rule 62-4.080, F.A.C. & 40 CFR 70.7(f).

TV18.	Permit Renewal.  The permittee shall renew its permit as required by Rules 62-4.090, 62.213.420(1) and 62-213.430(3), F.A.C.  Permits being renewed are subject to the same requirements that apply to permit issuance at the time of application for renewal.  Permit renewal applications shall contain that information identified in Rules 62-210.900(1) [Application for Air Permit - Long Form], 62-213.420(3) [Required Information], 62-213.420(6) [CAIR Part Form], F.A.C.  Unless a Title V source submits a timely and complete application for permit renewal in accordance with the requirements this rule, the existing permit shall expire and the source's right to operate shall terminate.  For purposes of a permit renewal, a timely application is one that is submitted 225 days before the expiration of a permit that expires on or after June 1, 2009.  No Title V permit will be issued for a new term except through the renewal process.  [Rules 62-213.420 & 62-213.430, F.A.C.]

TV19.	Insignificant Emissions Units or Pollutant-Emitting Activities.  The permittee shall identify and evaluate insignificant emissions units and activities as set forth in Rule 62-213.430(6), F.A.C.

TV20.	Savings Clause.  If any portion of the final permit is invalidated, the remainder of the permit shall remain in effect.  [Rule 62-213.440(1)(d)1., F.A.C.]

TV21.	Suspension and Revocation.

a.	Permits shall be effective until suspended, revoked, surrendered, or expired and shall be subject to the provisions of Chapter 403, F.S., and rules of the Department.

b.	Failure to comply with pollution control laws and rules shall be grounds for suspension or revocation.

c.	A permit issued pursuant to Chapter 62-4, F.A.C., shall not become a vested property right in the permittee.  The Department may revoke any permit issued by it if it finds that the permit holder or his agent:

(1)	Submitted false or inaccurate information in his application or operational reports.

(2)	Has violated law, Department orders, rules or permit conditions.

(3)	Has failed to submit operational reports or other information required by Department rules.

(4)	Has refused lawful inspection under Section 403.091, F.S.

d.	No revocation shall become effective except after notice is served by personal services, certified mail, or newspaper notice pursuant to Section 120.60(5), F.S., upon the person or persons named therein and a hearing held if requested within the time specified in the notice.  The notice shall specify the provision of the law, or rule alleged to be violated, or the permit condition or Department order alleged to be violated, and the facts alleged to constitute a violation thereof.

[Rule 62-4.100, F.A.C.]

TV22.	Not federally enforceable.  Financial Responsibility.  The Department may require an applicant to submit proof of financial responsibility and may require the applicant to post an appropriate bond to guarantee compliance with the law and Department rules.  [Rule 62-4.110, F.A.C.]

TV23.	Emissions Unit Reclassification.

a.	Any emissions unit whose operation permit has been revoked as provided for in Chapter 62-4, F.A.C., shall be deemed permanently shut down for purposes of Rule 62-212.500, F.A.C.  Any emissions unit whose permit to operate has expired without timely renewal or transfer may be deemed permanently shut down, provided, however, that no such emissions unit shall be deemed permanently shut down if, within 20 days after receipt of written notice from the Department, the emissions unit owner or operator demonstrates that the permit expiration resulted from inadvertent failure to comply with the requirements of Rule 62-4.090, F.A.C., and that the owner or operator intends to continue the emissions unit in operation, and either submits an application for an air operation permit or complies with permit transfer requirements, if applicable.

b.	If the owner or operator of an emissions unit which is so permanently shut down, applies to the Department for a permit to reactivate or operate such emissions unit, the emissions unit will be reviewed and permitted as a new emissions unit.

[Rule 62-210.300(6), F.A.C.]

TV24.	Transfer of Permits.  Per Rule 62-4.160(11), F.A.C., this permit is transferable only upon Department approval in accordance with Rule 62-4.120, F.A.C., as applicable.  The permittee shall be liable for any non-compliance of the permitted activity until the transfer is approved by the Department.  The permittee transferring the permit shall remain liable for corrective actions that may be required as a result of any violations occurring prior to the sale or legal transfer of the facility.  The permittee shall also comply with the requirements of Rule 62-210.300(7), F.A.C., and use DEP Form No. 62-210.900(7).  [Rules 62-4.160(11), 62-4.120, and 62-210.300(7), F.A.C.]

Rights, Title, Liability, and Agreements

TV25.	Rights.  As provided in Subsections 403.987(6) and 403.722(5), F.S., the issuance of this permit does not convey any vested rights or any exclusive privileges.  Neither does it authorize any injury to public or private property or any invasion of personal rights, nor any infringement of federal, state, or local laws or regulations.  This permit is not a waiver of or approval of any other Department permit that may be required for other aspects of the total project which are not addressed in this permit.  [Rule 62-4.160(3),  F.A.C.]

TV26.	Title.  This permit conveys no title to land or water, does not constitute State recognition or acknowledgment of title, and does not constitute authority for the use of submerged lands unless herein provided and the necessary title or leasehold interests have been obtained from the State.  Only the Trustees of the Internal Improvement Trust Fund may express State opinion as to title.  [Rule 62-4.160(4),  (F.A.C.]

TV27.	Liability.  This permit does not relieve the permittee from liability for harm or injury to human health or welfare, animal, or plant life, or property caused by the construction or operation of this permitted source, or from penalties therefore; nor does it allow the permittee to cause pollution in contravention of F.S. and Department rules, unless specifically authorized by an order from the Department.  [Rule 62-4.160(5), F.A.C.]

TV28.	Agreements.

a.	The permittee, by accepting this permit, specifically agrees to allow authorized Department personnel, upon presentation of credentials or other documents as may be required by law and at reasonable times, access to the premises where the permitted activity is located or conducted to:

(1)	Have access to and copy any records that must be kept under conditions of the permit;

(2)	Inspect the facility, equipment, practices, or operations regulated or required under this permit; and,

(3)	Sample or monitor any substances or parameters at any location reasonably necessary to assure compliance with this permit or Department rules.  Reasonable time may depend on the nature of the concern being investigated.

b.	In accepting this permit, the permittee understands and agrees that all records, notes, monitoring data and other information relating to the construction or operation of this permitted source which are submitted to the Department may be used by the Department as evidence in any enforcement case involving the permitted source arising under the Florida Statutes or Department rules, except where such use is prescribed by Sections 403.111 and 403.73, F.S.  Such evidence shall only be used to the extent it is consistent with the Florida Rules of Civil Procedure and appropriate evidentiary rules.

c.	The permittee agrees to comply with changes in Department rules and Florida Statutes after a reasonable time for compliance; provided, however, the permittee does not waive any other rights granted by Florida Statutes or Department rules.

[Rules 62-4.160(7), (9), and (10), F.A.C.]

Recordkeeping and Emissions Computation

TV29.	Permit.  The permittee shall keep this permit or a copy thereof at the work site of the permitted activity.  [Rule 62-4.160(12), F.A.C.]

TV30.	Recordkeeping.

a.	Upon request, the permittee shall furnish all records and plans required under Department rules.  During enforcement actions, the retention period for all records will be extended automatically unless otherwise stipulated by the Department.

b.	The permittee shall hold at the facility or other location designated by this permit records of all monitoring information (including all calibration and maintenance records and all original strip chart recordings for continuous monitoring instrumentation) required by the permit, copies of all reports required by this permit, and records of all data used to complete the application for this permit.  These materials shall be retained at least five (5) years from the date of the sample, measurement, report, or application unless otherwise specified by Department rule.

c.	Records of monitoring information shall include:

(1)	The date, exact place, and time of sampling or measurements, and the operating conditions at the time of sampling or measurement;

(2)	The person responsible for performing the sampling or measurements;

(3)	The dates analyses were performed;

(4)	The person and company that performed the analyses;

(5)	The analytical techniques or methods used;

(6)	The results of such analyses.

[Rules 62-4.160(14) and 62-213.440(1)(b)2., F.A.C.]

TV31.	Emissions Computation.  Pursuant to Rule 62-210.370, F.A.C., the following required methodologies are to be used by the owner or operator of a facility for computing actual emissions, baseline actual emissions, and net emissions increase, as defined at Rule 62-210.200, F.A.C., and for computing emissions for purposes of the reporting requirements of subsection 62-210.370(3) and paragraph 62-212.300(1)(e), F.A.C., or of any permit condition that requires emissions be computed in accordance with Rule 62-210.370, F.A.C.  Rule 62-210.370, F.A.C., is not intended to establish methodologies for determining compliance with the emission limitations of any air permit.

For any of the purposes specified above, the owner or operator of a facility shall compute emissions in accordance with the requirements set forth in this subsection.

a.	Basic Approach.  The owner or operator shall employ, on a pollutant-specific basis, the most accurate of the approaches set forth below to compute the emissions of a pollutant from an emissions unit; provided, however, that nothing in this rule shall be construed to require installation and operation of any continuous emissions monitoring system (CEMS), continuous parameter monitoring system (CPMS), or predictive emissions monitoring system (PEMS) not otherwise required by rule or permit, nor shall anything in this rule be construed to require performance of any stack testing not otherwise required by rule or permit.

(1)	If the emissions unit is equipped with a CEMS meeting the requirements of paragraph 62-210.370(2)(b), F.A.C., the owner or operator shall use such CEMS to compute the emissions of the pollutant, unless the owner or operator demonstrates to the department that an alternative approach is more accurate because the CEMS represents still-emerging technology.

(2)	If a CEMS is not available or does not meet the requirements of paragraph 62-210.370(2)(b), F.A.C, but emissions of the pollutant can be computed pursuant to the mass balance methodology of paragraph 62-210.370(2)(c), F.A.C., the owner or operator shall use such methodology, unless the owner or operator demonstrates to the department that an alternative approach is more accurate.

(3)	If a CEMS is not available or does not meet the requirements of paragraph 62-210.370(2)(b), F.A.C., and emissions cannot be computed pursuant to the mass balance methodology, the owner or operator shall use an emission factor meeting the requirements of paragraph 62-210.370(2)(d), F.A.C., unless the owner or operator demonstrates to the department that an alternative approach is more accurate.

b.	Continuous Emissions Monitoring System (CEMS).

(1)	An owner or operator may use a CEMS to compute emissions of a pollutant for purposes of this rule provided:

(a)	The CEMS complies with the applicable certification and quality assurance requirements of 40 CFR Part 60, Appendices B and F, or, for an acid rain unit, the certification and quality assurance requirements of 40 CFR Part 75, all adopted by reference at Rule 62-204.800, F.A.C.; or,

(b)	The owner or operator demonstrates that the CEMS otherwise represents the most accurate means of computing emissions for purposes of this rule.

(2)	Stack gas volumetric flow rates used with the CEMS to compute emissions shall be obtained by the most accurate of the following methods as demonstrated by the owner or operator:

(a)	A calibrated flowmeter that records data on a continuous basis, if available; or

(b)	The average flow rate of all valid stack tests conducted during a five-year period encompassing the period over which the emissions are being computed, provided all stack tests used shall represent the same operational and physical configuration of the unit.

(3)	The owner or operator may use CEMS data in combination with an appropriate f-factor, heat input data, and any other necessary parameters to compute emissions if such method is demonstrated by the owner or operator to be more accurate than using a stack gas volumetric flow rate as set forth at subparagraph 62-210.370(2)(b)2., F.A.C., above.

c.	Mass Balance Calculations.

(1)	An owner or operator may use mass balance calculations to compute emissions of a pollutant for purposes of this rule provided the owner or operator:

(a)	Demonstrates a means of validating the content of the pollutant that is contained in or created by all materials or fuels used in or at the emissions unit; and,

(b)	Assumes that the emissions unit emits all of the pollutant that is contained in or created by any material or fuel 	used in or at the emissions unit if it cannot otherwise be accounted for in the process or in the capture and destruction of the pollutant by the unit’s air pollution control equipment.

(2)	Where the vendor of a raw material or fuel which is used in or at the emissions unit publishes a range of pollutant content from such material or fuel, the owner or operator shall use the highest value of the range to compute the emissions, unless the owner or operator demonstrates using site-specific data that another content within the range is more accurate.

(3)	In the case of an emissions unit using coatings or solvents, the owner or operator shall document, through purchase receipts, records and sales receipts, the beginning and ending VOC inventories, the amount of VOC purchased during the computational period, and the amount of VOC disposed of in the liquid phase during such period.

d.	Emission Factors.

(1)	An owner or operator may use an emission factor to compute emissions of a pollutant for purposes of this rule provided the emission factor is based on site-specific data such as stack test data, where available, unless the owner or operator demonstrates to the department that an alternative emission factor is more accurate.  An owner or operator using site-specific data to derive an emission factor, or set of factors, shall meet the following requirements.

(a)	If stack test data are used, the emission factor shall be based on the average emissions per unit of input, output, or gas volume, whichever is appropriate, of all valid stack tests conducted during at least a five-year period encompassing the period over which the emissions are being computed, provided all stack tests used shall represent the same operational and physical configuration of the unit.

(b)	Multiple emission factors shall be used as necessary to account for variations in emission rate associated with variations in the emissions unit’s operating rate or operating conditions during the period over which emissions are computed.

(c)	The owner or operator shall compute emissions by multiplying the appropriate emission factor by the appropriate input, output or gas volume value for the period over which the emissions are computed.  The owner or operator shall not compute emissions by converting an emission factor to pounds per hour and then multiplying by hours of operation, unless the owner or operator demonstrates that such computation is the most accurate method available.

(2)	If site-specific data are not available to derive an emission factor, the owner or operator may use a published emission factor directly applicable to the process for which emissions are computed.  If no directly-applicable emission factor is available, the owner or operator may use a factor based on a similar, but different, process.

e.	Accounting for Emissions During Periods of Missing Data from CEMS, PEMS, or CPMS.  In computing the emissions of a pollutant, the owner or operator shall account for the emissions during periods of missing data from CEMS, PEMS, or CPMS using other site-specific data to generate a reasonable estimate of such emissions.

f.	Accounting for Emissions During Periods of Startup and Shutdown.  In computing the emissions of a pollutant, the owner or operator shall account for the emissions during periods of startup and shutdown of the emissions unit.

g.	Fugitive Emissions.  In computing the emissions of a pollutant from a facility or emissions unit, the owner or operator shall account for the fugitive emissions of the pollutant, to the extent quantifiable, associated with such facility or emissions unit.

h.	Recordkeeping.  The owner or operator shall retain a copy of all records used to compute emissions pursuant to this rule for a period of five years from the date on which such emissions information is submitted to the department for any regulatory purpose.

[Rule 62-210.370(1) & (2), F.A.C.]

Responsible Official

TV32.	Designation and Update.  The permittee shall designate and update a responsible official as required by Rule 62-213.202, F.A.C.

Prohibitions and Restrictions

TV33.	Asbestos.  This permit does not authorize any demolition or renovation of the facility or its parts or components which involves asbestos removal.  This permit does not constitute a waiver of any of the requirements of Chapter 62-257, F.A.C., and 40 CFR 61, Subpart M, National Emission Standard for Asbestos, adopted and incorporated by reference in Rule 62-204.800, F.A.C.  Compliance with Chapter 62-257, F.A.C., and 40 CFR 61, Subpart M, Section 61.145, is required for any asbestos demolition or renovation at the source.  [40 CFR 61; Rule 62-204.800, F.A.C.; and, Chapter 62-257, F.A.C.]

TV34.	Refrigerant Requirements.  Any facility having refrigeration equipment, including air conditioning equipment, which uses a Class I or II substance (listed at 40 CFR 82, Subpart A, Appendices A and B), and any facility which maintains, services, or repairs motor vehicles using a Class I or Class II substance as refrigerant must comply with all requirements of 40 CFR 82, Subparts B and F, and with Chapter 62-281, F.A.C.

TV35.	Open Burning Prohibited.  Open burning is prohibited unless performed in accordance with the provisions of Rule 62-296.320(3) or Chapter 62-256, F.A.

Back to Top

Unregulated Emissions Units and/or Activities.  An emissions unit which emits no “emissions-limited pollutant” and which is subject to no unit-specific work practice standard, though it may be subject to regulations applied on a facility-wide basis (e.g., unconfined emissions, odor, general opacity) or to regulations that require only that it be able to prove exemption from unit-specific emissions or work practice standards.

The below listed emissions units and/or activities are neither ‘regulated emissions units’ nor ‘insignificant emissions units’.

A.  	External Combustion Hot Water Generators operated by WDW Resort Complex staff, and fired by Natural Gas.  These units are used to heat water.

| EU No. | ID Code | Description | Location |
| --- | --- | --- | --- |
| 035 | GFR2 thru 18 | 16 Hot Water Heaters | Disney’s Grand Floridian Hotel |
| 053 | STB-1, 2A, 2B1, 2B2, 3 thru 8 | 10 Hot Water Heaters | Disney’s Hollywood Studios |
| 072 | LAU-1 & 2 | 2 Laundry Thermal Oil Heaters | Administrative Area Laundry |
| 083 | BB-1 thru 5 | 5 Hot Water Heaters | Blizzard Beach |
| 090 | BDW-1 & 2 | 2 Boilers (hot water generators) | Boardwalk Resort |
| 091 | BDW-3 thru 10 | 8 Hot Water Heaters | Boardwalk Resort |
| 092 | MK-3 | Hot Water Heater | Magic Kingdom |
| 095 | COS-1 thru 37 | 37 Hot Water Heaters | Coronado Springs Resort |
| 103 | DAKU-1 thru 51 | 51 Hot Water Heaters | Disney’s Animal Kingdom |
| 113 | ASR-2 thru 108 | 107 Hot Water Heaters | All Star Resort |
| 115 | DAKU-52 | 1.075 MMBtu/hr boiler firing Natural Gas | Tree of Life Boiler |

B.	External Combustion Hot Water Generators operated by Reedy Creek Energy Services staff, and fired by Natural Gas.  These units are used to heat water.

| EU No. | ID Code | Description | Location |
| --- | --- | --- | --- |
| 076 | Epcot HWG-1, 2 & 3 | 3 Hot Water Heaters | Epcot |
| 081 | CEP-2 | Hot Water Heater | Reedy Creek Energy Services |

C.	Emergency Engines.  EU 125 consists of the emergency engines, listed below, which are exempt RICE based on the exemption provisions in 40 CFR 63.6590(b) for emergency engines over 500 hp at a Major HAP source.  “Existing” stationary emergency (as defined in 40 CFR 63.6675) compression ignition reciprocating internal combustion engine (CI RICE) exempted from having to meet the requirements of either 40 CFR 63, Subpart ZZZZ – National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines or 40 CFR 63, Subpart A – General Provisions, including initial notification, pursuant to 40 CFR 63.6590(b)(3)(iii) and are not subject to regulations under 40 CFR 60, Subpart IIII - New Source Performance for Stationary Internal Combustion Engines (ICE) based on the manufacturer date (before 07/11/05).

{Permitting Note:  In order to retain the Unregulated Emissions Unit status, these engines must be operated in accordance with the definition of an Emergency Stationary RICE found in 40 CFR 63.6675.}

| ID Code | Owner* | Generator Description | Location |
| --- | --- | --- | --- |
| EX002 | RCES | DIESEL, 375 kW | To be relocated |
| EX003 | RCES | DIESEL, 500 kW | Lift Station 07 |
| EX004 | RCES | DIESEL, 500 kW | Lift Station 55 |
| EX005 | RCES | DIESEL, 500 kW | Pump Station B |
| EX006 | RCES | DIESEL, 500 kW | Pump Station C |
| EX007 | RCES | DIESEL, 900 kW | Pump Station D |
| EX008 | RCES | DIESEL, 400 kW | Well 16 |
| EX009 | RCES | DIESEL, 400 kW | Well 17 |
| EX010 | RCES | DIESEL, 350 kW | Well 2 |
| EX011 | RCES | Detroit Diesel, 500 kW | WWTP #1 Gen |
| EX012 | RCES | Detroit Diesel, 600 kW | WWTP #2 Gen |
| EX013 | RCES | Detroit Diesel, 400 kW | WWTP #3 Gen |
| EX014 | WDW | Caterpillar, 500 kW | Board Walk #2 Convention Center Chiller |
| EX015 | WDW | Caterpillar, 500 kW | Board Walk #3 Beach Club Villas |
| EX016 | WDW | Caterpillar, 600 kW | Board Walk #5 Yacht & Beach Club |
| EX017 | WDW | Caterpillar, 375 kW | Contemporary #1 Loading Dock |
| EX018 | WDW | Kohler, 500 kW | Coronado Springs #1 Main Bldg |
| EX019 | WDW | Caterpillar, 350 kW | DAK #34 Everest |
| EX020 | WDW | Kohler, 750 kW | DAK Lodge Loading Dock |
| EX021 | WDW | Caterpillar SR4, 350 kW | DHS #04 Great Movie Ride |
| EX022 | WDW | Caterpillar 3508 B, 1000 kW | DHS #18 Feature Animation |
| EX023 | WDW | Caterpillar SR-4, 335 kW | Downtown Disney Cirque Du Soleil |
| EX024 | WDW | Caterpillar SR-4, 400 kW | Downtown Disney Quest |
| EX025 | WDW | Cummins Power, 900 kW | Grand Floridian Loading Dock |
| EX026 | WDW | Kohler, 500 kW | MK #08 Tunnel Entrance |
| EX027 | WDW | Kohler, 350 kW | Pop Century Classic Hall |
| EX028 | WDW | North Cummins, 750 kW | Team Disney North |
| EX029 | WDW | North Cummins, 750 kW | Team Disney South |
| EX030 | WDW | Caterpillar, 800 kW | Wilderness Lodge |
| EX031 | WDW | Kohler, 500 kW | Wilderness Lodge Annex (Villas) |

* RCES = Reedy Creek Energy Services.    WDW = Walt Disney World Resort Complex.

D.	Paint Spray Booths.  EU 126 consists of 33 Paint Spray Booths (PSB) operated by WDW Resort Complex staff, listed below by location.   Also included in EU126 are architectural coating operations (painting outdoors and indoors) that occur throughout the facility but are not listed below:

| ID Code | Description | Location |
| --- | --- | --- |
| NSA-18 | NSA Boat Maintenance & Painting Facility PSB | Central Shops NSA |
| NSA-1 thru 7, 11, 12, 14 thru 16 | NSA Central Shops Building 12 PSBs | Central Shops NSA |
| NSA-8 | NSA Lofting Building Paint Spray Booth (PSB) | Central Shops NSA |
| NSA-9 & 10 | NSA Central Shops Building Annex 2 PSBs | Central Shops NSA |
| MGM-10 | PSB | Disney’s Hollywood Studios |
| BVC-1 | PSB | Buena Vista Construction |
| LBV-1 & 2 | 2 PSBs | Facilities Services |
| VM-3 | PSB | Downtown Disney Service Building |
| LBV-3 | PSB | Facilities Services |
| YBC-3 | PSB | Yacht & Beach Club |
| EP-1 & 2 | 2 PSBs | EPCOT |
| EP-3 | PSB | EPCOT |
| MK-1 | PSB | Magic Kingdom |
| MK-2 | PSB | Magic Kingdom |
| BR-1 | PSB | Boardwalk Resort |
| COS-41 | PSB | Coronado Springs Resort |
| ASR-1 | PSB | All Star Resort |
| NSA-20 | Monorail Trains PSB | NSA Monorail Building |
| DAKU-53 | Maintenance PSB | Disney’s Animal Kingdom |

Back to Top

The following attachments are included for convenient reference:

Figure 1, Summary Report-Gaseous and Opacity Excess Emission and

Monitoring System Performance (40 CFR 60, July, 1996).

Table H, Permit History.

Table 1, Summary of Air Pollutant Standards and Terms.

Table 2, Summary of Compliance Requirements.

Back to Top

[Note: This form is referenced in 40 CFR 60.7, Subpart A-General Provisions]

Pollutant (Circle One):	SO2	NOX	TRS	H2S	CO	Opacity

Reporting period dates:   From ________________________    to ____________________________

Company:   _____________________________________________________________________________________

Emission Limitation:   ____________________________________________________________________________

Address:   ______________________________________________________________________________________

Monitor Manufacturer:   ___________________________________________________________________________

Model No.:   ___________________________________________________________________________

Date of Latest CMS Certification or Audit:   _____________________________

Process Unit(s) Description:   _______________________________________________________________________

Total source operating time in reporting period 1:   ____________________________

| Emission data summary 1 | CMS performance summary 1 |
| --- | --- |
| 1. Duration of excess emissions in reporting period due to: | 1. CMS downtime in reporting period due to: |
| a. Startup/shutdown ...........................…............. ____ | a. Monitor equipment malfunctions ..................... ____ |
| b. Control equipment problems .......…............... ____ | b. Non-Monitor equipment malfunctions ............. ____ |
| c. Process problems ........................................... ____ | c. Quality assurance calibration ........................... ____ |
| d. Other known causes ....................................... ____ | d. Other known causes ......................................... ____ |
| e. Unknown causes ........................…................ ____ | e. Unknown causes ............................................... ____ |
| 2. Total duration of excess emissions .................. ____ | 2. Total CMS Downtime ......................................... ____ |
| 3. Total duration of excess emissions x (100) / [Total source operating time] .......................................... ____ %2 | 3. [Total CMS Downtime] x (100) / [Total source operating time] ............................................……………......... ____ %2 |

1	For opacity, record all times in minutes. For gases, record all times in hours.

2	For the reporting period: If the total duration of excess emissions is 1 percent or greater of the total operating time or the total CMS downtime is 5 percent or greater of the total operating time, both the summary report form and the excess emission report described in 40 CFR 60.7(c) shall be submitted.

Note:  On a separate page, describe any changes since the last in CMS, process or controls.

I certify that the information contained in this report is true, accurate, and complete.

Name:  _________________________________________________________

Signature:  _________________________________________________________ Date:  ___________________

Title:  _________________________________________________________

Back to Top

| E.U. ID No. | # Description | Permit No. | Effective Date | Expiration Date | Project Type |
| --- | --- | --- | --- | --- | --- |
| All | Facility | 0950111-005-AV | 01/01/1998 | 12/31/2002 | Initial Title V |
| 088/CEP-1 | CCCT and HRSG | 0950111-016-AC | 05/25/1999 | 12/31/2002 | Construction (mod.) |
|  |  | 0950111-017-AV | 05/25/1999 | 12/31/2002 | Revision |
| 112/DAK-1 | Necropsy Bldg.: Animal Crematory | 0950111-013-AC | 03/18/1998 | 12/31/1999 | Construction (new) |
|  |  | 0950111-017-AV | 05/25/1999 | 12/31/2002 | Revision |
| 115/DAKU-52 | Tree of Life Boiler | 0950111-016-AC | 05/25/1999 | 12/31/2002 | Construction (new) |
| All | Facility | 0950111-021-AV | 01/01/2003 | 12/31/20073 | Renewal |
| 120 | Three Diesel Electric Generators Serving the DISC Building | 0950111-022-AC | 06/16/2004 | 12/31/2004 | Construction (new) |
| 120 | Three Diesel Electric Generators Serving the DISC Building | 0950111-023-AC | 12/01/2004 | 2/28/2005 | Construction (mod.) |
| All | Facility | 0950111-024-AV | 2/2/2005 | 12/31/2007 | Revision |
| 088/CEP-1 | CCCT and HRSG | 0950111-025-AC | 6/13/2005 | 11/1/2006 | Construction (new) |
| 088/CEP-1 | CCCT and HRSG | 0950111-026-AC | 8/16/2006 | 11/1/2006 | Construction (mod.) |
| 088/CEP-1 | CCCT and HRSG | 0950111-027-AV1 | 2/1/2007 | 12/31/07 | Revision |
| 121 | Dry cleaner replacement NSA drycleaner --replaced M. Atlas 45 dry cleaning machine EU-001 | 0950111-028-AC | 7/03007 | 12/31/2008 | Construction |
| All | Facility | 0950111-029-AV | 1/01/20082 | 12/31/2012 | Renewal |
| 081 (CEP-2) | Replacement of 60 MMBtu/hr water heater, placed in insignificant list | 0950111-030-AV |  |  | Withdrawn (b/c EPA vacated Boiler MACT) |
| 088 (CEP-1) | Power Plant CAIR Part added | 0950111-031-AV | 1/27/2009 | 12/31/2012 | Revision |
| All | Facility | 0950111-032-AV | 10/26/2012 | 12/31/2016 | Renewal |
| 079 and 080 | EPCOT Engines/Generators | 0950111-033-AC | 1/1/13 | n/a | Revision |
| 079 and 080 | EPCOT Engines/Generators | 0950111-034-AC | MM/DD/2014 | MM/DD/YY | Minor AC Revision |
| Engines | Engine regulatory revisions/corrections | 0950111-035-AV | Day 55 | 12/31/16 | Minor AV Revisions |

Back to Top

Back to Top

Back to Top