Georgia-Pacific Consumer Operations LLC

Palatka Mill

Facility ID No.: 1070005

Putnam County

#### Title V Air Operation Permit Revision

#### Permit No. 1070005-076-AV

#### Revision of Title V Air Operation Permit No. 1070005-068-AV

# Permitting Authority:

State of Florida

Department of Environmental Protection

Air Resource Management, Northeast District Air Program

Northeast District Air Program

8800 Baymeadows Way West, Suite 100

Jacksonville, Florida 32256

Telephone: 904/256-1700

Fax: 904/256-1590

Title V Air Operation Permit Revision

Permit No. 1070005-076-AV

Table of Contents

Section	Page Number

I.	Facility Information.

A.	Facility Description. 	 2

B.	Summary of Emissions Units. 	 2

C.	Applicable Regulations. 	 3

II.	Facility-wide Conditions. 	 4

III.	Emissions Units and Conditions.

A.	Emissions Unit 014- No. 4 Power Boiler (removed) 	7

B.	Emissions Unit 015 – No. 5 Power Boiler. 	8

C.	Emissions Unit 016 – No. 4 Combination Boiler. 	13

D.	Emissions Unit 017 – No. 4 Lime Kiln. 	19

E.	Emissions Unit 018 – No. 4 Recovery Boiler.... .....................................................................................27

F.	Emissions Unit 019 – No. 4 Smelt Dissolving Tanks (2)..... ..................................................................39

G.	Emissions Unit 031 – Tall Oil Plant........................................................................................................42

H.	Emissions Unit 032 (removed) – NCG/TRS Incinerator.........................................................................44

I.	Emissions Unit 034 (removed) – No. 6  Boiler........................................................................................45

J.	Emissions Unit 035 – ClO2 Plant and Methanol Storage Tank................................................................46

K.	Emissions Unit 036 – SCF No. 3 Bleach Plant........................................................................................47

L.	Emissions Unit 037 – Thermal Oxidizer..................................................................................................54

M.	Emissions Unit 039 – New Bark Hog & Existing Bark/Wood Handling System....................................64

N.	Emissions Unit 044.-.No. 7 Package Boiler.............................................................................................66

O.	Emissions Unit 045 -. Wide-web Flexographic Printers..........................................................................71

P.	Emissions Unit 046 - Condensate Stripper System....……………………...........……………......…….72

Q.	Emissions Unit 047- Brown Stock Washer Lines 3, 5, 6 & 7..................................................................81

R. 	Emissions Unit 048 - New Two-Stage Oxygen Delignification System..................................................82

S.	Emissions Unit 050 -Converting Department.….......……………............................................................	83

T.	Emissions Unit 051 Emergency Engines..............…………….....………………………………….......87

U.	Common Conditions – Subpart RR.........................................................................................................104

V.	Common Conditions – Subpart MM.........………………………….....…………………………….....109

W.	Common Conditions – Used Oil..........………………………………….....………………………......118

X.	Common Conditions – Excess Emissions.........…………………………….....………………….........119

Y.	Common Conditions F.A.C.Test Requirements......................................................................................121

Z.	Common Conditions Kraft (Sulfate) Pulp Mills........………………………………......…………........129

AA Common Conditions................................................................................................................................139

BB.	Common Conditions- Subpart S..............................................................................................................141

CC	Common Conditions (EUs 015, 016 & 044)- Subpart DDDDD.............................................................148

IV.	Appendices........................... .........................................................................................................................180

Appendix A, Glossary.

Appendix ASP, ASP Number 97-B-01 (With Scrivener’s Order Dated July 9, 1997).

Appendix CAM, Compliance Assurance Monitoring Plan.

Appendix I, List of Insignificant Emissions Units and/or Activities.

Appendix NESHAP, Subpart A – General Provisions.

Appendix NESHAP, Subpart S.

Appendix NESHAP, Subpart KK.

Appendix NESHAP, Subpart MM.

Appendix NESHAP, Subpart RR.

Appendix NESHAP, Subpart JJJJ.

Appendix NESHAP, Subpart ZZZZ.

Appendix NESHAP, Subpart DDDDD.

Appendix NESHAP, Subpart S.

Appendix NSPS, Subpart A – General Provisions.

Appendix NSPS, Subpart B – Performance Specification.

Appendix NSPS, Subpart Db.

Appendix NSPS, Subpart BB.

Appendix NSPS, Subpart IIII.

Appendix NSPS, Subpart JJJJ.

Appendix RR, Facility-wide Reporting Requirements.

Appendix TR, Facility-wide Testing Requirements.

Appendix TV, Title V General Conditions.

Appendix U, List of Unregulated Emissions Units and/or Activities.

Referenced Attachments. 	 At End

Figure 1, Summary Report-Gaseous and Opacity Excess Emission and

Monitoring System Performance (40 CFR 60, July, 1996).

Table H, Permit History.

Table 1, Summary of Air Pollutant Standards and Terms.

Table 2, Compliance Requirements.

Permittee:	Permit No. 1070005-076-AV

Georgia-Pacific Consumer Operations LLC   	Palatka Mill

215 County Road 216	Facility ID No. 1070005

Palatka, Florida  32178-0919	Title V Air Operation Permit Revision

The purpose of this permit is to revise Title V air operation permit No. 1070005-068-AV to incorporate the terms and conditions of permit Nos. 1070005-072-AC and 1070005-079-AC for the above referenced facility.  The existing Palatka Mill is located in Putnam County at 215 CR 216, Palatka, Florida  32177.  UTM Coordinates are:  Zone 17, 434.0- km East and 3283.4 km North; Latitude:  2940’00” North and Longitude:  8140’45” West.

The Title V air operation permit is issued under the provisions of Chapter 403, Florida Statutes (F.S.), and Florida Administrative Code (F.A.C.) Chapters 62-4, 62-210, 62-213.  The above named permittee is hereby authorized to operate the facility in accordance with the terms and conditions of this permit.

Revision Effective Date: xx/xx/xxxx

Effective Date:  July 9, 2012

Renewal Application Due Date:  Exp. November 26, 2016

Expiration Date: Eff. July 9, 2017

(Draft/Proposed)

Khalid AlNahdy, P.E., MBA

Program Administrator

Waste & Air Resource Management

KAA: jw

Subsection A.  Facility Description:

This facility is a Kraft pulp and paper mill that consists of major activities areas such as: chip handling, pulping, bleaching, chemical recovery, utilities, paper machines, converting, turpentine and tall oil production.

Subsection B.  Summary of Emissions Units:

| EU No. | ## Brief Description |
| --- | --- |
| Regulated Emissions Units |  |
| -014 | No. 4 Power Boiler (removed) |
| -015 | No. 5 Power Boiler |
| -016 | No. 4 Combination Boiler |
| -017 | No. 4 Lime Kiln |
| -018 | No. 4 Recovery Boiler |
| -019 | No. 4 Smelt Dissolving Tanks (2) |
| -031 | Tall Oil Plant |
| -032 | Noncondensible Gas System/TRS Incinerator (removed) |
| -034 | No. 6 Boiler (removed) |
| -035 | ClO2 Plant and Methanol Storage Tank |
| -036 | Elemental Chlorine Free (ECF) No. 3 Bleach Plant |
| -037 | Thermal Oxidizer |
| -039 | New Bark Hog & Existing Bark/Wood Chip Handling System |
| -044 | No. 7 Package Boiler |
| -045 | Wide-web Flexographic Printers |
| -046 | Condensate Stripper System |
| -047 | Brown Stock Washer Lines 3, 5, 6 & 7 |
| -048 | New Two-Stage Oxygen Delignification System |
| -050 | Converting Department |
| -051 | Emergency Engines |
| Unregulated Emissions Units and Activities |  |
| See Appendix U-1, attached |  |

Subsection C.  Applicable Regulations:

Based on the Title V air operation permit renewal application received May 13, 2011, this facility is a major source of hazardous air pollutants (HAP).   Because this facility operates stationary reciprocating internal combustion engines, it is subject to regulation under 40 CFR 63, Subpart ZZZZ, - National Emissions Standards For Hazardous Air Pollutants For Stationary Reciprocating Internal Combustion Engines.  The existing facility is a PSD major source of air pollutants in accordance with Rule 62-212.400, F.A.C.  A summary of applicable regulations is shown in the following table.

| Regulation | ## EU No (s). |
| --- | --- |
| 40 CFR 60, Subpart A, NSPS General Provisions | 037, 044, 046 |
| 40 CFR 60, Subpart Db | 044 |
| 40 CFR 60, Subpart BB | 037, 046 |
| 40 CFR 60, Subpart IIII | 051 |
| 40 CFR 60, Subpart JJJJ | 051 |
| 40 CFR 63, Subpart A, NESHAP General Provisions | 015, 016, 017, 036 |
| 40 CFR 63, Subpart S | 015, 016, 017, 036, 037, 043, 046, 047, 048 |
| 40 CFR 63, Subpart KK | 045 |
| 40 CFR 63, Subpart MM | 017, 018, 019 |
| 40 CFR 63, Subpart RR. | 037, 046 |
| 40 CFR 63, Subpart JJJJ | 050 |
| State Rule Citations 62-296.404, 62- 296.406, 62-296.410, 62-296.320, BACT, Rule 62-212.400) | 015, 016, 017, 018, 019, 031, 037, 039, 044, 046 |
| 40 CFR 63, Subpart ZZZZ | 051 |
| 40 CFR 63, Subpart DDDDD. | 015, 016, 044 |

The following conditions apply facility-wide to all emission units and activities:

- Appendices.  The permittee shall comply with all documents identified in Section IV, Appendices, listed in the Table of Contents.  Each document is an enforceable part of this permit unless otherwise indicated.  [Rule 62-213.440, F.A.C.]

Emissions and Controls

- Not federally Enforceable.  Objectionable Odor Prohibited.  No person shall cause, suffer, allow or permit the discharge of air pollutants, which cause or contribute to an objectionable odor.  An “objectionable odor” means any odor present in the outdoor atmosphere which by itself or in combination with other odors, is or may be harmful or injurious to human health or welfare, which unreasonably interferes with the comfortable use and enjoyment of life or property, or which creates a nuisance.  [Rule 62-296.320(2) and 62-210.200(Definitions), F.A.C.]

- Not federally Enforceable.  General Volatile Organic Compounds (VOC) Emissions or Organic Solvents (OS) Emissions.  The permittee shall allow no person to store, pump, handle, process, load, unload or use in any process or installation, volatile organic compounds or organic solvents without applying known and existing vapor emission control devices or systems deemed necessary and ordered by the Department.  [Rule 62-296.320(1), F.A.C.]

{Permitting Note: Nothing is deemed necessary and ordered at this time.}

- General Visible Emissions.  No person shall cause, let, permit, suffer or allow to be discharged into the atmosphere the emissions of air pollutants from any activity equal to or greater than 20% opacity.  EPA Method 9 is the method of compliance pursuant to Chapter 62-297, F.A.C.  This regulation does not impose a specific testing requirement.  [Rule 62-296.320(4)(b)1, F.A.C.]

- Not federally Enforceable.  Unconfined Particulate Matter.  No person shall cause, let, permit, suffer or allow the emissions of unconfined particulate matter from any activity, including vehicular movement; transportation of materials; construction; alteration; demolition or wrecking; or industrially related activities such as loading, unloading, storing or handling; without taking reasonable precautions to prevent such emissions.  Reasonable precautions to prevent emissions of unconfined particulate matter at this facility include:

(a)	Conveyors that are covered or enclosed where feasible and practical.

(b)	Paved roads entering and exiting the plant.

(c)	Limiting vehicle speeds.

(d)   Good housekeeping practices.

[Rule 62-296.320(4)(c), F.A.C.]

Annual Reports and Fees

See Appendix RR, Facility-wide Reporting Requirements for additional details.

- Annual Operating Report.  The permittee shall submit an annual report that summarizes the actual operating rates and emissions from this facility.  Annual operating reports shall be submitted to the Compliance Authority by April 1st of each year.  [Rule 62-210.370(3), F.A.C.]

- Annual Emissions Fee Form and Fee.  The annual Title V emissions fees are due (postmarked) by March 1st of each year.  The completed form and calculated fee shall be submitted to:  Major Air Pollution Source Annual Emissions Fee, P.O. Box 3070, Tallahassee, Florida  32315-3070.  The forms are available for download by accessing the Title V Annual Emissions Fee On-line Information Center at the following Internet web site:  http://www.dep.state.fl.us/air/emission/tvfee.htm.

[Rule 62-213.205, F.A.C.]

- Annual Statement of Compliance.  The permittee shall submit an annual statement of compliance to the compliance authority at the address shown on the cover of this permit within 60 days after the end of each calendar year during which the Title V permit was effective.  [Rules 62-213.440(3)(a)2. & 3. and (3)(b), F.A.C.]

- Prevention of Accidental Releases (Section 112(r) of CAA).

(a)	As required by Section 112(r)(7)(B)(iii) of the CAA and 40 CFR 68, the owner or operator shall submit an updated Risk Management Plan (RMP) to the Chemical Emergency Preparedness and Prevention Office (CEPPO) RMP Reporting Center.

(b)	As required under Section 252.941(1)(c), F.S., the owner or operator shall report to the appropriate representative of the Department of Community Affairs (DCA), as established by department rule, within one working day of discovery of an accidental release of a regulated substance from the stationary source, if the owner or operator is required to report the release to the United States Environmental Protection Agency under Section 112(r)(6) of the CAA.

(c)	The owner or operator shall submit the required annual registration fee to the DCA on or before April 1, in accordance with Part IV, Chapter 252, F.S., and Rule 9G-21, F.A.C.

(d)	Any required written reports, notifications, certifications, and data required to be sent to the DCA, should be sent to:  Department of Community Affairs, Division of Emergency Management, 2555 Shumard Oak Boulevard, Tallahassee, FL  32399-2100, Telephone: (850) 413-9921, Fax: (850) 488-1739.

(e)	Any Risk Management Plans, original submittals, revisions, or updates to submittals, should be sent to:  RMP Reporting Center, Post Office Box 10162, Fairfax, VA  22038, Telephone:  (703) 227-7650.

(f)	Any required reports to be sent to the National Response Center, should be sent to:  National Response Center, EPA Office of Solid Waste and Emergency Response, USEPA (5305 W), 401 M Street SW, Washington, D.C.  20460, Telephone: (800) 424-8802.

(g)	Send the required annual registration fee using approved forms made payable to: Cashier, Department of Community Affairs, State Emergency Response Commission, 2555 Shumard Oak Boulevard, Tallahassee, FL  32399-2149

[Part IV, Chapter 252, F.S.; and, Rule 9G-21, F.A.C.]

FW10.  Unregulated Emissions Units and/or Activities.  Appendix U-1, List of Unregulated Emissions Units and/or Activities, is a part of this permit.

[Rule 62-213.440(1), F.A.C.]

FW11.  Insignificant Emissions Units and/or Activities.  Appendix I-1, List of Insignificant Emissions Units and/or Activities, is a part of this permit.

[Rules 62-213.440(1), 62-213.430(6) and 62-4.040(1)(b), F.A.C.]

FW12.  Georgia Pacific will take measures to ensure that all property boundaries are properly fenced or have other physical barriers (equivalent to a fence), and/or are properly posted and routinely patrolled.

[Rules 62-4.070(3) and 62-212.400(5), F.A.C., Construction Permit No. 1070005-017-AC]

FW13.  When appropriate, any recording, monitoring, or reporting requirements that are time-specific shall be in accordance with the effective date of the permit, which defines day one.  For purposes of this permit, an official year is defined as from January 1 through December 31, except for stack testing purposes, in which case an official year is defined as the federal fiscal year (October 1 – September 30).  An official day is defined as the time period from 6 A.M. to 6 A.M.

[Rule 62-213.440, F.A.C.; Applicant Request]

FW14.  Startup, Shutdown, Malfunction Plan.   The Permittee shall adopt and implement a written startup, shutdown, and malfunction (SSM) plan that describes, in detail, procedures for operating and maintaining the source during periods of startup, shutdown, and malfunction.  The plan shall meet the requirements of 40 CFR 63.6(e)(3) including containing a program of corrective action for malfunctioning processes and the air pollution control and monitoring equipment used to comply with the relevant standards of 40 CFR Part 63.  The current SSM Plan shall be maintained at the facility and be available for inspection and copying by the Administrator upon request. If the SSM Plan is subsequently revised pursuant to 40 CFR 63.6(e)(3)(viii), the Permittee shall maintain at the facility each previous (i.e., superseded) version of the SSM Plan, and shall make each such previous version available for inspection and copying by the Administrator for a period of 5 years after revision of the plan.  Any revisions made to the startup, shutdown, and malfunction plan in accordance with the procedures established by 40 CFR 63.6(e), shall not be deemed to constitute a Part 70 or 71 permit revision. Moreover, none of the procedures specified by the startup, shutdown, and malfunction plan for an affected source shall be deemed to fall within the permit shield.

FW15.  The DEP has determined that the applicable requirements in the attached Appendix SC (Specific Conditions) Applicability List, based on applicant submittal, were identified in the permit application.

[Rule 62-213.460, F.A.C. (Permit Shield)]

FW16.  The applicable requirements identified in the attached Appendix AR (Applicable Rules) Applicability List, based on applicant submittal, and listed in the application are included in the permit in a correct manner to the best knowledge of the DEP.

[Rule 62-213.460, F.A.C. (Permit Shield)]

FW17. The non-applicable requirements identified in the attached Appendix NAR (Non-applicable Rules) Non-Applicability List based on applicant submittal, and listed in the application were specifically determined to be not applicable to this facility for the reason noted for each requirement.

[Rule 62-213.460, F.A.C. (Permit Shield)]

FW18.  Fuel Sulfur Content.  The sulfur content of the No. 6 fuel oil used by the facility for all of the fuel sources shall not exceed 2.35% by weight, based on a 3-barge rolling average.  A record of analysis of each fuel oil shipment received shall be maintained and an annual report submitted.  In order to demonstrate compliance with this conditions, and Conditions D.2. and E.3., the Permittee shall calculate and maintain a log of the rolling 3-barge average sulfur content (i.e., the average of three consecutive barge deliveries, based on the certified fuel oil analysis receipt).  Fuel oil analysis shall be conducted using ASTM Methods D-129, D-1552, D-2622, D-4294, or equivalent methods approved by the Department.  The Annual Report is due by April 1st for the previous year.

[Rule 62-213.410, F.A.C.; Construction Permit No. 1070005-017-AC; PCP Exclusion dated March 14, 2002; Georgia-Pacific Letter dated April 1, 2003, Air Construction Permit No. 1070005-032-AC]

FW19.  Semi-Annual Monitoring Reports.  The permittee shall submit reports of any required monitoring at least every six (6) months.  The reports shall be submitted within 60 (sixty) days after the end of each semi-annual reporting period, i.e., by March 1 and September 1 of each year.  At the Permittee’s option, these reports may be submitted on a calendar quarter basis.

In order to provide better customer service and enhance the permitting experience in the Draft/Proposed permit only the emission unit(s) (EU) which are changed in the revision are listed in Section III. EMISSIONS UNITS AND SPECIFIC CONDITIONS. {Permitting Note: Strikethroughs indicate items deleted and red font double underlined indicates items added.}

Subsection E.  This section addresses the following emissions unit(s).

| EU No. | Brief Description |
| --- | --- |
| 018 | #4 Recovery Boiler with an electrostatic precipitator to control particulate matter emissions is a low odor design (non-direct contact evaporator) recovery boiler. Total Reduced Sulfur emissions are reduced by low odor design. |

As part of the recovery process at the mill, this unit fires black liquor solids (BLS) to recover the cooking liquor. The total maximum operational rate of this emissions unit is 210,000 lbs Black Liquor Solids/hr based on a 24-hour average (equivalent to 5.04x106 lb/day BLS and equivalent to 1345 MMBtu/hour based on the permitted capacity and an average heating value of 6410 Btu/lb of BLS).  Residual fuel oil is fired as a startup, shutdown and supplemental fuel.

This boiler also fires a continuous addition of virgin, ultra low sulfur diesel fuel (No. 2 fuel oil) into the piping that feeds black liquor into the No. 4 Recovery Boiler. The virgin ultra low sulfur diesel (ULSD) will have a maximum sulfur content of 15 parts per million (0.0015 percent by weight) as defined in 40 CFR 80.150(b), and be normally injected into the black liquor at a rate between 0.1% to 0.2% (by volume), but not to exceed 1% (by volume) or 280 gallons per hour (24-hour average).

The maximum steam production rate is 789,000 lb/hour (24-hour average) for steam conditions of 850° F to 900° F at 1250 psi.  Particulate matter emissions are controlled by an electrostatic precipitator (ESP) with automatic voltage control, 2-chambers, and 6 electric fields per chamber.  Total reduced sulfur (TRS) emissions are controlled by the low-odor boiler design.  Emissions of nitrogen oxides (NOX) are controlled by a four-level overfire air system.  Emissions of carbon monoxide (CO) and volatile organic compounds (VOC) are controlled by the combustion design and good operating practices.

The following pollutants are monitored with continuous emissions monitoring systems (CEMS):  CO, NOX, SO2, and TRS. and opacity.  Visible Emissions are monitored with a continuous opacity monitoring system (COMS). At permitted BLS capacity, the exhaust gas flow rate is 294,000 dscfm at 8% oxygen with an exit temperature of 400° F.  Exhaust gases exit a stack that is 12 feet in diameter and 230 feet tall.

This emissions unit is regulated under Rule 62-296.404, F.A.C. – Kraft Pulp Mills, Rule 212.400(5), F.A.C., Prevention of Significant Deterioration (PSD): Permit(s) No(s). PSD-FL-171, PSD-FL-226; Rule 62-212.400(6), F.A.C., Best Available Control Technology (BACT) Determination, dated June 7, 1991 and September 18, 1995 and 40 CFR 63, Subpart MM- National Emission Standards for Hazardous Air Pollutants for Chemical Recovery Combustion Sources at Kraft, Soda, Sulfite, and Stand-Alone Semichemical Pulp Mills.

The following specific conditions apply to the emissions unit(s) listed above:

#### OPERATIONAL PARAMETERS

E.1.	 Permitted Capacity:  The operation rate shall not exceed 210,000 lb (BLS)/hr where BLS is Black Liquor Solids as a 24-hr average.

{Permitting Note: The following conditions related to SO2 emissions and oil firing requirements replace all other similar conditions in previously issued air construction permits and or Title V permits.}

E.2.	Permitted Oil Firing Capacity:  The following table specifies the capabilities of the oil firing system designed by Combustion Engineering:

| Burner Type | Quantity | Oil Pressure | Maximum Design Capacities |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Oil Firing Rate (gph) |  | Heat Input Rates (MMBtu/hour)* |  |
|  |  |  | Each Burner | Total | Each Burner | Total |
| Startup Burners | 4 | 88 psig | 250375 | 10001500 | 37.556.25 | 150225 |
| Load Burners | 8 | 80 psig | 480925 | 38407400 | 72138.75 | 5761110 |

* For No. 6 fuel oil, assumes a heating value of 150,000 Btu/gallon and a density of 8.2 lb/gallon.

Any changes to the design or operation of the oil firing system shall require a modification of this permit and a corresponding PSD applicability determination.

[Design and Rule 62-210.200(PTE), F.A.C.; and Construction Permit No. 1070005-050-AC, and Applicant's Request in Application No. 1070005-076-AV/079-AC]Reserved

# E.3.(a).	 Authorized Fuels:  The No. 4 Recovery Boiler is authorized to fire the listed fuels as specified below:

- Black Liquor Solids (Black Liquor at approximately 66% BLS content and 11.37 lb/gallon density);

Ultra Low Sulfur Diesel with a maximum sulfur content not to exceed 15 ppm (0.0015 percent by weight) prior to injection into the black liquor feed line, i.e. a USLD/BLS blend;

- No. 6 Fuel Oil with a maximum sulfur content not to exceed 2.35% by weight (with or without any prior blending with on-specification used oil as stated in paragraph f. E.3.(b)(iii) below).  This fuel shall be fired as a startup, shutdown, and supplemental fuel (e.g. maintain the flame stability of the boiler);

- Subject to the requirements of Appendix G of Construction Permit No. 1070005-038-AC, limited amounts of on-specification used oil may be blended and fired with the No. 6 fuel oil.

[Rules 62-4.070(3), 62-4.160, 62-210.200(Definitions - PTE), Construction Permit No. 1070005-038-AC; Construction Permit No. 1070005-050-AC; FINAL Title V Permit No. 1070005-054-AV and Construction Permit No. 1070005-059-AC, and Applicant's Request in Application No. 1070005-076-AV/079-AC]

Excess Emissions due to startup and shutdown are conditionally allowed for up to 8 hours in any 24-hour period unless specifically authorized by the Department for longer duration.

{Permitting Note:  The Excess Emissions Rule at Rule 62-210.700, F.A.C., cannot vary any requirement of a NSPS or NESHAP provision.}

[Rule 62-213.410, F.A.C.; Rule 62-210.700, F.A.C.; Construction Permit No. 1070005-017-AC; PCP Exclusion dated March 14, 2002]

E.3.(b)	 Permitted Capacity & Fuel Restrictions:

  - Black Liquor Solids:  The maximum operating capacity is 210,000 lb/hour of BLS based on a 24-hour average, which is equivalent to a heat input rate of 1345 MMBtu per hour based on a fuel heating value of 6,410 Btu/lb of BLS.   This is also equivalent to approximately 27,984 gallons per hour of black liquor.

- Permitted Oil Firing CapacityOil Burner Capacity:  The following table specifies the physical design capabilities capacities of the oil firing system designed by Combustion Engineering:

| Burner Type | Quantity | Oil Pressure | Maximum Design Capacities |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Oil Firing Rate (gph) |  | Heat Input Rates (MMBtu/hour)* |  |
|  |  |  | Each Burner | Total | Each Burner | Total |
| Startup Burners | 4 | 88 psig | 250375 | 10001500 | 37.556.25 | 150225 |
| Load Burners | 8 | 80 psig | 480925 | 38407400 | 72138.75 | 5761110 |

* For No. 6 fuel oil, assumes a heating value of 150,000 Btu/gallon and a density of 8.2 lb/gallon.

Any changes to the design or operation of the oil firing system shall require a modification of this permit and a corresponding PSD applicability determination.

- No. 6 Fuel Oil:  The maximum firing rate shall not exceed 67,680 gallons of No. 6 fuel oil (including that blended with on-spec used oil) during any consecutive rolling 24 hours.1

- Virgin ULSD.  The maximum total addition rate of virgin ULSD into the black liquor feed line is 1%, by volume of the maximum BLS firing rate, i.e. no more than 280 gallons per hour [based on a 24-hour average].

- The maximum permitted firing rate of the ULSD/Black Liquor Solids Blend shall not exceed 203,637 lbs/hr [201,593 lb BLS/hour + 2044 lb ULSD/hour].  This is equivalent to a flow rate of no more than 27,427 gallons per hour of black liquor and USLD blended [26,864 gal BL/hr + 280 gal ULSD/hr]2,3

- The maximum consumption of ULSD shall not exceed 2,452,800 gallons during any consecutive 12-month period.

- (iv)On-spec Used Oil.  The on-specification used oil shall be blended with residual oil (No. 6 Fuel Oil), and shall not exceed 10% of the oil consumed.

- (v)All Fuel Oil.  The maximum consumption of all fuel oil (No. 6 residual oil, and on-specification used oil, and virgin ULSD) shall not exceed 7,860,640 gallons during any consecutive 12-month period4.

- (vi)Annual Heat Input.  The heat input rate to the No. 4 Recovery Boiler from firing oil shall be less than 1,178,220 MMBtu during any consecutive 12 months42.

1  	This is equivalent to a 24-hour average of 47 gpm, which was the basis of the air quality analysis for ensuring compliance with the Ambient Air Quality Standards as stated in Construction Permit No. 1070005-050-AC.  The oil firing system consists of 4 burners each rated at 250375 gph for startup, and 8 load burners each rated at 480925 gph. See oil burner design capacity in E.3.(b)(ii) above.

2 	Assumes a heating value of 140,161 Btu/gallon and a density of 7.3 lb/gallon for ULSD.

3  	A reduction of 4 gallons of black liquor for each gallon of ULSD actually fired in the boiler.

42	As stated in Construction Permit Nos. 1070005-038-AC and 1070005-050-AC, the oil firing restriction and maximum annual heat input rate maintains an annual capacity factor of less than 10% for fossil fuel firing at the emissions unit.

[Rules 62-4.070(3), 62-4.160, Design and Rule 62-210.200(Definitions - PTE); 62-212.400(12)(c), F.A.C., Construction Permit No. 1070005-038-AC; Construction Permit No. 1070005-050-AC; FINAL Title V Permit No. 1070005-054-AV, and Construction Permit No. 1070005-059-AC, and Applicant's Request in Application No. 1070005-076-AV/079-AC]

E.4.	  Hours of Operation:  The hours of operation are not limited.

[Rules 62-4.160(2) and 62-210.200(PTE), F.A.C.]

EMISSION LIMITATIONS AND STANDARDS

{Permitting note:  Table 1-1, Summary of Air Pollutant Standards and Terms, summarizes information for convenience purposes only.  This table does not supersede any of the terms or conditions of this permit.}

{Permitting Note:  Unless otherwise specified, the averaging time for this condition is based on the specified averaging time of the applicable test method.}

E.5. 	 PM Standard:  As determined by EPA Method 5 or 29, PM emissions shall not exceed 0.030 grains per dscf @ 8% O2 and 75.6 lb/hour based on the average of three test runs.

[Rule 62-212.400(BACT), F.A.C., and Construction Permit No. 1070005-038-AC]

E.6.	  TRS Standard:  As determined by data collected from the existing CEMS, TRS emissions shall not exceed 34.2 tons per year based on a 12-month rolling CEMS total.

[Rule 62-212.400(12), F.A.C.; and Construction Permit No. 1070005-038-AC]

E.7.	 Visible Emissions: Once the ESP in placed in service during startup of the recovery boiler, visible emissions shall not exceed 20% opacity based on a 6-minute average as determined by the existing COMS and EPA Method 9.

[Rule 62-212.400 (BACT), F.A.C.; and Construction Permit No. 1070005-038-AC]

E.8.	  SO2 Emissions Standards:  As determined by CEMS, SO2 emissions from the No. 4 Recovery Boiler shall not exceed 100 ppmvd at 8% O2 based on a 24-hour rolling average.  This emissions standard includes all valid SO2 CEMS data collected except during periods of boiler startup and shutdown.

{Permitting Note:  The limit of 100 ppmvd corrected to 8% oxygen is equivalent to 292.8 lb/hour.  This limit is based on the PSD modeling analysis for PSD-FL-380 and PSD-FL-393.}

[Rules 62-4.070(3), 62-210.200(PTE) and 62-212.400(12), F.A.C.; and Construction Permit No. 1070005-050-AC]

E.9. 	 SO2 Emissions Cap:  As determined by all valid CEMS data, SO2 emissions from the No. 4 Recovery Boiler shall not exceed 153.9 tons during any consecutive 12 months.  This emissions cap includes valid SO2 CEMS data collected including all periods of startup, shutdown, malfunction and oil firing.

{Permitting Note: The purpose of this emissions cap is to avoid PSD preconstruction review for PSD-FL-380 and PSD-FL-393.}

[Rules 62-4.070(3), 62-210.200(PTE) and 62-212.400(12), F.A.C.; and Construction Permit No. 1070005-050-AC]

E.10.	  CO Emissions:  CO emissions shall not exceed 400.0 ppmvd @ 8% O2 and 512.7 lb/hour based on a 30-day rolling CEMS average, excluding periods of startup and shutdown.

[Rule 62-212.400 (BACT), F.A.C. ; Permit No. 1070005-038-AC]

E.11.	 VOC (Volatile Organic Compounds) Emissions: VOC (Volatile Organic Compounds) Emissions shall not exceed 0.20 lb/ton of BLS and 21.0 lb/hour (THC determined as methane) based on the average of three test runs.

[Rule 62-212.400 (BACT), F.A.C.; Permit No. 1070005-038-AC]

Emissions based on the average of three (3) test runs conducted in accordance with EPA Method 25A to measure the total hydrocarbon concentration, EPA Methods 1 through 4 to measure the volumetric flow rate, and EPA Method 3A or 3B to measure the oxygen concentration to correct the VOC concentration.

[BACT; Permit #AC54-266676; PSD-FL-226]

E.12.	 Sulfuric Acid Mist (SAM) Emissions: Sulfuric Acid Mist (SAM) Emissions shall not exceed 0.81 ppmvd; 3.6 lb/hr and 15.9 TPY, based on the average of three (3) test runs conducted in accordance with EPA Method 8, incorporated and adopted by reference in Chapter 62-297, F.A.C.) or NCASI Method 106 (8A).

[BACT; Permit #AC54-266676; PSD-FL-226]

E.13.	 Beryllium Emissions: Beryllium Emissions shall not exceed 0.5 lb/E+12 Btu; 6.4E-4 lb/hr and 2.8E-3 TPY, based on the average of three (3) test runs conducted in accordance with EPA Method 104.

[BACT; Permit #AC54-266676; PSD-FL-226]

E.14.	  NOX Emissions:  As determined by data collected from the required CEMS, NOX emissions shall not exceed 80.0 ppmvd @ 8% O2 and 168.5 lb/hour based on a 30-day rolling CEMS average, excluding periods of startup and shutdown.

[Rule 62-212.400 (BACT), F.A.C.]

E.15.	 FUEL VENDOR DELIVERY

Virgin ULSD:  For each delivery of ULSD, the permittee shall retain at least the following records:

- ULSD vendor certification;

- The analysis identifying the sulfur content of the oil;

- Statement that the ULSD is virgin fuel;

- Quantity of oil supplied.

[Rule 62-4.070, F.A.C.]

TEST METHODS AND PROCEDURES

{Permitting note:  Table 2-1, Summary of Compliance Requirements, summarizes information for convenience purposes only.  This table does not supersede any of the terms or conditions of this permit.}

E.16.E.15.	 VOC (Volatile Organic Compounds): VOC (Volatile Organic Compounds) Emissions testing shall comply with Rule 62-297.401(25)(a), F.A.C. (EPA Method 25A to measure the total hydrocarbon concentration, EPA Methods 1 through 4 to measure the volumetric flow rate, and EPA Method 3A or 3B to measure the oxygen concentration to correct the VOC concentration, incorporated and adopted by reference in Chapter 62-297, F.A.C.).  These tests shall be performed prior to renewal of operation permit or when the Department requests a special test pursuant to Rule 62-297.310(7)(b), F.A.C.

[Permit #AC54-266676; PSD-FL-226, 3/11/93 Alternate Procedures and Requirements Order, and Construction Permit No. 1070005-038-AC]

E.17.E.16.	 SAM (Sulfuric Acid Mist):  SAM (Sulfuric Acid Mist) Emissions testing shall comply with Rule 62-297.401(8), F.A.C. (EPA Method 8, incorporated and adopted by reference in Chapter 62-297, F.A.C.) or NCASI Method 106 (8A) and be performed once each federal fiscal year.

[Permit #AC54-266676; PSD-FL-226, Applicant Request dated March 23, 2004]

E.18.E.17.	 Beryllium Emissions:  Beryllium Emissions testing shall comply with Rule 62-297.401(35), F.A.C. (EPA Method 104, incorporated and adopted by reference in Chapter 62-297, F.A.C.) and be performed every 5 years

[Permit #AC54-266676; PSD-FL-226]

E.19.E.18.	 Compliance Tests:  In accordance with the following requirements, the permittee shall have stack tests conducted to demonstrate compliance with the emissions standards specified in this permit for PM and VOC.

- During each federal fiscal year (October 1st to September 30th), compliance tests shall be conducted to determine PM emissions.  Because VOC emissions are expected to be low and the CO CEMS will ensure efficient combustion, subsequent VOC tests shall be conducted prior to renewal of the operation permit or when the Department requests a special test pursuant to Rule 62-297.310(7)(b), F.A.C.

- Test Fuel:  Compliance tests shall be conducted when firing BLS at permitted capacity.  [Rules 62-4.070(3), 62-212.400 (BACT) and 62-297.310, F.A.C.]

Operational Data for Tests:  For each test run, the permittee shall monitor and record the following information:  fuel feed rate; the secondary power input to the ESP; the flue gas oxygen content (%); CO, NOX, SO2 and TRS CEMS data; and opacity COMS data.  [Rules 62-297.310 and 62-4.070(3), F.A.C.]

#### CONTINUOUS MONITORING REQUIREMENTS

E.20.E.19.	 Total Reduced Sulfur (TRS): Total Reduced Sulfur (TRS) continuous emissions monitoring shall comply with the applicable requirements in Rule 62-296.404(5)(b)1.a., F.A.C. and compliance with the 12-month rolling average for TRS shall be based on the CEM data.

[PSD-FL-226]

E.21.E.20.	  Fuel Monitoring:  The permittee shall continuously monitor and record the flow/firing rate of each authorized fuel stated in Specific Condition No. E.3. (a) & (b) for the No. 4 Recovery Boiler including the fuel firing and heat input rate restrictions.

This may consist of fuel flow meters with integrators to monitor each flow rate.

[Rules 62-4.070(3); 62-212.400 (PSD), F.A.C.; Construction Permit No. 1070005-038-AC and Construction Permit No. 1070005-059-AC]

E.22.E.21.	 CEMS:  To demonstrate compliance with the emissions standards for the No. 4 Recovery Boiler, the permittee shall calibrate, operate and maintain continuous emissions monitoring systems (CEMS) to measure and record CO,TRS, SO2 and NOX emissions in the terms of the applicable standard.  The systems shall include continuous monitors to determine the flue gas oxygen content and exhaust flow rate.  Each CEMS shall have been installed such that representative measurements of emissions or process parameters from the facility are obtained.

As an alternative to a continuous flow monitor, the permittee has developed a site specific F-factor for BLS.

[Rules 62-4.070(3) and 62-212.400 (PSD), F.A.C.; and Construction Permit No. 1070005-038-AC]

E.23.E.22. 	Compliance by CEMS:  Compliance with the opacity and TRS standards shall be demonstrated with data collected from the existing COMS and CEMS.  Compliance with the CO and NOX standards shall be demonstrated with data collected from the CEMS required by Construction Permit No. 1070005-038-AC.  The permittee shall comply with Specific Conditions E.31E.30. of this permit.

[Rules 62-4.070(3) and 62-212.400 (BACT), F.A.C.; and Construction Permit No. 1070005-038-AC]

E.24.E.23.	SO2 CEMS:  The permittee shall calibrate, operate and maintain a CEMS to measure and record SO2 emissions to demonstrate compliance with the standards specified in this permit.  The CEMS shall include the measurement of oxygen (or carbon monoxide) for correction of SO2 emission concentrations to 8% oxygen.  The CEMS shall comply with the applicable requirements of Performance Specification 2 in Appendix B of 40 CFR Part 60 and the quality assurance procedures in Appendix F of 40 CFR Part 60.  The permittee shall comply with Specific Conditions E.31E.30. of this permit.

[Rule 62-4.070(3), F.A.C.; and Construction Permit No. 1070005-050-AC]

E.25.E.24.	 SO2 CEMS Data Substitution:  The following procedures shall be used for missing data.

- SO2 24-hour Rolling Average.  No data shall be substituted for the missing data to determine compliance with the standard based on 24-hour rolling average.  The next valid 1-hour emissions average shall be used to complete the 24-hour rolling average.

- SO2 Emissions Cap.  All valid CEMS data shall be used to determine compliance with the SO2 emissions cap.  This includes periods of startup, shutdown, malfunction, oil firing and operation while firing BLS.  For periods of missing data, the permittee shall calculate the maximum 24-hour rolling average for each method of operation (e.g., startup, shutdown, malfunction, oil firing and operation while firing BLS).  For the 12-month period, this average shall be substituted for each missing 1-hour emissions average under the given method of operation.

[Rule 62-4.070(3), F.A.C.; and Construction Permit No. 1070005-050-AC]

E.26.E.25.	ESP Operation;  The permittee shall operate and maintain the ESP to minimize PM emissions.  The permittee is authorized to operate the ESP with fields removed from service, under the operating conditions that demonstrated compliance during testing, when conducting repairs or maintenance on the ESP.

[Rules 62-4.070(3) and 62-212.400 (BACT), F.A.C.]

RECORDKEEPING AND REPORTING REQUIREMENTS

E.27.E.26.	Total Reduced Sulfur (TRS) continuous emissions monitoring quarterly report shall comply with the applicable requirements in Rule 62-296.404(6), F.A.C.

E.28.(a).E.27.(a).	Semiannual Monitoring Reports:  The permittee shall submit a written report to the Compliance Authority summarizing the following for each calendar quarter:  CO, NOX, SO2, and TRS emissions; opacity; CEMS monitor availability; gallons of oil fired; and total hours of operation.  The reports shall identify any exceedance of an emissions or performance limitation.  The reports are due within 30 days following the second and fourth calendar quarters.

[Rule 62-4.070(3), F.A.C.; and Construction Permit No. 1070005-038-AC]

E.28.(b).E.27.(b).	Semiannual Monitoring Reports: The permittee shall submit a written report to the Northeast District Office (Compliance Authority) summarizing the following for each calendar quarter:

- Gallons of virgin ULSD fired;

- Gallons of Black Liquor fired (including percent solids, estimated density);

- Total Hours of operation;

- Demonstration that the fuel firing and heat input rate limitations of Specific Condition E.3.  have been met;

- Copies of vendor certification for each ULSD fuel delivery as required in Specific Condition E.15.

The reports shall identify any exceedance of an emissions or performance limitation.  The reports shall be submitted no later than 30 days following the second and fourth calendar quarters.

[Rule 62-4.070(3), F.A.C.; Construction Permit No. 1070005-038-AC, and Applicant's Request in Application No. 1070005-076-AV/079-AC]

E.29.E.28.	 CEMS Required for Reporting Annual Emissions:  The permittee shall use SO2 data from the CEMS when calculating annual emissions for purposes of computing actual emissions, baseline actual emissions and net emissions increase, as defined at Rule 62-210.200, F.A.C., and for purposes of computing emissions pursuant to the reporting requirements of Rules 62-210.370(3) and 62-212.300(1)(e), F.A.C.  The permittee shall comply with Specific Conditions E.34E.30.Calculating and Reporting Annual Emissions, Condition. 14. of this permit.

[Rule 62-4.070(3), F.A.C.; Construction Permit No. 1070005-050-AC]

E.30.E.29.	 Fuel Oil Firing Records:  The permittee shall operate and maintain an oil flow monitoring system to determine compliance with the oil firing limitations for the No. 4 Recovery Boiler (gallons per consecutive rolling 24-hour period and MMBtu per consecutive rolling 12-month period).

[Rules 62-4.160(15) and 62-4.070(3), F.A.C.; and Construction Permit No. 1070005-050-AC]

Standard Continuous Monitoring Requirements

The No. 4 Recovery Boiler (EU-018) is subject to the following requirements for the new continuous emissions monitoring systems (CEMS) required for CO and NOX emissions.

E.31.E.30.	 CEMS Operation Plan: The permittee shall implement a plan for the proper calibration, maintenance, and operation of each CEMS required by this permit

[Rule 62-4.070(3), F.A.C.]

Monitors, Performance Specifications and Quality Assurance

- Span Values and Dual Range Monitors:  The permittee shall set appropriate span values for the CEMS based on the emissions standards and range of operation.  If necessary, the permittee shall install dual range monitors in accordance with the CEMS Operation Plan.

[Rule 62-4.070(3), F.A.C.]

- Diluent Monitor:  If required by permit to correct the CEMS output to the oxygen concentrations specified in the applicable emissions standard, the permittee shall either install an oxygen monitor or install a CO2 monitor and use an appropriate F-Factor computational approach.

[Rules 62-212.400 (BACT) and 62-4.070(3), F.A.C.]

- Moisture Correction:  If necessary, the permittee shall install a system to determine the moisture content of the exhaust gas and develop an algorithm to enable correction of the monitoring results to a dry basis (0% moisture).

[Rules 62-212.400 (BACT) and 62-4.070(3), F.A.C.]

- Continuous Flow Monitor:  For compliance with mass emission flow rate standards, the permittee shall install a continuous flow monitor to determine the stack exhaust flow rate.  The flow monitor shall be certified pursuant to 40 CFR Part 60, Appendix B, Performance Specification 6.  Alternatively, the permittee may install a fuel flow monitor and use an appropriate F-Factor computational approach to calculate stack exhaust flow rate.

[Rules 62-212.400 (BACT) and 62-4.070(3), F.A.C.]

- Performance Specifications:  The permittee shall evaluate the “acceptability” of each CEMS by conducting the appropriate performance specification.  For CO monitors, the permittee shall conduct Performance Specification 4 of 40 CFR Part 60, Appendix B.  For NOX monitors, the permittee shall conduct Performance Specification 2 of 40 CFR Part 60, Appendix B.

[Rule 62-4.070(3), F.A.C.]

- Quality Assurance:  The permittee shall follow the quality assurance procedures of 40 CFR Part 60, Appendix F.  For CO, the required relative accuracy test audit (RATA) tests shall be performed using EPA Method 10 in Appendix A of 40 CFR Part 60.  For NOX, the RATA tests shall be performed using EPA Method 7E in Appendix A of 40 CFR Part 60.  [Rule 62-4.070(3), F.A.C.]

CALCULATION APPROACH FOR SIP COMPLIANCE

- CEMS for Compliance:  The permittee shall use the CEMS to demonstrate compliance with the applicable emission standards as specified by this permit.

[Rules 62-212.400 (BACT) and 62-4.070(3), F.A.C.]

- CEMS Data:  Each CEMS shall monitor and record emissions during all operations and whenever emissions are being generated, including during episodes of startups, shutdowns, and malfunctions.  All data shall be used, except for invalid measurements taken during monitor system breakdowns, repairs, calibration checks, zero adjustments, and span adjustments.  [Rule 62-4.070(3), F.A.C.]

- Operating Hours and Operating Days:  For purposes of this Specific Condition, the following definitions shall apply.  An hour is the 60-minute period beginning at the top of each hour.  Any hour during which an emissions unit is in operation for more than 15 minutes is an operating hour for that emission unit.  A day is the 24-hour period from 6:00 am to 6:00 am.  Any day with at least one operating hour for an emissions unit is an operating day for that emission unit.

[Rule 62-4.070(3), F.A.C.]

- Valid Hourly Averages:  Each CEMS shall be designed and operated to sample, analyze, and record data evenly spaced over the hour at a minimum of one measurement per minute.  All valid measurements collected during an hour shall be used to calculate a 1-hour block average that begins at the top of each hour.

Hours that are not operating hours are not valid hours.

For each operating hour, the 1-hour block average shall be computed from at least two data points separated by a minimum of 15 minutes.  If less than two such data points are available, there is insufficient data, the 1-hour block average is not valid, and the hour is considered as “monitor unavailable.”

[Rule 62-4.070(3), F.A.C.]

- Calculation Approaches:  The permittee shall implement the calculation approach specified by this permit for each CEMS, as follows:

Daily Averages:  A daily average shall be calculated and recorded for each operating day as the arithmetic average of all valid hourly averages occurring from midnight to midnight.

Rolling 30-day Average.  Compliance with the 30-day rolling average shall be determined after each operating day by calculating and recording the arithmetic average of all valid hourly averages for the previous 30 operating days (compliance period).

Rolling 12-month Average:

Rolling 12-month Totals:

[Rules 62-212.400 (BACT) and 62-4.070(3), F.A.C.]

- Minimum Valid Hours:  At least one valid hourly average shall be used to calculate the emissions over any averaging period specified by this permit.  One valid hourly average shall be sufficient to calculate the emissions over any averaging period.

[Rule 62-4.070(3), F.A.C.]

MONITOR AVAILABILITY

13.  Monitor Availability:  Monitor availability shall be calculated on a quarterly basis for each emission unit as the number of valid hourly averages obtained by the CEMS, divided by the number of operating hours, times 100%.  The monitor availability calculation shall not include periods of time where the monitor was functioning properly, but was unable to collect data while conducting a mandated quality assurance/quality control activity such as calibration error tests, RATA, calibration gas audit, or relative accuracy audits (RAA).  Monitor availability for each CEMS shall be 95% or greater in any calendar quarter.

Monitor availability shall be reported in the quarterly excess emissions report.  In the event 95% availability is not achieved, the permittee shall provide the Department with a report identifying the problems in achieving 95% availability and a plan of corrective actions that will be taken to achieve 95% availability.  The permittee shall implement the reported corrective actions within the next calendar quarter.  Failure to take corrective actions or continued failure to achieve the minimum monitor availability shall be violations of this permit.                           [Rules 62-212.400 (BACT) and 62-4.070(3), F.A.C.]

CALCULATING and Reporting ANNUAL EMISSIONS

- a.	CEMS for Calculating Annual Emissions:  As defined by this Specific Condition, all valid data shall be used when calculating annual emissions.

Annual emissions shall include data collected during startup, shutdown, and malfunction periods.

Annual emissions shall include data collected during periods when the emission unit is not operating, but emissions are being generated (for example, firing fuel to warm up a process for some period of time prior to the emission unit’s “official” startup).

Annual emissions shall not include data from periods of time where the monitor was functioning properly but was unable to collect data while conducting a mandated quality assurance/quality control activity such as calibration error tests, RATA, calibration gas audit, or RAA.  These periods of time shall be considered “missing data” for purposes of calculating annual emissions.

Annual emissions shall not include data from periods of time when emissions are in excess of the calibrated span of the CEMS.  These periods of time shall be considered “missing data” for purposes of calculating annual emissions.

Accounting for Missing Data:  All valid measurements collected during each hour shall be used to calculate a 1-hour block average that begins at the top of each hour.  For each hour, the 1-hour block average shall be computed from at least two data points separated by a minimum of 15 minutes.  If less than two such data points are available, the permittee shall account for emissions during that hour using site-specific data to generate a reasonable estimate of the 1-hour block average.

Emissions Calculation:  Annual emissions shall be calculated as the sum of all valid emissions occurring during the year.

Reporting Annual Emissions:  The permittee shall use data from each required CEMS when calculating annual emissions for purposes of computing actual emissions, baseline actual emissions, and net emissions increase, as defined at Rule 62-210.200, F.A.C., and for purposes of computing emissions pursuant to the reporting requirements of Rules 62-210.370(3) and 62-212.300(1)(e), F.A.C.

[Rules 62-212.400 (BACT) and 62-4.070(3), F.A.C.]

b. 	Actual Emissions Reporting: Permit No. 1070005-072-AC is based on an analysis that compared baseline actual emissions with projected actual emissions and the project avoided the requirements of subsection 62-212.400(4) through (12), F.A.C. for several pollutants.  Therefore, pursuant to Rule 62-212.300(1)(e), F.A.C., the permittee is subject to the following monitoring, reporting and recordkeeping provisions.

- The permittee shall monitor the emissions of any PSD pollutant that the Department identifies could increase as a result of the construction or modification and that is emitted by any emissions unit that could be affected; and, using the most reliable information available, calculate and maintain a record of the annual emissions, in tons per year on a calendar year basis, for a period of 5 years following resumption of regular operations after the change.  Emissions shall be computed in accordance with the provisions in Rule 62-210.370, F.A.C., which are provided in Appendix C of this permit.

- The permittee shall report to the Department within 60 days after the end of each calendar year during the 5-year period setting out the unit’s annual emissions during the calendar year that preceded submission of the report.  The report shall contain the following:

  - The name, address and telephone number of the owner or operator of the major stationary source;

  - The annual emissions as calculated pursuant to the provisions of 62-210.370, F.A.C., which are provided in Appendix C of this permit;

  - If the emissions differ from the preconstruction projection, an explanation as to why there is a difference; and

  - Any other information that the owner or operator wishes to include in the report.

- The information required to be documented and maintained pursuant to subparagraphs 62-212.300(1)(e)1 and 2, F.A.C., shall be submitted to the Department, which shall make it available for review to the general public.

- The permittee shall compute and report annual emissions in accordance with Rule 62-210.370(2), F.A.C. as provided by Appendix C of this permit.  For this project, the permittee shall use the following methods in reporting the actual annual emissions for the No. 4 Recovery Boiler to show compliance with the established BACT emission limits included in the previous permit PSD-FL-380 (1070005-038-AC):

  - The permittee shall use data collected from the CEMS to determine and report the actual annual emissions of CO, NOX, SO2, and TRS and opacity.

  - The permittee shall use the data collected from the required stack tests to determine and report the actual annual emissions of filterable PM/PM10.  The permittee shall follow the stack test methods, test procedures and test frequencies specified in the current Title V air operation permit.

  - The permittee shall use the data collected from the required stack tests to determine and report the actual emissions of VOC in accordance with the stack test methods, test procedures and test frequencies specified in the current Title V air operation permit.

  - As defined in Rule 62-210.370(2), F.A.C., the permittee shall use a more accurate methodology if it becomes available.

[Project No. 1070005-076-AV/079-AC Application; Rules 62-212.300(1)(e) and 62-210.370, F.A.C.]

COMMON CONDITIONS - ON-SPEC USED OIL

E.32.E.31.	 This emissions unit is also subject to the On-Spec Used Oil requirements in Subsection W.

COMMON CONDITIONS - EXCESS EMISSIONS

E.33.E.32.	 This emissions unit is also subject to applicable Excess Emissions requirements in Subsection X.

COMMON CONDITIONS - F.A.C. TEST REQUIREMENTS

E.34.E.33.	 This emissions unit is also subject to applicable F.A.C. Test Requirements in Subsection Y.

COMMON CONDITIONS - KRAFT (SULFATE) PULP MILLS

E.35.E.34.	 This emissions unit is also subject to applicable Kraft (Sulfate) Pulp Mills Requirements in Subsection Z.

COMMON CONDITIONS - PERIODIC MONITORING

E.36.E.35.	 This emissions unit is also subject to applicable Periodic Monitoring Requirements in Subsection AA.