##### PERMITTEE

Broward County Water & Wastewater Services

2555 West Copans Road

Pompano Beach, Florida 33069

##### Permitting Authority

Florida Department of Environmental Protection

Air Resource Section

Southeast District Office

400 North Congress Avenue

West Palm Beach, Florida 33401

##### PROJECT

Air Permit Nos. 0112357-015-AC

Minor Source Air Construction Permit

Broward County North Regional Wastewater Treatment Plant

##### This is the final air construction permit, which authorizes the permittee to install a digester gas fired electric generator with waste heat recovery/reuse.

##### NOTICE AND PUBLICATION

The Department distributed a draft minor source air construction permit package on July 7, 2014.  The applicant published the Public Notice in the Broward Daily Business Review on July 17, 2014.  The Department received the proof of publication on July 22, 2014.  No requests for administrative hearings or requests for extensions of time to file a petition for administrative hearing were received.

# COMMENTS

Applicant

On August 4, 2014, the Department received comments from the applicant.  The following summarizes the comments and the Department’s response.

- On page 3 of 7 of the Technical Evaluation and Preliminary Determination:

PSD Applicability for Project

The proposed new equipment is a GE/Jenbacher Spark Ignition Internal Combustion Engine (Model JMS 616GX-B.L) utilizing digester gas as its fuel. The engine will be powering a 1.999 MW electrical generator. Waste heat from the engine will be utilized for heating the digester tanks. The facility currently has a 90 ton per year limit on NOx emissions in order to escape Title V Applicability and the applicant requests that the facility have a 90 ton per year CO limit in addition. Would this not be “instead”?  If not, how will the plant’s annual testing requirements change?

DEP Response:  The facility is close to 90 tons per year for both CO and NOx.  With the uncertainty of the emission rates from both the Co-generator and the generators (which are to be modified soon), the Department feels that changing the synthetic limit for both CO and NOx is best left until more test data is available.  If, with more test data, the facility appears to be very close to emitting 90 tons per year for both CO and NOx, the annual testing will be modified to include both.

- On page 4 of 7 of the Technical Evaluation and Preliminary Determination:

Since the emissions of engines running on digester gas are difficult to predict, the facility will be required to request a modification in the emergency generator diesel fuel limit based on the results of the co-generator’s initial performance tests.

Depending on test results, could the diesel fuel limits be raised above those shown in the table on page 5 of 7 for EU 003 for HOP?

DEP Response:  It is possible that the synthetic fuel limits may be adjusted up or down depending on the results of the performance testing.

- On page 6 of 7 of the Technical Evaluation and Preliminary Determination in the 2nd column of Table A, the Current Emissions (TPY) listed are not limits (except NOx) but rather actual outputs.  Should the word “Permitted” be stuck from the column heading?

DEP Response:  The table should have indicated that only the 90 ton per year for NOx limit is a permit limit.  The other actual emissions are permitted, but not the permit limits.

- In the Air Construction Permit (Draft), on page 5 of 10, Item 4 of EU 005: The hours of operation are limited to 7621 hours per year.  Is this a hard annual limit?  Or can it vary as long as the annual CO is less than 90 TPY?  Its runtime was intended to be an average that will vary depending upon the particular maintenance activities that will occur during a given year.  For example, some years will have greater downtime than others due to minor or major overhauls.  Additionally, initial test results may show a lower hourly emissions rate than permitted in which case 7621 annual hours could be overly restrictive.

DEP Response:  The Department understood that the estimated maintenance time reported in the application would be the minimum amount of maintenance the units would require per year.  The Department will change the Condition to read:

4. Restricted Operation: The hours of operation of are only limited to 7621 hours per year by required maintenance. [Application No. 0112357-015-AC, Rules 62-4.070(3) and 62-210.200(PTE), F.A.C.]

- In the Air Construction Permit (Draft), on page 9 of 10, Item 16c.  Is the CO emission for the unit for EU 005 only?

DEP Response:  This Construction Permit covers the construction of EU005, therefore the requirement in this construction permit only applies to EU005.  However, at the time of Operation Permit modification, it may be decided to expand the AOR Requirement to include the highest 12-month total to include CO for the other emission units, depending on the results of initial performance tests for the cogenerator and the new and modified generators.

- Same page, Item 20.  We just couldn’t find Specific Condition A.8.

DEP Response:  The text will be changed to

20. The permittee shall submit a copy of each performance test that was conducted in accordance of with Specific Conditions A.89. and 10., within 60 days after the test has been completed.

[40 CFR 60.4245(d)]

# CONCLUSION

The final action is to issue the permit with the minor changes, corrections and clarifications as described above.