NOTICE OF ADMINISTRATIVELY CORRECTED TITLE V AIR OPERATION PERMIT

In the Matter of a Request for Administrative Correction:

| Florida Power Development, LLC 10311 Cement Plant Road Brooksville, Florida 34601 Authorized Representative: Terry Woodard, Plant Manager | Project No. 0530380-003-AC |
| --- | --- |
|  | Administrative Correction to: Permit No. 0530380-001-AC (PSD-FL-090E) |
|  | Hernando County |

Dear Mr. Woodard,

Enclosed is an administratively correction for Air Construction Permit No. 0530380-001-AC (PSD-FL-090E) for Brooksville Power Plant, which is located in Hernando County at 10311 Cement Plant Road, Brooksville, Florida.  This action will correct reference to the quarterly emissions reporting requirements identified in the previously issued Permit No. 0530380-001-AC.

This administrative correction is issued pursuant to Rule 62-210.360, Florida Administrative Code (F.A.C.), and Chapter 403, Florida Statutes (F.S.).  This change is made at the applicant’s request dated July 1, 2014.  This corrective action does not alter the effective dates of the existing permit.

The Department of Environmental Protection (Department) will consider the above-noted action final unless a timely petition for an administrative hearing is filed pursuant to Sections 120.569 and 120.57, F.S.  Mediation under Section 120.573, F.S., will not be available for this proposed action.

Petitions:  A person whose substantial interests are affected by the proposed permitting decision may petition for an administrative hearing in accordance with Sections 120.569 and 120.57, F.S.  The petition must contain the information set forth below and must be filed with (received by) the Department’s Agency Clerk in the Office of General Counsel of the Department of Environmental Protection, 3900 Commonwealth Boulevard, Mail Station #35, Tallahassee, Florida 32399-3000.  Petitions must be filed within 14 days of receipt of this administratively corrected permit.  A petitioner shall mail a copy of the petition to the applicant at the address indicated above, at the time of filing.  The failure of any person to file a petition within the appropriate time period shall constitute a waiver of that person’s right to request an administrative determination (hearing) under Sections 120.569 and 120.57, F.S., or to intervene in this proceeding and participate as a party to it.  Any subsequent intervention (in a proceeding initiated by another party) will be only at the approval of the presiding officer upon the filing of a motion in compliance with Rule 28-106.205, F.A.C.

A petition that disputes the material facts on which the Permitting Authority’s action is based must contain the following information: (a) The name and address of each agency affected and each agency’s file or identification number, if known; (b) The name, address, and telephone number of the petitioner; the name, address and telephone number of the petitioner’s representative, if any, which shall be the address for service purposes during the course of the proceeding; and an explanation of how the petitioner’s substantial interests will be affected by the agency determination; (c) A statement of when and how each petitioner received notice of the agency action or proposed decision; (d) A statement of all disputed issues of material fact.  If there are none, the petition must so state; (e) A concise statement of the ultimate facts alleged, including the specific facts the petitioner contends warrant reversal or modification of the agency’s proposed action; (f) A statement of the specific rules or statutes the petitioner contends require reversal or modification of the agency’s proposed action including an explanation of how the alleged facts relate to the specific rules or statutes; and, (g) A statement of the relief sought by the petitioner, stating precisely the action the petitioner wishes the agency to take with respect to the agency’s proposed action.  A petition that does not dispute the material facts upon which the Permitting Authority’s action is based shall state that no such facts are in dispute and otherwise shall contain the same information as set forth above, as required by Rule 28-106.301, F.A.C.

Because the administrative hearing process is designed to formulate final agency action, the filing of a petition means that the Permitting Authority’s final action may be different from the position taken by it in this written notice.  Persons whose substantial interests will be affected by any such final decision of the Permitting Authority on the application have the right to petition to become a party to the proceeding, in accordance with the requirements set forth above.

Judicial Review:  Any party to this permitting decision (order) has the right to seek judicial review of it under Section 120.68, F.S., by filing a notice of appeal under Rule 9.110 of the Florida Rules of Appellate Procedure with the clerk of the Department of Environmental Protection in the Office of General Counsel, Mail Station #35, 3900 Commonwealth Boulevard, Tallahassee, Florida, 32399-3000, and by filing a copy of the notice of appeal accompanied by the applicable filing fees with the appropriate District Court of Appeal.  The notice must be filed within 30 days after this order is filed with the clerk of the Department.

# Executed in Tallahassee, Florida.

for	Jeffery F. Koerner, Program Administrator

Office of Permitting and Compliance

Division of Air Resource Management

JFK/dr/ttm

# CERTIFICATE OF SERVICE

The undersigned duly designated deputy agency clerk hereby certifies that this Air Permit package was sent by electronic mail (including the corrected pages), or a link to these documents made available electronically on a publicly accessible server, with received receipt requested before the close of business on the date indicated below to the following persons.

Mr. Terry Woodard, Plant Manager, FPD:  wwoodard@deltapowerservices.com

Mr. Larry Roberts, FPD:  lroberts@deltapowerservices.com

Mr. Max Lee, Ph.D., P.E., Koogler:  mlee@kooglerassociates.com

Ms. Kelley Boatwright, Program Administrator, SWD:  kelley.m.boatwright@dep.state.fl.us

Mr. Justin Green, DEP Siting Office:  justin.b.green@dep.state.fl.us

# Ms. Ana Oquendo, EPA Region 4:  Oquendo.Ana@epamail.epa.gov

# Ms. Natasha Hazziez, EPA Region 4:  hazziez.natasha@epa.gov

# Ms. Barbara Friday, DEP OPC:  barbara.friday@dep.state.fl.us

# Ms. Lynn Scearce, DEP OPC:  lynn.scearce@dep.state.fl.us

# Clerk Stamp

# FILING AND ACKNOWLEDGMENT FILED, on this date, pursuant to Section 120.52(7), Florida Statutes, with the designated agency clerk, receipt of which is hereby acknowledged.

The following permit condition is revised as indicated.  Strikethrough is used to denote the deletion of test Double-underlines are used to denote the addition of text.  All changes are emphasized with shading.

Permit Being Administratively Corrected:  Permit No. 0530380-001-AC (PSD-FL-090E)

Affected Emissions Unit:  Woody Biomass-Fueled Grate Suspension Boiler (EU 002)

SECTION III.  EMISSION UNITS AND SPECIFIC CONDITIONS

Subsection B.  Grate Suspension Boiler (EU 002)

Specific Condition 28 is corrected as follows:

- Quarterly SO2, CO, NOX and Opacity Emissions Report:  Within 30 days following the end of each quarter, the permittee shall submit a report to the Compliance Authority summarizing SO2, CO, NOX and opacity emissions including periods of startups, shutdowns, malfunctions, and CEMS and COMS systems monitor availability for the previous quarter.  If opacity COMS data is excluded from a compliance determination during the quarter due to a malfunction, the permittee shall include a description of the malfunction, the actual emissions recorded, and the actions taken to correct the malfunction in the quarterly report.  After the first full four quarters of operation, the permittee may request approval from the Compliance Authority to submit these reports on a semiannual basis.  See Appendix CTR of this permitFigure 1 in 40 CFR 60,7(d) for the reporting format.  [Rules 62-4.070(3), 62-4.130, and 62-210.400(5)(c), F.A.C.]

Subsection E.  Emergency Equipment (EU 005)

Based on clarification received from the applicant, the emergency diesel generator and the fire pump are not subject to NESHAP Subpart ZZZZ of Title 40, Part 63 of the code of federal regulations.  The 250 kilowatt (kW) emergency ditch pump was removed from the site and the 500 kW emergency diesel engine was corrected to a 460 kW (610 brake-horse power (bhp)) emergency diesel engine.  Based on the engines size and nature of its use, the emergency diesel fired engine is not subject to Subpart ZZZZ of 40 CFR 63.  In addition, the emergency diesel engine fires less than 64,000 gallons of diesel fuel; therefore, is exempt from permitting pursuant to Rule 62-210.300(a) and is listed as an unregulated emission unit.  Therefore, the following conditions in the air construction permit are obsolete and are removed from the permit.

Subsection E.  Emergency Equipment (EU 005).

| EU ID No. | EU Description |
| --- | --- |
| 005 | One emergency diesel generator with a maximum design rating of 500 kilowatt (kW) and one emergency ditch pump with a maximum design rating of 250 kW.Emergency Diesel Generator (610 bhp) |

nsps and NESHAP APPLICABILITY

- NSPS Subpart IIII Applicability:  The emergency generator was manufactured in 1963 while the emergency ditch pump was manufactured in 1961.  Consequently, while both are stationary compression ignition internal combustion engine, the provisions of 40 CFR 60, Subpart IIII, including emission testing or certification do not apply.  [40 CFR 60, Subpart IIII - Standards of Performance for Stationary Compression Ignition Internal Combustion Engines]

- NESHAPS Subpart ZZZZ Applicability:  The emergency generator and emergency ditch pump are subject to the applicable provisions of 40 CFR 63, Subpart ZZZZ.

- Change oil and filter every 500 hours of operation or annually, whichever comes first;

- Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first;

- Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary.

Minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes, after which time the non-startup emission limitations apply.  [§§63.6600 and 63.6640]

If you own or operate an existing emergency stationary RICE with a site rating of less than or equal to 500 brake HP located at a major source of HAP emissions or an existing emergency stationary RICE located at an area source of HAP emissions, you must install a non-resettable hour meter if one is not already installed.  [§ 63.6625(f)]

[40 CFR 63, Subpart ZZZZ - National Emission Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines]

EQUIPMENT

- Emergency Ditch Pump:  The permittee is authorized to continue to operate, and maintain one emergency ditch pump with a maximum design rating of 250 kW (335 hp).  
[Application No. 0530380-001-AC and Rule 62-210.200 (PTE), F.A.C.]

Performance Restrictions

- Hours of Operation:  The emergency generator and the emergency ditch pump may each operate up to 100 hours per year for maintenance and testing purposes.  Operation during emergency conditions is unlimited.  [Application No. 0530380-001-AC and Rule 62-210.200 (PTE), F.A.C.]

- Authorized Fuel:  The emergency generator and emergency ditch pump shall fire ultra low sulfur distillate fuel only.  The ultra low sulfur distillate fuel oil fired in the generator and ditch pump shall have a vendor certification indicating its sulfur content is 0.0015% or less.  [Application No. 0530380-001-AC and Rule 62-210.200 (PTE), F.A.C.]

RECORDS AND REPORTS

- Notification, Recordkeeping and Reporting Requirements:  The permittee shall maintain records demonstrating fuel usage and quality along with the hours of operation for testing and maintenance purposes for both the emergency generate and ditch pump.  [Rule 62-4.070(3), F.A.C.]