# APPENDIX A

Operation and Maintenance Plan

for Particulate Control for

CSX Transportation, Inc.

Newport Terminal

Emission Unit No. 100 - Baghouse A

Operation and Maintenance Plan for Particulate Control: [Rule 62-296.700, F.A.C.]

A)	Process Parameters:

- Source Designators: Railcar Unloader w/Baghouse A

- Baghouse Manufacturer: Mikro-Pulsaire

- Model Name and Number: 2G-8

- Flow Rate: 154,670 DSCFM

- Efficiency Rating at Design Capacity:  99.99%

- Pressure Drop: 0-8 in. H2O

- Air to Cloth Ratio:  11.05 : 1

- Bag Weave:  Felt

- Bag Material:  Polyester

- Bag Cleaning Conditions:  Pulse at 90 psig

- Gas Temperatures:  inlet; Ambient, outlet; Ambient

- Stack Height Above Ground:  14 ft

- Exit Diameter: 7.5 ft.

- Water Vapor Content:  Ambient

- Process Controlled by Collection System:  Railcar Unloading

- Material Handling Rate: Wet Phosphate Rock – 2,800 TPH max, MAP/DAP/GTSP – 2,000 TPH max

- Operation Schedule:  1,800 hours per year

B)	The following observations, checks and operations apply to this source and shall be conducted on the schedule specified:

Daily

- Check the pressure drop if the baghouse is in operation while material is being handled.

- Observe stack (visual).

- Walk through system listening for proper operation (audible leaks, proper fan/motor functions, bag cleaning systems).

- Note any unusual occurrence in the process being ventilated.

- Observe all indicators on control panel.

- Check pulse (compressed) air pressure.

- Assure that dust is being removed from system.

Weekly

- Inspect screw conveyor and air lock bearings for lubrication.

- Check packing glands.

- Operate all damper valves (isolation, by-pass, etc.).

- Check bag cleaning sequence to see that all valves are opening and closing properly.

- Spot check bag tension inside bag collectors.

- Check pressure drop indicating equipment for plugged lines.

- Check compressed air lines, including line oilers and filters.

Monthly

- Check cleaning mechanism moving parts.

- Inspect fans for corrosion and material build-up.

- Check all drive belts and chains for wear and tension.

- Check all hoses and clamps.

- Check accuracy of all indicating equipment.

- Inspect housing for corrosion.

Quarterly

- Inspect baffle plate for wear.

- Thoroughly inspect bags.

- Check duct for dust build-up.

- Observe damper valves for proper seating.

- Check gaskets on all doors.

- Inspect paint.

- Check screw conveyor flighting.

Annually

- Check all bolts.

- Check welds.

- Inspect hopper for wear.

- Check airlock rotor for wear.

C)	Records:

Records of inspections, maintenance, and performance parameters shall be retained for a minimum of five years and shall be made available to the Department or Environmental Protection Commission of Hillsborough County upon request. [Rule 62-296.700(6)(e), F.A.C.]

Emission Unit No. 102 - Baghouse B

Operation and Maintenance Plan for Particulate Control: [Rule 62-296.700, F.A.C.]

A)	Process Parameters:

- Source Designators: Belt 7 to 8 or 9 Transfer Point with Baghouse B

- Baghouse Manufacturer:  Mikro-Pulsaire

- Model Name and Number: 1F-2

- Design Flow Rate: 11,250 ACFM

- Efficiency Rating at Design Capacity:  99.99%

- Pressure Drop: 0-8 in. H2O

- Air to Cloth Ratio:  2.89 to 1

- Bag Weave:  Felt

- Bag Material:  Polyester

- Bag Cleaning Conditions:  Pulse at 90 psig

- Gas Flow Rate: 9,563 DCSFM (design)

- Gas Temperatures:  inlet; Ambient, outlet; Ambient

- Stack Height Above Ground:  10.5  ft.

- Exit Diameter: 16" x 183/8"

- Water Vapor Content:  Ambient

- Process Controlled by Collection System: Conveyor Belt Transfer Point

- Material Handling Rate: Wet Phosphate Rock - 2,800 TPH max, MAP/DAP/GTSP - 2,000 TPH max

- Operation Schedule:  1,800 hours per year

B)	The following observations, checks and operations apply to this source and shall be conducted on the schedule specified:

Daily

- Check the pressure drop if the baghouse is in operation while material is being handled.

- Observe stack (visual).

- Walk through system listening for proper operation (audible leaks, proper fan and motor functions, bag cleaning systems, etc.).

- Note any unusual occurrence in the process being ventilated.

- Observe all indicators on control panel.

- Check pulse (compressed) air pressure.

- Assure that dust is being removed from system.

Weekly

- Inspect screw conveyor and air lock bearings for lubrication.

- Check packing glands.

- Operate all damper valves (isolation, by-pass, etc.).

- Check bag cleaning sequence to see that all valves are opening and closing properly.

- Spot check bag tension inside bag collectors.

- Check pressure drop indicating equipment for plugged lines.

- Check compressed air lines, including line oilers and filters.

Monthly

- Check cleaning mechanism moving parts.

- Inspect fans for corrosion and material build-up.

- Check all drive belts and chains for wear and tension.

- Check all hoses and clamps.

- Check accuracy of all indicating equipment.

- Inspect housing for corrosion.

Quarterly

- Inspect baffle plate for wear.

- Thoroughly inspect bags.

- Check duct for dust build-up.

- Observe damper valves for proper seating.

- Check gaskets on all doors.

- Inspect paint.

- Check screw conveyor flighting.

Annually

- Check all bolts.

- Check welds.

- Inspect hopper for wear.

- Check airlock rotor for wear.

C)	Records:

Records of inspections, maintenance, and performance parameters shall be retained for a minimum of five years and shall be made available to the Department or Environmental Protection Commission of Hillsborough County upon request. [Rule 62-296.700(6)(e), F.A.C.]

Emission Unit No. 104 - Baghouse D

Operation and Maintenance Plan for Particulate Control: [Rule 62-296.700, F.A.C.]

A)	Process Parameters:

- Source Designators: Belt #9 to #4 Transfer Point with Baghouse "D"

- Baghouse Manufacturer: Mikro-Pulsaire

- Model Name and Number: 64S-8-20

- Design Flow Rate: 4,500 ACFM

- Efficiency Rating at Design Capacity:  99.99%

- Pressure Drop: 0-8 in. H2O

- Air to Cloth Ratio:  7.48 : 1

- Bag Weave:  Felt

- Bag Material:  Polyester

- Bag Cleaning Conditions:  Pulse Air @ 90 psi

- Gas Flow Rate: 4,050 DSCFM (design)

- Gas Temperatures:  inlet; Ambient,  outlet; Ambient.

- Stack Height Above Ground:  10.5  ft.

- Exit Diameter: 11" X 12 13/16"

- Water Vapor Content:  Ambient

- Process Controlled by Collection System:  Outgoing Transfer

- Material Handling Rate:  Wet Phosphate Rock – 2,800 TPH max, MAP/DAP/GTSP – 2,000 TPH max.

- Operation Schedule:  1,800 hours per year

B)	The following observations, checks and operations apply to this source and shall be conducted on the schedule specified:

Daily

- Check the pressure drop if the baghouse is in operation while material is being handled.

- Observe stack (visual).

- Walk through system listening for proper operation (audible leaks, proper fan and motor functions, bag cleaning systems, etc.).

- Note any unusual occurrence in the process being ventilated.

- Check pulse (compressed) air pressure.

- Assure that dust is being removed from system.

Weekly

- Inspect screw conveyor and air lock bearings for lubrication.

- Check packing glands.

- Operate all damper valves (isolation, by-pass, etc.).

- Check bag cleaning sequence to see that all valves are opening and closing properly.

- Spot check bag tension inside bag collectors.

- Check pressure drop indicating equipment for plugged lines.

- Check compressed air lines, including line oilers and filters.

Monthly

- Check cleaning mechanism moving parts.

- Inspect fans for corrosion and material build-up.

- Check all drive belts and chains for wear and tension.

- Check all hoses and clamps.

- Check accuracy of all indicating equipment.

- Inspect housing for corrosion.

Quarterly

- Inspect baffle plate for wear.

- Thoroughly inspect bags.

- Check duct for dust build-up.

- Observe damper valves for proper seating.

- Check gaskets on all doors.

- Inspect paint.

- Check screw conveyor flighting.

Annually

- Check all bolts.

- Check welds.

- Inspect hopper for wear.

- Check airlock rotor for wear.

C)	Records:

Records of inspections, maintenance, and performance parameters shall be retained for a minimum of five years and shall be made available to the Department or Environmental Protection Commission of Hillsborough County upon request. [Rule 62-296.700(6)(e), F.A.C.]

Emission Unit No. 106 - Baghouse G

Operation and Maintenance Plan for Particulate Control: [Rule 62-296.700, F.A.C.]

A)	Process Parameters:

- Source Designators: Belt #5 to #6 Transfer Point with Baghouse "G"

- Baghouse Manufacturer: Mikro-Pulsaire

- Model Name and Number: 64S-8-20

- Design Flow Rate: 4500 ACFM

- Efficiency Rating at Design Capacity:  99.99%

- Pressure Drop: 0-8 in. H2O

- Air to Cloth Ratio:  7.48 to 1

- Bag Weave:  Felt

- Bag Material:  Polyester

- Bag Cleaning Conditions:  Pulse Air @ 90 psi

- Gas Flow Rate: 4,050 DSCFM (Design)

- Gas Temperatures:  inlet; Ambient  outlet; Ambient.

- Stack Height Above Ground:  10.5  ft.

- Exit Diameter: 11" X 12 13/16

- Water Vapor Content:  Ambient

- Process Controlled by Collection System:  Material Transfer

- Material Handling Rate: Wet Phosphate Rock - 2,800 TPH max, MAP/DAP/GTSP - 2,000 TPH max

- Operation Schedule:  1,800 hours per year

B)	The following observations, checks and operations apply to this source and shall be conducted on the schedule specified:

Daily

- Check the pressure drop if the baghouse is in operation while material is being handled.

- Observe stack (visual).

- Walk through system listening for proper operation (audible leaks, proper fan and motor functions, bag cleaning systems, etc.).

- Note any unusual occurrence in the process being ventilated.

- Check pulse (compressed) air pressure.

- Assure that dust is being removed from system.

Weekly

- Inspect screw conveyor and air lock bearings for lubrication.

- Check packing glands.

- Operate all damper valves (isolation, by-pass, etc.).

- Check bag cleaning sequence to see that all valves are opening and closing properly.

- Spot check bag tension inside bag collectors.

- Check pressure drop indicating equipment for plugged lines.

- Check compressed air lines, including line oilers and filters.

Monthly

- Check cleaning mechanism moving parts.

- Inspect fans for corrosion and material build-up.

- Check all drive belts and chains for wear and tension.

- Check all hoses and clamps.

- Check accuracy of all indicating equipment.

- Inspect housing for corrosion.

Quarterly

- Inspect baffle plate for wear.

- Thoroughly inspect bags.

- Check duct for dust build-up.

- Observe damper valves for proper seating.

- Check gaskets on all doors.

- Inspect paint.

- Check screw conveyor flighting.

Annually

- Check all bolts.

- Check welds.

- Inspect hopper for wear.

- Check airlock rotor for wear.

C)	Records:

Records of inspections, maintenance, and performance parameters shall be retained for a minimum of five years and shall be made available to the Department or Environmental Protection Commission of Hillsborough County upon request. [Rule 62-296.700(6)(e), F.A.C.]

Emission Unit No. 107 - Baghouse H

Operation and Maintenance Plan for Particulate Control: [Rule 62-296.700, F.A.C.]

A)	Process Parameters:

- Source Designators: Shiploader with Baghouse H

- Baghouse Manufacturer: Standard Havens

- Model Name and Number: Alpha Mark I Size 30

- Design Flow Rate: 52,000 ACFM

- Efficiency Rating at Design Capacity:  99.99%

- Pressure Drop: 0-8 in. H2O

- Air to Cloth Ratio:  7.43 : 1

- Bag Weave: Felt

- Bag Material:  Polyester

- Bag Cleaning Conditions:  Pulse Air 90 psig 14 second cycles

- Gas Flow Rate: 46,800 DSCFM (design)

- Gas Temperatures:  inlet; Ambient ;  outlet; Ambient.

- Stack Height Above Ground:  55  ft.

- Exit Diameter: 52" x 38"

- Water Vapor Content:  Ambient %

- Process Controlled by Collection System: Shiploading

- Material Handling Rate: Wet Phosphate Rock (2,800 tons/hour max.) MAP/DAP/GTSP (2,000 tons/hour max.)

- Operation Schedule:  1,800 hours per year

B)	The following observations, checks and operations apply to this source and shall be conducted on the schedule specified:

Daily

- Check the pressure drop if the baghouse is in operation while material is     being handled.

- Observe stack (visual).

- Walk through system listening for proper operation (audible leaks, proper fan and motor functions, bag cleaning systems, etc.).

- Note any unusual occurrence in the process being ventilated.

- Check pulse (compressed) air pressure.

- Observe indicators on control panel.

- Assure that dust is being removed from system.

Weekly

- Inspect screw conveyor and air lock bearings for lubrication.

- Check packing glands.

- Operate all damper valves (isolation, by-pass, etc.).

- Check bag cleaning sequence to see that all valves are opening and closing properly.

- Spot check bag tension inside bag collectors.

- Check pressure drop indicating equipment for plugged lines.

- Check compressed air lines, including line oilers and filters.

Monthly

- Check cleaning mechanism moving parts.

- Inspect fans for corrosion and material build-up.

- Check all drive belts and chains for wear and tension.

- Check all hoses and clamps.

- Check accuracy of all indicating equipment.

- Inspect housing for corrosion.

Quarterly

- Inspect baffle plate for wear.

- Thoroughly inspect bags.

- Check duct for dust build-up.

- Observe damper valves for proper seating.

- Check gaskets on all doors.

- Inspect paint.

- Check screw conveyor flighting.

Annually

- Check all bolts.

- Check welds.

- Inspect hopper for wear.

- Check airlock rotor for wear.

C)	Records:

Records of inspections, maintenance, and performance parameters shall be retained for a minimum of five years and shall be made available to the Department or Environmental Protection Commission of Hillsborough County upon request. [Rule 62-296.700(6)(e), F.A.C.]

Emission Unit No. 108 - Storage Building Ventilation,

S.E. Baghouse I

Operation and Maintenance Plan for Particulate Control: [Rule 62-296.700, F.A.C.]

A)	Process Parameters:

- Source Designators: Storage Building With S.E. Baghouse

- Baghouse Manufacturer: American Air Filter

- Model Name and Number: Amerpulse Size 10-312

- Design Flow Rate: 79,000 ACFM

- Efficiency Rating at Design Capacity:  99.99%

- Pressure Drop: 0-8 in. H2O

- Air to Cloth Ratio:  11.51 to 1

- Bag Weave: 200 Mesh

- Bag Material:  Polyester-felt

- Bag Cleaning Conditions:  Pulse-air (pressure 90 psi)

- Gas Flow Rate: 77,818 DSCFM

- Gas Temperatures:  inlet; Ambient ;  outlet; Ambient

- Stack Height Above Ground:  15  ft.

- Exit Diameter: 8 ft. 5 in.

- Water Vapor Content:  Ambient

- Process Controlled by Collection System:  Storage Building

- Material Handling Rate: Wet Phosphate Rock - 2,800 TPH max., MAP/DAP/GTSP - 2,000 TPH max.

- Operation Schedule:  1,800 hours per year

B)	The following observations, checks and operations apply to this source and shall be conducted on the schedule specified:

Daily

- Check the pressure drop if the baghouse is in operation while material is being handled.

- Observe stack (visual).

- Walk through system listening for proper operation (audible leaks, proper fan and motor functions, bag cleaning systems, etc.).

- Note any unusual occurrence in the process being ventilated.

Weekly

- Inspect screw conveyor and air lock bearings for lubrication.

- Check packing glands.

- Operate all damper valves (isolation, by-pass, etc.).

- Check bag cleaning sequence to see that all valves are opening and closing properly.

- Spot check bag tension inside bag collectors.

- Check pressure drop indicating equipment for plugged lines.

- Check inlet filter on reverse air blower.

- Check compressed air lines, including line oilers and filters.

Monthly

- Check cleaning mechanism moving parts.

- Inspect fans for corrosion and material build-up.

- Check all drive belts and chains for wear and tension.

- Check all hoses and clamps.

- Check accuracy of all indicating equipment.

- Inspect housing for corrosion.

Quarterly

- Inspect baffle plate for wear.

- Thoroughly inspect bags.

- Check duct for dust build-up.

- Observe damper valves for proper seating.

- Check gaskets on all doors.

- Inspect paint.

- Check screw conveyor flighting.

Annually

- Check all bolts.

- Check welds.

- Inspect hopper for wear.

- Check airlock rotor for wear.

C)	Records:

Records of inspections, maintenance, and performance parameters shall be retained for a minimum of five years and shall be made available to the Department or Environmental Protection Commission of Hillsborough County upon request. [Rule 62-296.700(6)(e), F.A.C.]

Emission Unit No. 109 - Storage Building Ventilation,

S.W. Baghouse II

Operation and Maintenance Plan for Particulate Control: [Rule 62-296.700, F.A.C.]

A)	Process Parameters:

- Source Designators: Storage Building With S.W. Baghouse

- Baghouse Manufacturer: American Air Filter

- Model Name and Number: Amerpulse Size 10-312

- Design Flow Rate: 79,000 ACFM

- Efficiency Rating at Design Capacity:  99.99%

- Pressure Drop: 0-8 in. H2O

- Air to Cloth Ratio:  11.51 to 1

- Bag Weave: 200 Mesh

- Bag Material:  Polyester-felt

- Bag Cleaning Conditions:  Pulse-air (pressure 90 psi)

- Gas Flow Rate: 78,329 DSCFM

- Gas Temperatures:  inlet; Ambient ;  outlet; Ambient

- Stack Height Above Ground:  15 ft.

- Exit Diameter: 8 ft. 5 in.

- Water Vapor Content:  Ambient

- Process Controlled by Collection System:  Storage Building

- Material Handling Rate: Wet Phosphate Rock - 2,800 TPH max, MAP/DAP/GTSP - 2,000 TPH max.

- Operation Schedule:  1,800 hours per year

B)	The following observations, checks and operations apply to this source and shall be conducted on the schedule specified:

Daily

- Check the pressure drop if the baghouse is in operation while material is being handled.

- Observe stack (visual).

- Walk through system listening for proper operation (audible leaks, proper fan and motor functions, bag cleaning systems, etc.).

- Note any unusual occurrence in the process being ventilated.

Weekly

- Inspect screw conveyor and air lock bearings for lubrication.

- Check packing glands.

- Operate all damper valves (isolation, by-pass, etc.)

- Check bag cleaning sequence to see that all valves are  opening and closing properly.

- Spot check bag tension inside bag collectors.

- Check pressure drop indicating equipment for plugged lines.

- Check inlet filter on reverse air blower.

- Check compressed air lines, including line oilers and filters.

Monthly

- Check cleaning mechanism moving parts.

- Inspect fans for corrosion and material build-up.

- Check all drive belts and chains for wear and tension.

- Check all hoses and clamps.

- Check accuracy of all indicating equipment.

- Inspect housing for corrosion.

Quarterly

- Inspect baffle plate for wear.

- Thoroughly inspect bags.

- Check duct for dust build-up.

- Observe damper valves for proper seating.

- Check gaskets on all doors.

- Inspect paint.

- Check screw conveyor flighting.

Annually

- Check all bolts.

- Check welds.

- Inspect hopper for wear.

- Check airlock rotor for wear.

C)	Records:

Records of inspections, maintenance, and performance parameters shall be retained for a minimum of five years and shall be made available to the Department or Environmental Protection Commission of Hillsborough County upon request. [Rule 62-296.700(6)(e), F.A.C.]

Emission Unit No. 110 - Storage Building Ventilation,

N.W. Baghouse III

Operation and Maintenance Plan for Particulate Control: [Rule 62-296.700, F.A.C.]

A)	Process Parameters:

- Source Designators: Storage Building  N.W. Baghouse

- Baghouse Manufacturer: American Air Filter

- Model Name and Number: Amerpulse Size 10-312

- Design Flow Rate: 79,000 ACFM

- Efficiency Rating at Design Capacity:  99.99%

- Pressure Drop: 0-8 in. H2O

- Air to Cloth Ratio:  11.51 to 1

- Bag Weave: 200 Mesh

- Bag Material:  Polyester-felt

- Bag Cleaning Conditions:  Pulse-air (pressure 90 psi)

- Gas Flow Rate: 78,667 DSCFM

- Gas Temperatures:  inlet; Ambient ;  outlet; Ambient

- Stack Height Above Ground:  15 ft.

- Exit Diameter: 8 ft. 5 in.

- Water Vapor Content:  Ambient

- Process Controlled by Collection System:  Storage Building

- Material Handling Rate: Wet Phosphate Rock - 2,800 TPH max, MAP/DAP/GTSP - 2,000 TPH max.

- Operation Schedule:  1,800 hours per year

B)	The following observations, checks and operations apply to this source and shall be conducted on the schedule specified:

Daily

- Check the pressure drop if the baghouse is in operation while material is being handled.

- Observe stack (visual).

- Walk through system listening for proper operation (audible leaks, proper fan and motor functions, bag cleaning systems, etc.).

- Note any unusual occurrence in the process being ventilated.

Weekly

- Inspect screw conveyor and air lock bearings for lubrication.

- Check packing glands.

- Operate all damper valves (isolation, by-pass, etc.).

- Check bag cleaning sequence to see that all valves are opening and closing properly.

- Spot check bag tension inside bag collectors.

- Check pressure drop indicating equipment for plugged lines.

- Check inlet filter on reverse air blower.

- Check compressed air lines, including line oilers and filters.

Monthly

- Check cleaning mechanism moving parts.

- Inspect fans for corrosion and material build-up.

- Check all drive belts and chains for wear and tension.

- Check all hoses and clamps.

- Check accuracy of all indicating equipment.

- Inspect housing for corrosion.

Quarterly

- Inspect baffle plate for wear.

- Thoroughly inspect bags.

- Check duct for dust build-up.

- Observe damper valves for proper seating.

- Check gaskets on all doors.

- Inspect paint.

- Check screw conveyor flighting.

Annually

- Check all bolts.

- Check welds.

- Inspect hopper for wear.

- Check airlock rotor for wear.

C)	Records:

Records of inspections, maintenance, and performance parameters shall be retained for a minimum of five years and shall be made available to the Department or Environmental Protection Commission of Hillsborough County upon request. [Rule 62-296.700(6)(e), F.A.C.]

Emission Unit No. 111 - Storage Building Ventilation,

N.E. Baghouse IV

Operation and Maintenance Plan for Particulate Control: [Rule 62-296.700, F.A.C.]

A)	Process Parameters:

- Source Designators: Storage Building With N.E. Baghouse (IV)

- Baghouse Manufacturer: American Air Filter

- Model Name and Number: Amerpulse Size 10-312

- Design Flow Rate: 79,000 ACFM

- Efficiency Rating at Design Capacity:  99.99%

- Pressure Drop: 0-8 in. H2O

- Air to Cloth Ratio:  11.51 to 1

- Bag Weave: 200 Mesh

- Bag Material:  Polyester-felt

- Bag Cleaning Conditions:  Pulse-air (pressure 90 psi)

- Gas Flow Rate: 73,205 DSCFM (measured)

- Gas Temperatures:  inlet; Ambient ;  outlet; Ambient

- Stack Height Above Ground:  15 ft.

- Exit Diameter: 8 ft. 5 in.

- Water Vapor Content:  Ambient

- Process Controlled by Collection System:  Storage Building

- Material Handling Rate: Wet Phosphate Rock - 2,800 TPH max, MAP/DAP/GTSP - 2,000 TPH max

- Operation Schedule:  1,800 hours per year

B)	The following observations, checks and operations apply to this source and shall be conducted on the schedule specified:

Daily

- Check the pressure drop if the baghouse is in operation while material is being handled.

- Observe stack (visual).

- Walk through system listening for proper operation (audible leaks, proper fan and motor functions, bag cleaning systems, etc.).

- Note any unusual occurrence in the process being ventilated.

Weekly

- Inspect screw conveyor and air lock bearings for lubrication.

- Check packing glands.

- Operate all damper valves (isolation, by-pass, etc.).

- Check bag cleaning sequence to see that all valves are opening and closing properly.

- Spot check bag tension inside bag collectors.

- Check pressure drop indicating equipment for plugged lines.

- Check inlet filter on reverse air blower.

- Check compressed air lines, including line oilers and filters.

Monthly

- Check cleaning mechanism moving parts.

- Inspect fans for corrosion and material build-up.

- Check all drive belts and chains for wear and tension.

- Check all hoses and clamps.

- Check accuracy of all indicating equipment.

- Inspect housing for corrosion.

Quarterly

- Inspect baffle plate for wear.

- Thoroughly inspect bags.

- Check duct for dust build-up.

- Observe damper valves for proper seating.

- Check gaskets on all doors.

- Inspect paint.

- Check screw conveyor flighting.

Annually

- Check all bolts.

- Check welds.

- Inspect hopper for wear.

- Check airlock rotor for wear.

C)	Records:

Records of inspections, maintenance, and performance parameters shall be retained for a minimum of five years and shall be made available to the Department or Environmental Protection Commission of Hillsborough County upon request. [Rule 62-296.700(6)(e), F.A.C.]